## Cover
Tollaust Pty Ltd
Lane Cove Tunnel
Marden St Ventilation Stack Validated Data
2021-01-01 00:05 | to | 2021-02-01
Issue Date: | 2021-02-08
Norditech Pty Ltd. 2/87 Station Road, Seven Hills, NSW, 2147 Australia.
Ph: 1300 572 822, Email: admin@norditech.com.au, Web: www.norditech.com.au
Accredited for compliance with ISO/IEC 17025 - Testing Accreditation No. 19660.
This document shall not be reproduced except in full, without the written approval of Norditech Pty Ltd.

## Marden St 5m Avg
Date/Time | CO (mg/m³) | NO (mg/m³) | NO2 (mg/m³) | NOx (NO2 eq., mg/m³) | PM10 (µg/m³) | PM2.5 (µg/m³) | Met (mg/m³) | NMHC (CH4 eq., mg/m³) | Stack Flow (m³/s) | Stack Temp (°C) | Stack RH (%)
2021-01-01 00:05 | 0.57325 | 0.13247 | 0.085824 | 0.28887 | -0.33631 |  | 1.3971 | 0.043659 | 286.6241 | 23.78 | 64.08
2021-01-01 00:10 | 0.54775 | 0.12973 | 0.069074 | 0.26792 | -7.7653 |  | 1.397 | 0.058209 | 286.6689 | 23.75 | 64.01
2021-01-01 00:15 | 0.58601 | 0.18846 | 0.066987 | 0.35587 | 2.1402 |  | 1.4044 | 0.072767 | 287.201 | 23.73 | 64.37
2021-01-01 00:20 | 0.54788 | 0.23493 | 0.073278 | 0.43548 | 2.2323 |  | 1.4046 | 0.065501 | 286.5694 | 23.78 | 64.72
2021-01-01 00:25 | 0.39503 | 0.19534 | 0.052347 | 0.35177 | -4.6995 |  | 1.4048 | 0.05823 | 287.0944 | 23.76 | 65.16
2021-01-01 00:30 | 0.34405 | 0.1967 | 0.056534 | 0.35805 | 8.726 |  | 1.4047 | 0.050949 | 287.1317 | 23.73 | 65.18
2021-01-01 00:35 | 0.36957 | 0.19126 | 0.060728 | 0.35599 | 10.1136 |  | 1.3904 | 0.050955 | 286.5714 | 23.72 | 65.61
2021-01-01 00:40 | 0.36962 | 0.19812 | 0.06702 | 0.3707 | 3.9155 |  | 1.3905 | 0.050962 | 285.4791 | 23.7 | 66.14
2021-01-01 00:45 | 0.33141 | 0.25005 | 0.064929 | 0.44822 | 2.3352 |  | 1.3906 | 0.058246 | 286.5336 | 23.7 | 66.36
2021-01-01 00:50 | 0.26767 | 0.21179 | 0.058645 | 0.38328 | 7.6273 |  | 1.3906 | 0.058245 | 287.0665 | 23.71 | 66.25
2021-01-01 00:55 | 0.3314 | 0.13937 | 0.052362 | 0.266 | 10.3398 |  | 1.3906 | 0.050965 | 286.8272 | 23.66 | 66.41
2021-01-01 01:00 | 0.26773 | 0.17767 | 0.054467 | 0.3268 | 3.3453 |  | 1.3909 | 0.058257 | 287.3062 | 23.66 | 67.08
2021-01-01 01:05 |  |  |  |  | 8.2303 |  |  |  | 287.319 | 23.66 | 66.93
2021-01-01 01:10 |  |  |  |  | 18.3893 |  |  |  | 286.7246 | 23.7 | 67
2021-01-01 01:15 |  |  |  |  | 16.4428 |  |  |  | 286.0954 | 23.77 | 67.02
2021-01-01 01:20 |  |  |  |  | 9.5162 |  |  |  | 286.1222 | 23.76 | 66.86
2021-01-01 01:25 |  |  |  |  | 14.4803 |  |  |  | 286.252 | 23.69 | 66.41
2021-01-01 01:30 |  |  |  |  | 9.5236 |  |  |  | 286.8593 | 23.64 | 66.34
2021-01-01 01:35 |  |  |  |  | 1.0197 |  |  |  | 287.4358 | 23.58 | 66.79
2021-01-01 01:40 |  |  |  |  | 4.2926 |  |  |  | 286.9987 | 23.51 | 66.7
2021-01-01 01:45 |  |  |  |  | 16.4976 |  |  |  | 285.9014 | 23.53 | 66.68
2021-01-01 01:50 |  |  |  |  | 5.0881 |  |  |  | 288.0482 | 23.52 | 66.82
2021-01-01 01:55 |  |  |  |  | -0.8158 |  |  |  | 288.5583 | 23.52 | 67.13
2021-01-01 02:00 |  |  |  |  | 10.9306 |  |  |  | 287.0379 | 23.46 | 67.01
2021-01-01 02:05 |  |  |  |  | 10.3185 |  |  |  | 287.094 | 23.41 | 67.12
2021-01-01 02:10 | 0.25495 | 0.20908 | 0.073313 | 0.39379 | 0.10198 |  | 1.4635 | -0.021844 | 286.5178 | 23.4 | 67.75
2021-01-01 02:15 | 0.22946 | 0.18722 | 0.060747 | 0.34773 | 6.3536 |  | 1.4345 | 0 | 286.4476 | 23.46 | 67.65
2021-01-01 02:20 | 0.19121 | 0.19814 | 0.10054 | 0.40636 | 9.0761 |  | 1.4126 | 0.072813 | 286.9967 | 23.46 | 67.5
2021-01-01 02:25 | 0.19121 | 0.15305 | 0.073313 | 0.30792 | 6.6389 |  | 1.4053 | 0.065532 | 285.9301 | 23.45 | 67.58
2021-01-01 02:30 | 0.089242 | 0.14897 | 0.079606 | 0.30795 | 2.2132 |  | 1.3982 | 0.043693 | 285.9194 | 23.43 | 68.02
2021-01-01 02:35 | 0.050995 | 0.15033 | 0.079605 | 0.31004 | 7.0169 |  | 1.4054 | 0.029128 | 288.6336 | 23.4 | 68.11
2021-01-01 02:40 | 0.15298 | 0.1148 | 0.064939 | 0.2409 | 12.0243 |  | 1.3981 | 0.029128 | 287.5673 | 23.4 | 68.03
2021-01-01 02:45 | 0.089245 | 0.12711 | 0.056564 | 0.25139 | -0.14279 |  | 1.3909 | 0.036412 | 286.4946 | 23.38 | 68.34
2021-01-01 02:50 | 0.050999 | 0.091573 | 0.058661 | 0.19903 | -0.061199 |  | 1.3983 | 0.036413 | 287.0406 | 23.36 | 68.54
2021-01-01 02:55 | 0.06375 | 0.11481 | 0.054472 | 0.23046 | 12.8315 |  | 1.391 | 0.021848 | 286.5276 | 23.33 | 68.73
2021-01-01 03:00 | [9 empty] | 23.25 | 68.69
2021-01-01 03:05 | 0.14024 | 0.1763 | 0.056562 | 0.3268 | 4.712 |  | 1.3909 | 0.043693 | 286.6497 | 23.23 | 68.84
2021-01-01 03:10 | 0.089237 | 0.16809 | 0.062843 | 0.3205 | 7.6387 |  | 1.3908 | 0.029127 | 286.0895 | 23.27 | 68.49
2021-01-01 03:15 | 0.16571 | 0.19541 | 0.064932 | 0.36446 | 13.8686 |  | 1.3907 | 0.029124 | 286.0974 | 23.29 | 68.08
2021-01-01 03:20 | 0.16572 | 0.23368 | 0.077503 | 0.43569 | 12.564 |  | 1.3835 | 0.029126 | 286.5623 | 23.35 | 68
2021-01-01 03:25 | 0.11473 | 0.15988 | 0.067028 | 0.3121 | -0.56088 |  | 1.3907 | 0.029125 | 286.6161 | 23.3 | 68.14
2021-01-01 03:30 | 0.25492 | 0.1544 | 0.05655 | 0.29532 | 6.5567 |  | 1.3906 | 0.029123 | 286.1611 | 23.24 | 68.1
2021-01-01 03:35 | 0.29312 | 0.12569 | 0.056542 | 0.2492 | 4.4656 |  | 1.3904 | 0.029118 | 286.2438 | 23.2 | 67.73
2021-01-01 03:40 | 0.16568 | 0.1175 | 0.05445 | 0.23246 | -1.7741 |  | 1.3832 | 0.02184 | 286.7961 | 23.17 | 68.02
2021-01-01 03:45 | 0.19116 | 0.11886 | 0.054447 | 0.23664 | 4.0985 |  | 1.3831 | 0.029118 | 286.8127 | 23.17 | 67.82
2021-01-01 03:50 | 0.2039 | 0.076503 | 0.056539 | 0.1759 | 16.7605 |  | 1.383 | 0.029117 | 286.2863 | 23.17 | 67.69
2021-01-01 03:55 | 0.24217 | 0.092913 | 0.054455 | 0.19687 | 9.3402 |  | 1.3906 | 0.036402 | 285.6794 | 23.19 | 68.22
2021-01-01 04:00 | 0.14021 | 0.086086 | 0.052363 | 0.18432 | 4.7316 |  | 1.3979 | 0.029124 | 286.1999 | 23.19 | 68.42
2021-01-01 04:05 | 0.15296 | 0.081987 | 0.054458 | 0.18013 | 16.7236 |  | 1.3979 | 0.021843 | 287.3025 | 23.16 | 68.55
2021-01-01 04:10 | 0.16571 | 0.14075 | 0.058649 | 0.27439 | 12.3188 |  | 1.398 | 0.036406 | 285.6523 | 23.19 | 68.55
2021-01-01 04:15 | 0.21668 | 0.1626 | 0.069117 | 0.32045 | 6.9747 |  | 1.3906 | 0.036403 | 287.7742 | 23.24 | 68.07
2021-01-01 04:20 | 0.25485 | 0.13113 | 0.050252 | 0.25126 | 9.6741 |  | 1.3902 | 0.029114 | 287.3399 | 23.22 | 67.15
2021-01-01 04:25 | 0.33125 | 0.12429 | 0.058618 | 0.24913 | 14.7891 |  | 1.39 | 0.029109 | 287.3847 | 23.22 | 66.61
2021-01-01 04:30 | 0.3313 | 0.18304 | 0.07119 | 0.35176 | 13.1093 |  | 1.3902 | 0.029114 | 286.2092 | 23.28 | 66.89
2021-01-01 04:35 | 0.39501 | 0.19124 | 0.073284 | 0.36642 | 10.0919 |  | 1.3975 | 0.04367 | 286.6993 | 23.33 | 66.67
2021-01-01 04:40 | 0.36938 | 0.17614 | 0.083719 | 0.35581 | 17.0169 |  | 1.3896 | 0.029102 | 286.7943 | 23.35 | 65.22
2021-01-01 04:45 | 0.22918 | 0.12693 | 0.075316 | 0.26988 | 22.5508 |  | 1.389 | 0.021817 | 288.0266 | 23.31 | 63.95
2021-01-01 04:50 | 0.19094 | 0.18831 | 0.081575 | 0.37023 | 4.6946 |  | 1.396 | 0.036355 | 287.3072 | 23.3 | 63.33
2021-01-01 04:55 | 0.33092 | 0.19784 | 0.071107 | 0.37436 | 8.8176 |  | 1.3886 | 0.03635 | 286.79 | 23.32 | 62.77
2021-01-01 05:00 | 0.33088 | 0.17462 | 0.066917 | 0.33668 | 18.6108 |  | 1.3884 | 0.021808 | 287.3477 | 23.33 | 62.38
2021-01-01 05:05 | 0.20367 | 0.20469 | 0.060659 | 0.37441 | 9.7456 |  | 1.3888 | 0.021813 | 286.681 | 23.39 | 63
2021-01-01 05:10 | 0.19098 | 0.3453 | 0.062762 | 0.59206 | 6.4372 |  | 1.389 | 0.021817 | 286.5886 | 23.43 | 63.49
2021-01-01 05:15 | 0.26735 | 0.33573 | 0.056482 | 0.57109 | 13.7289 |  | 1.3962 | 0.029087 | 286.5905 | 23.45 | 63.16
2021-01-01 05:20 | 0.22916 | 0.32072 | 0.066943 | 0.55855 | 17.691 |  | 1.3889 | 0.021816 | 286.5277 | 23.51 | 62.99
2021-01-01 05:25 | 0.43273 | 0.41477 | 0.10875 | 0.74452 | 9.2451 |  | 1.3958 | 0.02181 | 286.6006 | 23.52 | 61.97
2021-01-01 05:30 | 1.349 | 0.31379 | 0.081558 | 0.56254 | 10.1201 |  | 1.3885 | 0.065425 | 286.6569 | 23.48 | 61.91
2021-01-01 05:35 | 1.2599 | 0.3588 | 0.08783 | 0.63573 | 12.6551 |  | 1.3957 | 0.050885 | 286.6988 | 23.44 | 62.02
2021-01-01 05:40 | 0.91636 | 0.36292 | 0.07738 | 0.63577 | 9.408 |  | 1.3958 | 0.050889 | 287.2071 | 23.45 | 62.22
2021-01-01 05:45 | 1.9981 | 0.38336 | 0.083649 | 0.67128 | 11.7491 |  | 1.3957 | 0.079963 | 286.6672 | 23.47 | 61.94
2021-01-01 05:50 | 1.2214 | 0.37643 | 0.1108 | 0.68572 | 16.0511 |  | 1.3953 | 0.065405 | 287.289 | 23.47 | 60.94
2021-01-01 05:55 | 0.59787 | 0.2291 | 0.085701 | 0.43896 | 16.0586 |  | 1.3878 | 0.050863 | 287.3745 | 23.43 | 60.53
2021-01-01 06:00 | 0.89051 | 0.3273 | 0.11079 | 0.6104 | 11.1238 |  | 1.3952 | 0.065399 | 286.7685 | 23.48 | 60.58
2021-01-01 06:05 | 0.72511 | 0.2482 | 0.089886 | 0.47033 | 17.3417 |  | 1.4024 | 0.043598 | 287.2451 | 23.55 | 60.25
2021-01-01 06:10 | 0.39437 | 0.18547 | 0.098249 | 0.38254 | 26.5524 |  | 1.3879 | 0.050866 | 287.2298 | 23.56 | 60.28
2021-01-01 06:15 | 0.29257 | 0.16227 | 0.085699 | 0.33444 | 16.9335 |  | 1.3951 | 0.043596 | 287.3121 | 23.5 | 60.21
2021-01-01 06:20 | 0.41976 | 0.16908 | 0.075245 | 0.33233 | 15.4166 |  | 1.395 | 0.058125 | 287.3827 | 23.44 | 60.28
2021-01-01 06:25 | 0.38159 | 0.1609 | 0.064793 | 0.31143 | 22.4071 |  | 1.395 | 0.043593 | 287.4159 | 23.41 | 60.34
2021-01-01 06:30 | 0.31796 | 0.13089 | 0.064786 | 0.26333 | 17.3275 |  | 1.3876 | 0.050853 | 287.4852 | 23.37 | 60.12
2021-01-01 06:35 | 0.22892 | 0.14179 | 0.071053 | 0.28839 | 16.2382 |  | 1.3948 | 0.043587 | 286.4007 | 23.39 | 59.91
2021-01-01 06:40 | 0.22889 | 0.13632 | 0.068955 | 0.27791 | 16.9584 |  | 1.3946 | 0.043581 | 287.4555 | 23.45 | 59.26
2021-01-01 06:45 | 0.35597 | 0.12811 | 0.060581 | 0.25904 | 9.0924 |  | 1.3942 | 0.029047 | 286.4517 | 23.45 | 58.39
2021-01-01 06:50 | 0.35596 | 0.10085 | 0.058491 | 0.21308 | 4.0376 |  | 1.3942 | 0.036308 | 287.2794 | 23.45 | 58.4
2021-01-01 06:55 | 0.30509 | 0.080402 | 0.056399 | 0.17964 | 15.7021 |  | 1.3941 | 0.029045 | 287.8538 | 23.43 | 58.28
2021-01-01 07:00 | 0.25422 | 0.080396 | 0.058484 | 0.18172 | 21.3549 |  | 1.394 | 0.029043 | 288.4333 | 23.41 | 58.1
2021-01-01 07:05 | 0.52107 | 0.089919 | 0.062651 | 0.20048 | 6.2325 |  | 1.3938 | 0.043557 | 288.482 | 23.41 | 57.52
2021-01-01 07:10 | 0.38125 | 0.083102 | 0.064735 | 0.19421 | 9.4143 |  | 1.3865 | 0.029036 | 287.4018 | 23.43 | 57.24
2021-01-01 07:15 | 0.41933 | 0.098076 | 0.068904 | 0.21924 | 18.552 |  | 1.3936 | 0.036291 | 287.9552 | 23.45 | 56.77
2021-01-01 07:20 | 0.5845 | 0.10488 | 0.075165 | 0.23802 | 17.4332 |  | 1.4008 | 0.043547 | 287.9159 | 23.5 | 56.49
2021-01-01 07:25 | 0.49548 | 0.092612 | 0.062629 | 0.20459 | 16.1908 |  | 1.3933 | 0.036284 | 287.3879 | 23.53 | 55.91
2021-01-01 07:30 | 0.48274 | 0.093967 | 0.060537 | 0.20457 | 22.3484 |  | 1.3932 | 0.029026 | 287.4372 | 23.5 | 55.77
2021-01-01 07:35 | 0.48274 | 0.13891 | 0.066798 | 0.27972 | 14.7869 |  | 1.3859 | 0.036281 | 287.9907 | 23.49 | 55.75
2021-01-01 07:40 | 0.40647 | 0.16749 | 0.062617 | 0.32144 | 19.6733 |  | 1.3931 | 0.029022 | 287.4309 | 23.54 | 55.25
2021-01-01 07:45 | 0.39382 | 0.22334 | 0.0835 | 0.42794 | 28.609 |  | 1.3932 | 0.029026 | 288.4072 | 23.61 | 55.42
2021-01-01 07:50 | 0.31756 | 0.31727 | 0.083489 | 0.56981 | 17.9864 |  | 1.3931 | 0.029022 | 287.8557 | 23.66 | 54.83
2021-01-01 07:55 | 0.31748 | 0.40704 | 0.093903 | 0.71784 | 22.0864 |  | 1.3927 | 0.021761 | 287.8955 | 23.69 | 53.92
2021-01-01 08:00 | 0.33013 | 0.35798 | 0.093888 | 0.6447 | 27.5682 |  | 1.3925 | 0.021758 | 287.9011 | 23.73 | 53.27
2021-01-01 08:05 | 0.33011 | 0.29808 | 0.1064 | 0.5633 | 25.4441 |  | 1.3924 | 0.029009 | 287.9435 | 23.7 | 53.21
2021-01-01 08:10 | 0.57144 | 0.29132 | 0.10433 | 0.55088 | 26.3219 |  | 1.3999 | 0.050774 | 287.3288 | 23.73 | 53.66
2021-01-01 08:15 | 0.60947 | 0.31851 | 0.10223 | 0.58837 | 31.0931 |  | 1.3998 | 0.043516 | 287.3611 | 23.73 | 53.28
2021-01-01 08:20 | 0.34284 | 0.3158 | 0.10015 | 0.5863 | 19.0668 |  | 1.3926 | 0.029012 | 286.784 | 23.76 | 53.29
2021-01-01 08:25 | 0.36827 | 0.31039 | 0.095989 | 0.57176 | 15.625 |  | 1.3927 | 0.021761 | 287.8099 | 23.78 | 53.61
2021-01-01 08:30 | 0.41913 | 0.36898 | 0.10018 | 0.66367 | 29.8623 |  | 1.3857 | 0.021764 | 287.1831 | 23.83 | 53.91
2021-01-01 08:35 | 0.50801 | 0.30361 | 0.091824 | 0.55512 | 24.5775 |  | 1.3856 | 0.043526 | 287.7365 | 23.83 | 53.74
2021-01-01 08:40 | 1.9046 | 0.31307 | 0.089718 | 0.56961 | 23.4246 |  | 1.4071 | 0.15231 | 287.8145 | 23.81 | 53.12
2021-01-01 08:45 | 1.8413 | 0.38116 | 0.095985 | 0.68024 | 29.7146 |  | 1.3999 | 0.11605 | 286.1673 | 23.82 | 53.33
2021-01-01 08:50 | 1.4477 | 0.32944 | 0.098074 | 0.60514 | 25.5502 |  | 1.3999 | 0.1088 | 287.7566 | 23.84 | 53.36
2021-01-01 08:55 | 1.2194 | 0.27779 | 0.06888 | 0.49468 | 23.5248 |  | 1.3931 | 0.10883 | 287.129 | 23.85 | 54.25
2021-01-01 09:00 | 1.2959 | 0.23017 | 0.085592 | 0.44049 | 31.0297 |  | 1.4006 | 0.15965 | 285.9733 | 23.88 | 54.73
2021-01-01 09:05 | 0.66071 | 0.29829 | 0.085601 | 0.54284 | 28.014 |  | 1.3935 | 0.094349 | 286.444 | 23.92 | 54.94
2021-01-01 09:10 | 0.50827 | 0.35143 | 0.089782 | 0.62847 | 17.8401 |  | 1.4008 | 0.065322 | 286.3889 | 23.96 | 55
2021-01-01 09:15 | 0.88948 | 0.50128 | 0.12737 | 0.89575 | 10.5315 |  | 1.4008 | 0.07984 | 331.0182 | 24 | 54.94
2021-01-01 09:20 | 1.2452 | 0.53394 | 0.13989 | 0.95833 |  |  | 1.4007 | 0.079835 | 455.3583 | 24.07 | 54.45
2021-01-01 09:25 | 0.991 | 0.28057 | 0.10439 | 0.53445 |  |  | 1.3934 | 0.058058 | 455.3771 | 24.08 | 54.17
2021-01-01 09:30 | 0.69881 | 0.28194 | 0.096038 | 0.52821 | -13.9254 |  | 1.3934 | 0.05806 | 455.4362 | 24.03 | 54.46
2021-01-01 09:35 | 0.88935 | 0.34185 | 0.085595 | 0.6096 | 3.6489 |  | 1.4006 | 0.065314 | 457.1975 | 23.95 | 54.54
2021-01-01 09:40 | 0.78782 | 0.2125 | 0.081431 | 0.40715 | 16.9355 |  | 1.3935 | 0.050806 | 456.1204 | 23.91 | 55.13
2021-01-01 09:45 | 0.68602 | 0.39494 | 0.13778 | 0.74316 | 18.8426 |  | 1.4005 | 0.065309 | 455.1716 | 23.89 | 54.49
2021-01-01 09:50 | 0.66052 | 0.44936 | 0.12315 | 0.81194 | 30.4451 |  | 1.4003 | 0.0653 | 456.2293 | 23.94 | 53.9
2021-01-01 09:55 | 0.88909 | 0.40983 | 0.1294 | 0.7576 | 30.991 |  | 1.3929 | 0.079804 | 455.7025 | 23.96 | 53.53
2021-01-01 10:00 | 0.96513 | 0.44788 | 0.1419 | 0.82633 | 19.7292 |  | 1.3927 | 0.094298 | 455.7508 | 23.98 | 52.89
2021-01-01 10:05 | 0.96513 | 0.39207 | 0.1252 | 0.72618 | 22.5333 |  | 1.3927 | 0.087045 | 455.1478 | 24.02 | 52.79
2021-01-01 10:10 | 1.0415 | 0.46565 | 0.12522 | 0.83899 | 15.8916 |  | 1.4002 | 0.087058 | 455.0323 | 24.05 | 53.2
2021-01-01 10:15 | 1.3335 | 0.49557 | 0.12521 | 0.88484 | 27.7372 |  | 1.3928 | 0.087052 | 455.0017 | 24.09 | 52.85
2021-01-01 10:20 | 0.9525 | 0.38665 | 0.13356 | 0.72832 | 28.3464 |  | 1.4001 | 0.065288 | 455.5012 | 24.12 | 52.7
2021-01-01 10:25 | 0.95261 | 0.36763 | 0.12523 | 0.69083 | 23.6756 |  | 1.4075 | 0.072551 | 454.3407 | 24.14 | 53.03
2021-01-01 10:30 | 0.93999 | 0.34043 | 0.13985 | 0.66167 | 22.4989 |  | 1.4076 | 0.087069 | 455.3462 | 24.16 | 53.25
2021-01-01 10:35 | 1.3466 | 0.39628 | 0.13986 | 0.7473 | 17.8051 |  | 1.4222 | 0.1161 | 454.72 | 24.2 | 53.32
2021-01-01 10:40 | 1.55 | 0.55023 | 0.15031 | 0.99372 | 25.4605 |  | 1.4224 | 0.14514 | 452.4117 | 24.27 | 53.47
2021-01-01 10:45 | 1.5625 | 0.56786 | 0.12316 | 0.99359 | 22.6725 |  | 1.4149 | 0.1161 | 454.6067 | 24.28 | 53
2021-01-01 10:50 | 1.7656 | 0.52015 | 0.13984 | 0.93715 | 31.4704 |  | 1.4075 | 0.13785 | 453.5878 | 24.27 | 52.74
2021-01-01 10:55 | 2.0959 | 0.50247 | 0.14193 | 0.91213 | 21.7566 |  | 1.4076 | 0.31199 | 454.1113 | 24.27 | 52.84
2021-01-01 11:00 | 1.8802 | 0.43309 | 0.12317 | 0.78702 | 22.4308 |  | 1.4078 | 0.24673 | 453.9951 | 24.3 | 53.25
2021-01-01 11:05 | 1.8164 | 0.43573 | 0.11688 | 0.78478 | 28.0864 |  | 1.4003 | 0.22491 | 454.0674 | 24.31 | 52.59
2021-01-01 11:10 | 1.3081 | 0.44247 | 0.14608 | 0.82432 | 23.7138 |  | 1.4001 | 0.10156 | 453.0232 | 24.33 | 52.09
2021-01-01 11:15 | 1.0923 | 0.56503 | 0.16904 | 1.0351 | 27.9617 |  | 1.3929 | 0.09431 | 454.589 | 24.35 | 52.14
2021-01-01 11:20 | 1.0543 | 0.50927 | 0.15863 | 0.93925 | 26.4512 |  | 1.3931 | 0.087066 | 453.4107 | 24.38 | 52.46
2021-01-01 11:25 | 1.2448 | 0.49428 | 0.15445 | 0.9121 | 24.9061 |  | 1.4003 | 0.13785 | 453.9255 | 24.4 | 52.34
2021-01-01 11:30 | 1.5242 | 0.43708 | 0.15654 | 0.82651 | 21.8266 |  | 1.4075 | 0.13785 | 453.3995 | 24.4 | 52.26
2021-01-01 11:35 | 1.4861 | 0.52423 | 0.1628 | 0.96636 | 25.8204 |  | 1.4075 | 0.15962 | 453.9297 | 24.4 | 52.31
2021-01-01 11:40 | 1.3081 | 0.6453 | 0.16903 | 1.1582 | 31.0885 |  | 1.4 | 0.12332 | 453.4612 | 24.41 | 51.68
2021-01-01 11:45 | 0.93979 | 0.57996 | 0.1586 | 1.0455 | 24.9424 |  | 1.4 | 0.072541 | 453.422 | 24.43 | 51.68
2021-01-01 11:50 | 0.91438 | 0.54593 | 0.13564 | 0.97246 | 23.7536 |  | 1.4 | 0.058033 | 454.9903 | 24.46 | 51.57
2021-01-01 11:55 | 1.3461 | 0.46285 | 0.12311 | 0.83258 | 24.8185 |  | 1.3999 | 0.10155 | 453.9343 | 24.47 | 51.3
2021-01-01 12:00 | 2.3749 | 0.3989 | 0.12104 | 0.73248 | 19.0803 |  | 1.4073 | 0.15234 | 454.3873 | 24.5 | 51.48
2021-01-01 12:05 | 2.4765 | 0.39345 | 0.14399 | 0.745 | 27.5026 |  | 1.4146 | 0.16684 | 453.3159 | 24.5 | 51.46
2021-01-01 12:10 | 2.1711 | 0.3811 | 0.11475 | 0.69891 | 24.2556 |  | 1.4142 | 0.18856 | 455.0403 | 24.5 | 50.66
2021-01-01 12:15 | 2.6284 | 0.47505 | 0.13145 | 0.85962 | 18.7618 |  | 1.407 | 0.15231 | 454.472 | 24.5 | 50.88
2021-01-01 12:20 | 3.3903 | 0.49548 | 0.1231 | 0.88259 | 24.8064 |  | 1.4071 | 0.15231 | 452.82 | 24.52 | 50.89
2021-01-01 12:25 | 2.9333 | 0.59079 | 0.14606 | 1.0516 | 22.4303 |  | 1.3999 | 0.13781 | 452.7849 | 24.53 | 51
2021-01-01 12:30 | 1.2952 | 0.54856 | 0.14605 | 0.98691 | 20.5195 |  | 1.4071 | 0.094288 | 453.3446 | 24.53 | 50.84
2021-01-01 12:35 | 1.9173 | 0.42739 | 0.14187 | 0.797 | 20.295 |  | 1.407 | 0.18131 | 454.4861 | 24.5 | 50.78
2021-01-01 12:40 | 1.5616 | 0.34707 | 0.121 | 0.653 | 24.6816 |  | 1.4142 | 0.10878 | 454.5157 | 24.5 | 50.57
2021-01-01 12:45 | 1.3585 | 0.40286 | 0.1356 | 0.75103 | 26.2043 |  | 1.4069 | 0.10153 | 454.5604 | 24.48 | 50.53
2021-01-01 12:50 | 1.3329 | 0.4205 | 0.15227 | 0.79683 | 13.578 |  | 1.4067 | 0.094264 | 454.1057 | 24.46 | 50.22
2021-01-01 12:55 | 0.9649 | 0.39197 | 0.11057 | 0.71348 | 14.9203 |  | 1.3996 | 0.079771 | 454.0648 | 24.45 | 50.65
2021-01-01 13:00 | 1.3713 | 0.35389 | 0.10849 | 0.65094 | 20.4268 |  | 1.407 | 0.094282 | 454.0171 | 24.46 | 50.85
2021-01-01 13:05 | 1.625 | 0.45184 | 0.11682 | 0.80943 | 29.8399 |  | 1.3996 | 0.10152 | 454.5981 | 24.46 | 50.54
2021-01-01 13:10 | 1.8279 | 0.51982 | 0.10638 | 0.90318 | 25.3066 |  | 1.4066 | 0.13051 | 455.2142 | 24.45 | 50.12
2021-01-01 13:15 | 1.5486 | 0.45993 | 0.12723 | 0.83432 | 19.2738 |  | 1.4139 | 0.10151 | 454.17 | 24.44 | 50.04
2021-01-01 13:20 | 1.6246 | 0.45307 | 0.1293 | 0.82379 | 18.7639 |  | 1.4064 | 0.12324 | 454.7443 | 24.45 | 49.64
2021-01-01 13:25 | 1.7256 | 0.51279 | 0.13969 | 0.92572 | 16.3021 |  | 1.406 | 0.13046 | 455.9795 | 24.43 | 48.78
2021-01-01 13:30 | 1.5225 | 0.43252 | 0.14802 | 0.811 | 12.9515 |  | 1.406 | 0.1232 | 453.4209 | 24.42 | 48.56
2021-01-01 13:35 | 1.9032 | 0.46789 | 0.1522 | 0.86939 | 20.8385 |  | 1.4132 | 0.15219 | 453.9966 | 24.39 | 48.7
2021-01-01 13:40 | 1.8143 | 0.5549 | 0.15844 | 1.009 | 15.6914 |  | 1.4131 | 0.16668 | 452.3962 | 24.4 | 48.48
2021-01-01 13:45 | 2.5121 | 0.73581 | 0.16053 | 1.2884 | 33.3834 |  | 1.4059 | 0.18118 | 453.9623 | 24.42 | 48.53
2021-01-01 13:50 | 3.3641 | 0.70086 | 0.16897 | 1.2433 | 36.5613 |  | 1.414 | 0.2538 | 453.0293 | 24.45 | 50.37
2021-01-01 13:55 | 3.2013 | 0.57741 | 0.15238 | 1.0375 | 45.6516 |  | 1.415 | 0.20318 | 453.2565 | 24.45 | 52.58
2021-01-01 14:00 | 1.9062 | 0.42231 | 0.13991 | 0.78515 | 34.5147 |  | 1.4082 | 0.15969 | 454.282 | 24.38 | 53.91
2021-01-01 14:05 | 1.3978 | 0.37053 | 0.1399 | 0.70786 | 29.1358 |  | 1.4009 | 0.094361 | 455.4937 | 24.3 | 54.06
2021-01-01 14:10 | 1.1063 | 0.35716 | 0.15254 | 0.7 | 30.1326 |  | 1.3873 | 0.072636 | 454.2119 | 24.23 | 56.55
2021-01-01 14:15 | 1.5006 | 0.4717 | 0.1421 | 0.86722 | 14.1009 |  | 1.3947 | 0.087169 | 454.8526 | 24.14 | 57.1
2021-01-01 14:20 | 1.5261 | 0.60667 | 0.17136 | 1.1013 | 14.4977 |  | 1.402 | 0.079905 | 454.928 | 24.09 | 57.28
2021-01-01 14:25 | 1.6783 | 0.63652 | 0.18177 | 1.1575 | 23.5475 |  | 1.4017 | 0.065363 | 454.0093 | 24.05 | 56.73
2021-01-01 14:30 | 2.4024 | 0.59957 | 0.17336 | 1.0924 | 26.9074 |  | 1.3868 | 0.10891 | 455.3163 | 24.03 | 55.89
2021-01-01 14:35 | 2.415 | 0.57092 | 0.17335 | 1.0485 | 30.9528 |  | 1.3867 | 0.13795 | 454.3316 | 23.99 | 55.82
2021-01-01 14:40 | 2.2251 | 0.47297 | 0.14416 | 0.87123 | 22.7644 |  | 1.3872 | 0.13073 | 454.2443 | 23.95 | 57.04
2021-01-01 14:45 | 2.4546 | 0.43765 | 0.12539 | 0.79623 | 7.5698 |  | 1.3875 | 0.13803 | 454.1676 | 23.92 | 58.04
2021-01-01 14:50 | 2.1746 | 0.53166 | 0.15045 | 0.9654 | 14.7209 |  | 1.3801 | 0.13075 | 453.1444 | 23.92 | 57.67
2021-01-01 14:55 | 1.6272 | 0.62281 | 0.16294 | 1.1176 | 18.8048 |  | 1.387 | 0.15249 | 454.8959 | 23.92 | 56.64
2021-01-01 15:00 | 1.8307 | 0.58331 | 0.16921 | 1.0612 | 21.7856 |  | 1.387 | 0.16702 | 453.7868 | 23.93 | 56.75
2021-01-01 15:05 | 1.3347 | 0.41832 | 0.13576 | 0.7749 | 24.8627 |  | 1.3795 | 0.13069 | 454.377 | 23.95 | 56.07
2021-01-01 15:10 | 1.1948 | 0.32701 | 0.14202 | 0.64328 | 14.2967 |  | 1.3867 | 0.11616 | 454.8426 | 24.01 | 55.72
2021-01-01 15:15 | 1.1821 | 0.35563 | 0.13785 | 0.68297 | 21.4555 |  | 1.3867 | 0.087124 | 455.3122 | 24.05 | 55.63
2021-01-01 15:20 | 1.22 | 0.46728 | 0.1587 | 0.87496 | 25.9045 |  | 1.3865 | 0.079848 | 455.382 | 24.06 | 54.98
2021-01-01 15:25 | 1.3214 | 0.46175 | 0.14615 | 0.85395 | 18.5409 |  | 1.379 | 0.079836 | 453.797 | 24.09 | 54.36
2021-01-01 15:30 | 1.169 | 0.38005 | 0.12737 | 0.70992 | 21.2258 |  | 1.3791 | 0.079841 | 454.8434 | 24.09 | 54.56
2021-01-01 15:35 | [9 empty] | 24.1 | 53.67
2021-01-01 15:40 | 0.97794 | 0.35535 | 0.12313 | 0.66782 | 14.062 |  | 1.3856 | 0.072545 | 455.0443 | 24.11 | 52.82
2021-01-01 15:45 | 1.5116 | 0.3799 | 0.12315 | 0.70548 | 18.7382 |  | 1.3858 | 0.1306 | 454.9267 | 24.15 | 53.1
2021-01-01 15:50 | 1.829 | 0.37579 | 0.1294 | 0.70543 | 12.0814 |  | 1.3929 | 0.15235 | 455.5126 | 24.14 | 52.89
2021-01-01 15:55 | 1.7905 | 0.35257 | 0.13772 | 0.67815 | 19.0479 |  | 1.3999 | 0.14507 | 454.1248 | 24.11 | 52.26
2021-01-01 16:00 | 1.803 | 0.42468 | 0.14188 | 0.79285 | 17.1568 |  | 1.3925 | 0.13055 | 454.7031 | 24.11 | 51.96
2021-01-01 16:05 | 2.2859 | 0.4656 | 0.1419 | 0.85559 | 32.0033 |  | 1.3928 | 0.10881 | 455.5653 | 24.14 | 52.51
2021-01-01 16:10 | 2.21 | 0.39758 | 0.12523 | 0.73674 | 27.6788 |  | 1.393 | 0.12334 | 452.8761 | 24.16 | 52.82
2021-01-01 16:15 | 2.21 | 0.33903 | 0.12522 | 0.6449 | 15.404 |  | 1.3929 | 0.17412 | 453.4041 | 24.17 | 52.74
2021-01-01 16:20 | 1.8926 | 0.38536 | 0.12523 | 0.71592 | 26.5224 |  | 1.4003 | 0.17413 | 454.406 | 24.19 | 52.97
2021-01-01 16:25 | 1.5115 | 0.43709 | 0.13358 | 0.80357 | 16.4111 |  | 1.4003 | 0.15236 | 453.3258 | 24.2 | 52.88
2021-01-01 16:30 | 1.2827 | 0.39073 | 0.12313 | 0.72206 | 21.3563 |  | 1.3928 | 0.10881 | 452.8936 | 24.18 | 52.41
2021-01-01 16:35 | 2.2859 | 0.38936 | 0.10851 | 0.70533 | 18.0638 |  | 1.4073 | 0.13057 | 454.0312 | 24.15 | 52.37
2021-01-01 16:40 | 2.0825 | 0.39885 | 0.10642 | 0.71779 | 17.1277 |  | 1.3999 | 0.13056 | 455.1265 | 24.16 | 52.07
2021-01-01 16:45 | 1.6131 | 0.35538 | 0.10853 | 0.65327 | 19.3065 |  | 1.393 | 0.10157 | 453.9382 | 24.16 | 52.9
2021-01-01 16:50 | 1.1304 | 0.33496 | 0.11897 | 0.6324 | 24.6817 |  | 1.393 | 0.087062 | 453.972 | 24.14 | 52.94
2021-01-01 16:55 | 1.0033 | 0.39208 | 0.14607 | 0.74707 | 20.4512 |  | 1.3855 | 0.087047 | 454.6608 | 24.09 | 52.55
2021-01-01 17:00 | 0.99049 | 0.41247 | 0.14606 | 0.77832 | 28.9122 |  | 1.3927 | 0.079788 | 453.6471 | 24.07 | 52.4
2021-01-01 17:05 | 0.88895 | 0.36212 | 0.1106 | 0.66567 | 20.7862 |  | 1.3855 | 0.072538 | 455.8332 | 24.03 | 52.69
2021-01-01 17:10 | 0.76195 | 0.29541 | 0.10016 | 0.55298 | 18.236 |  | 1.3855 | 0.079792 | 455.9126 | 23.98 | 52.83
2021-01-01 17:15 | 0.90156 | 0.29539 | 0.10641 | 0.55919 | 12.6472 |  | 1.3853 | 0.072531 | 454.3737 | 23.96 | 52.59
2021-01-01 17:20 | 0.85088 | 0.33082 | 0.12938 | 0.63648 | 18.7448 |  | 1.3855 | 0.065287 | 454.866 | 23.95 | 53.06
2021-01-01 17:25 | 0.91448 | 0.33358 | 0.13775 | 0.64907 | 18.8789 |  | 1.3929 | 0.065294 | 455.3679 | 23.94 | 53.46
2021-01-01 17:30 | 1.1432 | 0.37038 | 0.13985 | 0.70758 | 20.6084 |  | 1.3858 | 0.072556 | 454.2943 | 23.91 | 53.89
2021-01-01 17:35 | 1.4992 | 0.38135 | 0.14196 | 0.7265 | 28.1944 |  | 1.3933 | 0.07257 | 455.2678 | 23.92 | 54.48
2021-01-01 17:40 | 1.1818 | 0.35282 | 0.11484 | 0.65565 | 8.8341 |  | 1.3936 | 0.079843 | 454.6694 | 23.9 | 55.22
2021-01-01 17:45 | 1.4233 | 0.33241 | 0.10441 | 0.61394 | 12.9319 |  | 1.3937 | 0.11614 | 456.2108 | 23.87 | 55.61
2021-01-01 17:50 | 1.487 | 0.30792 | 0.098157 | 0.57014 | 24.1279 |  | 1.3939 | 0.1089 | 454.0584 | 23.84 | 56.07
2021-01-01 17:55 | 1.233 | 0.24801 | 0.08355 | 0.4637 | 14.8266 |  | 1.3941 | 0.087129 | 455.7644 | 23.79 | 56.67
2021-01-01 18:00 | 0.95367 | 0.22219 | 0.089846 | 0.43042 | 16.744 |  | 1.3945 | 0.079895 | 454.6319 | 23.73 | 57.99
2021-01-01 18:05 | 1.1827 | 0.24265 | 0.11075 | 0.48061 | 14.8022 |  | 1.4019 | 0.087165 | 455.7302 | 23.69 | 58.4
2021-01-01 18:10 | 1.4751 | 0.27809 | 0.11284 | 0.53911 | 14.0389 |  | 1.3946 | 0.0799 | 454.2226 | 23.63 | 58.53
2021-01-01 18:15 | 1.3738 | 0.32591 | 0.10242 | 0.60199 | 18.5414 |  | 1.4023 | 0.094457 | 454.6895 | 23.58 | 59.8
2021-01-01 18:20 | 1.3485 | 0.27957 | 0.10034 | 0.52888 | 18.6756 |  | 1.3952 | 0.0872 | 455.7471 | 23.56 | 60.22
2021-01-01 18:25 | 1.7429 | 0.21276 | 0.077349 | 0.40347 | 19.6024 |  | 1.3953 | 0.09447 | 456.2771 | 23.5 | 60.62
2021-01-01 18:30 | 1.6417 | 0.22646 | 0.081554 | 0.42868 | 16.5133 |  | 1.4029 | 0.094498 | 456.7256 | 23.47 | 61.74
2021-01-01 18:35 | 1.1961 | 0.33146 | 0.079452 | 0.58752 | 10.2608 |  | 1.3955 | 0.079948 | 455.8087 | 23.41 | 61.47
2021-01-01 18:40 | 1.2216 | 0.3233 | 0.10037 | 0.59593 | 14.639 |  | 1.3956 | 0.10176 | 456.3568 | 23.38 | 61.85
2021-01-01 18:45 | 1.1328 | 0.32336 | 0.094112 | 0.58977 | 9.2351 |  | 1.3958 | 0.08724 | 456.8709 | 23.34 | 62.64
2021-01-01 18:50 | 0.94176 | 0.32606 | 0.089922 | 0.58972 | 9.9979 |  | 1.4103 | 0.087232 | 455.9274 | 23.28 | 62.57
2021-01-01 18:55 | 1.311 | 0.27017 | 0.089937 | 0.50197 | 27.4732 |  | 1.4032 | 0.087246 | 456.4517 | 23.24 | 63.29
2021-01-01 19:00 | 1.2858 | 0.25793 | 0.081582 | 0.47694 | 19.452 |  | 1.4107 | 0.1018 | 456.9703 | 23.21 | 63.9
2021-01-01 19:05 | 1.031 | 0.24562 | 0.083665 | 0.46016 | 13.9 |  | 1.4033 | 0.10179 | 457.0508 | 23.19 | 63.6
2021-01-01 19:10 | 0.98009 | 0.22378 | 0.071112 | 0.41413 | 15.0502 |  | 1.3959 | 0.10179 | 456.6228 | 23.13 | 63.7
2021-01-01 19:15 | 0.9417 | 0.2742 | 0.083643 | 0.50395 | 5.6196 |  | 1.4029 | 0.094495 | 457.863 | 23.09 | 63.07
2021-01-01 19:20 | 0.81433 | 0.26053 | 0.10036 | 0.50179 | 18.292 |  | 1.3954 | 0.079947 | 456.3392 | 23.07 | 62.69
2021-01-01 19:25 | 0.64889 | 0.19504 | 0.079446 | 0.37632 | 29.2736 |  | 1.3881 | 0.065408 | 457.4568 | 23.06 | 62.53
2021-01-01 19:30 | 0.43258 | 0.20322 | 0.081535 | 0.39095 | 16.6112 |  | 1.3881 | 0.072674 | 457.0186 | 23 | 62.7
2021-01-01 19:35 | 0.4452 | 0.16363 | 0.077335 | 0.32815 | 4.742 |  | 1.3877 | 0.072657 | 455.6207 | 22.93 | 62.12
2021-01-01 19:40 | 0.33073 | 0.11864 | 0.060616 | 0.24247 | 11.8656 |  | 1.3805 | 0.058127 | 456.7593 | 22.88 | 62.43
2021-01-01 19:45 | 0.53425 | 0.16772 | 0.066886 | 0.32398 | 15.1522 |  | 1.3878 | 0.079923 | 457.8772 | 22.86 | 62.43
2021-01-01 19:50 | 0.8648 | 0.15815 | 0.071052 | 0.31555 | 16.7669 |  | 1.3802 | 0.079907 | 456.89 | 22.86 | 61.73
2021-01-01 19:55 | 0.63604 | 0.16637 | 0.075251 | 0.33027 | 11.4997 |  | 1.3878 | 0.065396 | 457.8197 | 22.88 | 62.56
2021-01-01 20:00 | 0.57238 | 0.1609 | 0.087783 | 0.33441 | -3.012 |  | 1.3877 | 0.058123 | 457.3743 | 22.85 | 62.31
2021-01-01 20:05 | 0.53413 | 0.15542 | 0.085679 | 0.32182 | -1.404 |  | 1.3875 | 0.065378 | 457.5273 | 22.8 | 61.91
2021-01-01 20:10 | 0.47057 | 0.16497 | 0.083594 | 0.33437 | 6.6541 |  | 1.3948 | 0.058117 | 457.0424 | 22.75 | 62.28
2021-01-01 20:15 | 0.29253 | 0.1418 | 0.077327 | 0.29468 | 14.8959 |  | 1.3876 | 0.050854 | 457.0586 | 22.73 | 62.47
2021-01-01 20:20 | 0.27986 | 0.16091 | 0.085702 | 0.33445 | 20.7401 |  | 1.3878 | 0.050863 | 455.9129 | 22.72 | 63.16
2021-01-01 20:25 | 0.26716 | 0.13228 | 0.064803 | 0.26757 | 9.6481 |  | 1.3879 | 0.036333 | 457.485 | 22.73 | 63.35
2021-01-01 20:30 | 0.29262 | 0.12957 | 0.056446 | 0.25505 | 15.8066 |  | 1.388 | 0.058137 | 456.9128 | 22.73 | 63.61
2021-01-01 20:35 | 0.41975 | 0.15954 | 0.062704 | 0.30725 | 6.6143 |  | 1.395 | 0.06539 | 456.9961 | 22.74 | 62.8
2021-01-01 20:40 | 0.63573 | 0.15266 | 0.062678 | 0.29668 | -6.3064 |  | 1.3944 | 0.065363 | 458.8017 | 22.74 | 61.33
2021-01-01 20:45 | 1.0299 | 0.15539 | 0.058503 | 0.2946 | 8.8702 |  | 1.3945 | 0.07263 | 458.2066 | 22.76 | 61.45
2021-01-01 20:50 | 1.0301 | 0.18814 | 0.056423 | 0.34481 | 4.8428 |  | 1.3947 | 0.072642 | 458.1295 | 22.76 | 62.05
2021-01-01 20:55 | 0.75036 | 0.16769 | 0.058515 | 0.31765 | 4.2529 |  | 1.3948 | 0.065381 | 456.5072 | 22.75 | 62.25
2021-01-01 21:00 | 0.61053 | 0.1459 | 0.056431 | 0.28007 | 7.6215 |  | 1.3877 | 0.050857 | 457.0279 | 22.73 | 62.71
2021-01-01 21:05 | 0.58499 | 0.15269 | 0.054332 | 0.28838 | 9.0852 |  | 1.3947 | 0.043584 | 458.2461 | 22.69 | 62.25
2021-01-01 21:10 | 0.63579 | 0.13904 | 0.054326 | 0.26745 | 3.947 |  | 1.3873 | 0.036316 | 456.2239 | 22.69 | 61.8
2021-01-01 21:15 | 0.96652 | 0.15951 | 0.050153 | 0.29465 | 6.9386 |  | 1.3875 | 0.043585 | 456.6748 | 22.71 | 62.17
2021-01-01 21:20 | 0.57227 | 0.15678 | 0.050153 | 0.28838 | 3.7236 |  | 1.3947 | 0.03632 | 456.6824 | 22.71 | 62.11
2021-01-01 21:25 | 0.45783 | 0.11179 | 0.041795 | 0.21315 | 7.3659 |  | 1.3947 | 0.029057 | 455.6582 | 22.67 | 62.33
2021-01-01 21:30 | 0.49596 | 0.13223 | 0.045972 | 0.25076 | 10.9161 |  | 1.3947 | 0.036319 | 457.3273 | 22.65 | 62.23
2021-01-01 21:35 | 0.38149 | 0.12269 | 0.033433 | 0.22149 | 14.7712 |  | 1.3946 | 0.036318 | 457.3312 | 22.66 | 62.04
2021-01-01 21:40 | 0.38145 | 0.10223 | 0.050144 | 0.20685 | 10.1823 |  | 1.3945 | 0.036314 | 456.3564 | 22.62 | 61.87
2021-01-01 21:45 | 0.35597 | 0.13492 | 0.039692 | 0.24442 | 1.312 |  | 1.4015 | 0.043571 | 458.5956 | 22.61 | 61.37
2021-01-01 21:50 | 0.29242 | 0.11994 | 0.058495 | 0.24234 | 7.6588 |  | 1.4161 | 0.043573 | 457.5466 | 22.58 | 61.62
2021-01-01 21:55 | 0.38147 | 0.11723 | 0.054326 | 0.23402 | 7.2836 |  | 1.4163 | 0.065369 | 456.9962 | 22.54 | 62.35
2021-01-01 22:00 | 0.30514 | 0.10086 | 0.054319 | 0.20892 | 3.0717 |  | 1.4234 | 0.050836 | 457.6389 | 22.51 | 62.01
2021-01-01 22:05 | 0.27974 | 0.066792 | 0.037609 | 0.13999 | 7.5479 |  | 1.4308 | 0.050841 | 457.6707 | 22.46 | 62.56
2021-01-01 22:10 | 0.34331 | 0.070879 | 0.043876 | 0.15043 | 4.8623 |  | 1.4235 | 0.05084 | 457.2216 | 22.41 | 62.65
2021-01-01 22:15 | 0.27973 | 0.070878 | 0.035518 | 0.14625 | 7.7408 |  | 1.4308 | 0.050839 | 457.2621 | 22.39 | 62.65
2021-01-01 22:20 | 0.25433 | 0.087244 | 0.04597 | 0.1797 | 3.6826 |  | 1.4309 | 0.036318 | 457.1954 | 22.4 | 63.02
2021-01-01 22:25 | 0.2416 | 0.13495 | 0.054326 | 0.26118 | 2.3906 |  | 1.4309 | 0.058106 | 457.2104 | 22.4 | 62.9
2021-01-01 22:30 | 0.22888 | 0.14449 | 0.062682 | 0.28416 | 11.5964 |  | 1.4381 | 0.065367 | 457.7355 | 22.42 | 62.69
2021-01-01 22:35 | 0.20348 | 0.13361 | 0.050154 | 0.25495 | 6.1349 |  | 1.4456 | 0.05085 | 458.2744 | 22.37 | 63.5
2021-01-01 22:40 | 0.24159 | 0.14858 | 0.052235 | 0.27789 | 6.8358 |  | 1.4454 | 0.050842 | 458.4722 | 22.29 | 63.22
2021-01-01 22:45 | 0.2289 | 0.19222 | 0.060599 | 0.35524 | 9.9089 |  | 1.4528 | 0.043583 | 458.4106 | 22.3 | 63.55
2021-01-01 22:50 | 0.24166 | 0.1268 | 0.04389 | 0.23826 | 10.1446 |  | 1.4457 | 0.04359 | 457.8541 | 22.26 | 64.34
2021-01-01 22:55 | 0.64867 | 0.17998 | 0.052249 | 0.32813 | 10.6229 |  | 1.4457 | 0.072651 | 458.4255 | 22.24 | 64.41
2021-01-01 23:00 | 0.4834 | 0.21001 | 0.041806 | 0.36371 | 14.4713 |  | 1.4532 | 0.072662 | 458.3068 | 22.27 | 64.87
2021-01-01 23:05 | 0.31805 | 0.12138 | 0.037629 | 0.22368 | 6.5545 |  | 1.4534 | 0.050868 | 459.4178 | 22.22 | 65.43
2021-01-01 23:10 | 0.20355 | 0.11183 | 0.037627 | 0.20904 | 5.8926 |  | 1.4533 | 0.050866 | 457.4896 | 22.14 | 65.51
2021-01-01 23:15 | 0.27991 | 0.13094 | 0.035542 | 0.23834 | -4.5295 |  | 1.4535 | 0.05814 | 457.9857 | 22.13 | 66.02
2021-01-01 23:20 | 0.78886 | 0.10503 | 0.041815 | 0.2028 | -1.8526 |  | 1.4681 | 0.13809 | 458.0331 | 22.09 | 66.3
2021-01-01 23:25 | 0.43259 | 0.079107 | 0.029269 | 0.15053 | 7.9392 |  | 1.4753 | 0.10901 | 458.0983 | 22.06 | 66.27
2021-01-01 23:30 | 0.35625 | 0.046373 | 0.029269 | 0.10035 | 2.1782 |  | 1.468 | 0.10174 | 457.6335 | 22.01 | 66.5
2021-01-01 23:35 | 0.38171 | 0.053195 | 0.027179 | 0.10663 | -8.8556 |  | 1.4753 | 0.11628 | 457.6835 | 21.97 | 66.76
2021-01-01 23:40 | 0.39444 | 0.05456 | 0.041816 | 0.12336 | 9.9654 |  | 1.4754 | 0.065411 | 458.1599 | 22 | 66.77
2021-01-01 23:45 | 0.35629 | 0.04365 | 0.029272 | 0.096181 | -2.382 |  | 1.4682 | 0.058146 | 457.6168 | 21.99 | 66.97
2021-01-01 23:50 |  | 0.058657 | 0.035546 | 0.12546 | -3.1049 |  | 1.4755 | 0.043611 | 459.2793 | 21.95 | 67.27
2021-01-01 23:55 | 0.29269 | 0.090035 | 0.041821 | 0.17983 | 12.7662 |  | 1.4756 | 0.036344 | 457.6594 | 21.94 | 67.46
2021-01-02 | 0.3436 | 0.17871 | 0.071099 | 0.34504 | 1.0995 |  | 1.4756 | 0.036346 | 457.5471 | 22 | 67.37
2021-01-02 00:05 | 0.31812 | 0.11185 | 0.031364 | 0.20282 | -1.5066 |  | 1.4755 | 0.029073 | 457.0584 | 22 | 66.96
2021-01-02 00:10 | 0.30538 | 0.076385 | 0.037635 | 0.15681 | 3.4406 |  | 1.4754 | 0.029072 | 457.1548 | 21.95 | 67.01
2021-01-02 00:15 | 0.20356 | 0.10502 | 0.03763 | 0.1986 | -5.8015 |  | 1.468 | 0.021801 | 457.8414 | 21.89 | 66.81
2021-01-02 00:20 | 0.22897 | 0.096818 | 0.043895 | 0.19439 | -0.35617 |  | 1.4605 | 0.021798 | 458.0105 | 21.83 | 66.43
2021-01-02 00:25 | 0.20353 | 0.088636 | 0.035534 | 0.1714 | -0.52917 |  | 1.4604 | 0.021798 | 458.0898 | 21.78 | 66.62
2021-01-02 00:30 | 0.16535 | 0.064084 | 0.03762 | 0.13585 | 1.6077 |  | 1.453 | 0.021795 | 458.1683 | 21.76 | 66.31
2021-01-02 00:35 | 0.17805 | 0.084529 | 0.035527 | 0.1651 | 3.8459 |  | 1.4456 | 0.021794 | 456.588 | 21.76 | 65.99
2021-01-02 00:40 | 0.17805 | 0.058625 | 0.033437 | 0.1233 | -2.7573 |  | 1.4456 | 0.014529 | 458.7948 | 21.73 | 66.1
2021-01-02 00:45 | 0.22889 | 0.064068 | 0.033431 | 0.13164 | -0.77312 |  | 1.4381 | 0.014527 | 457.8702 | 21.68 | 65.66
2021-01-02 00:50 | 0.21618 | 0.096786 | 0.041791 | 0.19015 | 5.4019 |  | 1.4309 | 0.014527 | 457.9523 | 21.67 | 65.77
2021-01-02 00:55 | 0.15259 | 0.064066 | 0.031341 | 0.12745 | -2.9297 |  | 1.4236 | 0.014526 | 458.5806 | 21.63 | 65.71
2021-01-02 01:00 | 0.13985 | 0.042251 | 0.029248 | 0.094011 | 3.0005 |  | 1.4161 | 0.0072622 | 457.6093 | 21.6 | 65.32
2021-01-02 01:05 |  |  |  |  | -3.8348 |  |  |  | 457.0708 | 21.58 | 65.65
2021-01-02 01:10 |  |  |  |  | -4.9943 |  |  |  | 459.8039 | 21.56 | 65.7
2021-01-02 01:15 |  |  |  |  | 0.80346 |  |  |  | 457.2093 | 21.53 | 65.34
2021-01-02 01:20 |  |  |  |  | -0.16271 |  |  |  | 458.3499 | 21.52 | 65
2021-01-02 01:25 |  |  |  |  | -5.7748 |  |  |  | 458.4812 | 21.51 | 64.07
2021-01-02 01:30 |  |  |  |  | 3.0195 |  |  |  | 457.9543 | 21.51 | 63.96
2021-01-02 01:35 |  |  |  |  | -7.0462 |  |  |  | 458.9507 | 21.53 | 64.32
2021-01-02 01:40 |  |  |  |  | 2.0233 |  |  |  | 459.5313 | 21.52 | 64.15
2021-01-02 01:45 | 0.50842 | 0.1199 | 0.037594 | 0.22139 | 2.8065 |  | 1.4811 | -0.058081 | 458.3214 | 21.57 | 64.39
2021-01-02 01:50 | 0.33054 | 0.12674 | 0.050136 | 0.24441 | 2.0951 |  | 1.4451 | -0.050832 | 457.6262 | 21.61 | 65.01
2021-01-02 01:55 | 0.33058 | 0.1104 | 0.050143 | 0.21937 | 7.3237 |  | 1.4235 | -0.0072626 | 457.5172 | 21.64 | 65.41
2021-01-02 02:00 | 0.27975 | 0.077699 | 0.0397 | 0.1588 | 1.5564 |  | 1.4091 | 0.0072633 | 457.5074 | 21.62 | 65.83
2021-01-02 02:05 | 0.30519 | 0.13768 | 0.035522 | 0.24656 | 0.81383 |  | 1.4091 | 0.014527 | 458.5924 | 21.61 | 65.95
2021-01-02 02:10 | 0.22888 | 0.11041 | 0.039699 | 0.21103 | 1.6378 |  | 1.4018 | 0.02179 | 458.0386 | 21.63 | 65.73
2021-01-02 02:15 | 0.15257 | 0.061333 | 0.033427 | 0.12744 | -4.7093 |  | 1.3944 | 0.029049 | 457.6827 | 21.6 | 65.33
2021-01-02 02:20 | 0.19071 | 0.044977 | 0.033426 | 0.10237 | -4.6177 |  | 1.4016 | 0.014524 | 457.1818 | 21.58 | 65.35
2021-01-02 02:25 | 0.1907 | 0.046338 | 0.039693 | 0.11072 | -1.4443 |  | 1.4016 | 0.021786 | 458.29 | 21.57 | 65.27
2021-01-02 02:30 | 0.17799 | 0.049065 | 0.037604 | 0.11281 | 1.0374 |  | 1.3943 | 0.029048 | 456.6654 | 21.57 | 65.33
2021-01-02 02:35 | 0.25427 | 0.046337 | 0.033425 | 0.10445 | 3.2139 |  | 1.4015 | 0.029047 | 457.2356 | 21.56 | 65.24
2021-01-02 02:40 | 0.24152 | 0.06541 | 0.045953 | 0.14413 | 5.6949 |  | 1.4086 | 0.07987 | 457.8144 | 21.57 | 64.74
2021-01-02 02:45 | 0.25425 | 0.0586 | 0.0188 | 0.10862 | 13.8923 |  | 1.4087 | 0.058091 | 457.1988 | 21.6 | 64.87
2021-01-02 02:50 | 0.36874 | 0.092689 | 0.043877 | 0.18386 | 7.7614 |  | 1.4163 | 0.058103 | 456.503 | 21.64 | 65.5
2021-01-02 02:55 | 0.27974 | 0.077697 | 0.033431 | 0.15462 | 3.1229 |  | 1.4236 | 0.050842 | 456.4624 | 21.66 | 65.5
2021-01-02 03:00 | [9 empty] | 21.62 | 65.49
2021-01-02 03:05 | 0.30511 | 0.08177 | 0.043869 | 0.16921 | -0.1017 |  | 1.4451 | 0.065355 | 457.2308 | 21.57 | 65.11
2021-01-02 03:10 | 0.29235 | 0.098106 | 0.039684 | 0.19215 | 14.6326 |  | 1.4593 | 0.058083 | 457.8515 | 21.57 | 64.43
2021-01-02 03:15 | 0.27969 | 0.10494 | 0.037602 | 0.19846 | 19.0594 |  | 1.4669 | 0.04357 | 456.0895 | 21.61 | 64.96
2021-01-02 03:20 | 0.19069 | 0.1063 | 0.039689 | 0.20054 | 10.6582 |  | 1.4813 | 0.05083 | 457.1238 | 21.65 | 64.65
2021-01-02 03:25 | 0.19069 | 0.062689 | 0.029246 | 0.12534 | 10.3025 |  | 1.4959 | 0.043569 | 457.1285 | 21.64 | 64.78
2021-01-02 03:30 | 0.21614 | 0.076326 | 0.041784 | 0.15878 | 7.3844 |  | 1.5033 | 0.043574 | 456.5533 | 21.63 | 65.25
2021-01-02 03:35 | 0.20339 | 0.099478 | 0.033421 | 0.1859 | 1.739 |  | 1.5176 | 0.050827 | 459.3663 | 21.61 | 64.61
2021-01-02 03:40 | 0.20338 | 0.096749 | 0.039686 | 0.18799 | 10.0573 |  | 1.5248 | 0.050825 | 456.7157 | 21.59 | 64.57
2021-01-02 03:45 | 0.25424 | 0.11719 | 0.043865 | 0.2235 | 4.261 |  | 1.5466 | 0.065349 | 457.2536 | 21.58 | 64.75
2021-01-02 03:50 | 0.26692 | 0.16351 | 0.060569 | 0.3112 | 8.5618 |  | 1.5537 | 0.065342 | 457.7659 | 21.63 | 64.13
2021-01-02 03:55 | 0.24152 | 0.19077 | 0.08355 | 0.37598 | 12.8335 |  | 1.5611 | 0.058086 | 457.129 | 21.67 | 64.27
2021-01-02 04:00 | 0.25424 | 0.26709 | 0.10026 | 0.50967 | 7.739 |  | 1.5684 | 0.058088 | 457.5444 | 21.74 | 64.12
2021-01-02 04:05 | 0.20334 | 0.1485 | 0.071004 | 0.29863 | 12.6785 |  | 1.5753 | 0.058075 | 456.0784 | 21.71 | 63.37
2021-01-02 04:10 | 0.24147 | 0.22207 | 0.062651 | 0.40097 | 10.269 |  | 1.5898 | 0.065335 | 457.2286 | 21.66 | 63.61
2021-01-02 04:15 | 0.22876 | 0.28065 | 0.064738 | 0.49702 | 4.5955 |  | 1.597 | 0.065333 | 457.703 | 21.71 | 63.31
2021-01-02 04:20 | 0.36854 | 0.2929 | 0.058471 | 0.50744 | 7.076 |  | 1.6115 | 0.079849 | 457.1336 | 21.74 | 63.06
2021-01-02 04:25 | 0.31769 | 0.23567 | 0.070996 | 0.43224 | 1.8706 |  | 1.6259 | 0.087103 | 456.6211 | 21.74 | 62.84
2021-01-02 04:30 | 0.26686 | 0.23022 | 0.062643 | 0.41345 | 10.3897 |  | 1.6332 | 0.079844 | 456.6058 | 21.75 | 62.8
2021-01-02 04:35 | 0.33046 | 0.19075 | 0.062656 | 0.35296 | 19.4923 |  | 1.6408 | 0.0726 | 456.5459 | 21.73 | 63.63
2021-01-02 04:40 | 0.36862 | 0.16624 | 0.054305 | 0.30912 | 7.4028 |  | 1.6554 | 0.072605 | 456.5501 | 21.71 | 63.93
2021-01-02 04:45 | 0.39403 | 0.14852 | 0.054304 | 0.28196 | 6.9247 |  | 1.6699 | 0.058082 | 457.6865 | 21.68 | 63.95
2021-01-02 04:50 | 0.61017 | 0.139 | 0.050131 | 0.2611 | 9.6508 |  | 1.6773 | 0.065349 | 457.687 | 21.65 | 64.45
2021-01-02 04:55 | 0.33053 | 0.12538 | 0.052224 | 0.24441 | 5.0241 |  | 1.6847 | 0.058092 | 457.1297 | 21.64 | 64.77
2021-01-02 05:00 | 0.29239 | 0.1172 | 0.058491 | 0.23814 | 10.9127 |  | 1.6919 | 0.058092 | 457.0976 | 21.66 | 64.7
2021-01-02 05:05 | 0.27971 | 0.15129 | 0.043872 | 0.27577 | 13.0598 |  | 1.6921 | 0.06536 | 456.5022 | 21.67 | 65
2021-01-02 05:10 | 0.33056 | 0.19762 | 0.064763 | 0.36769 | 4.7905 |  | 1.6921 | 0.065359 | 457.0484 | 21.67 | 64.94
2021-01-02 05:15 | 0.30512 | 0.18808 | 0.058494 | 0.34678 | 15.3069 |  | 1.7065 | 0.065357 | 458.1254 | 21.68 | 64.78
2021-01-02 05:20 | 0.69931 | 0.16084 | 0.054322 | 0.30086 | 9.6734 |  | 1.714 | 0.07989 | 457.5333 | 21.68 | 65.22
2021-01-02 05:25 | 0.7375 | 0.15539 | 0.045967 | 0.28625 | 9.7045 |  | 1.7141 | 0.079895 | 457.5211 | 21.67 | 65.49
2021-01-02 05:30 | 0.80115 | 0.19085 | 0.05015 | 0.34269 | 16.6639 |  | 1.7215 | 0.079901 | 456.8828 | 21.71 | 65.64
2021-01-02 05:35 | 0.8649 | 0.16498 | 0.03762 | 0.29051 | 12.4647 |  | 1.7218 | 0.079917 | 456.7325 | 21.75 | 66.21
2021-01-02 05:40 | 0.71224 | 0.16497 | 0.043888 | 0.29677 | 13.2883 |  | 1.729 | 0.072648 | 456.2611 | 21.72 | 66.16
2021-01-02 05:45 | 0.63591 | 0.17042 | 0.050157 | 0.31139 | 16.1776 |  | 1.729 | 0.065382 | 456.2707 | 21.72 | 66.08
2021-01-02 05:50 | 0.57233 | 0.21542 | 0.083596 | 0.4138 | 10.7039 |  | 1.7218 | 0.087178 | 456.7208 | 21.77 | 65.97
2021-01-02 05:55 | 1.1828 | 0.1936 | 0.077324 | 0.37408 | 19.0567 |  | 1.7217 | 0.1017 | 458.72 | 21.83 | 65.64
2021-01-02 06:00 | 0.89035 | 0.17726 | 0.058521 | 0.32814 | 8.2218 |  | 1.7219 | 0.065387 | 455.3779 | 21.87 | 65.86
2021-01-02 06:05 | 0.95393 | 0.29997 | 0.098229 | 0.55803 | 13.9807 |  | 1.7218 | 0.079916 | 456.4821 | 21.86 | 65.81
2021-01-02 06:10 | 0.83948 | 0.40496 | 0.079422 | 0.70016 | 14.3372 |  | 1.7219 | 0.072653 | 458.0712 | 21.87 | 65.87
2021-01-02 06:15 | 0.7633 | 0.40231 | 0.081527 | 0.6982 | 6.8901 |  | 1.7222 | 0.0654 | 455.8007 | 21.89 | 66.48
2021-01-02 06:20 | 0.69974 | 0.5019 | 0.094076 | 0.86341 | 15.9388 |  | 1.7223 | 0.065404 | 455.6927 | 21.94 | 66.53
2021-01-02 06:25 | 0.6616 | 0.40645 | 0.087808 | 0.70873 | 15.7054 |  | 1.7151 | 0.058139 | 456.1354 | 21.99 | 66.48
2021-01-02 06:30 | 0.72524 | 0.4351 | 0.12963 | 0.79657 | 15.9604 |  | 1.7152 | 0.087212 | 456.0419 | 22.04 | 66.41
2021-01-02 06:35 | 0.83964 | 0.42686 | 0.12752 | 0.78182 | 25.7386 |  | 1.7149 | 0.10173 | 456.5822 | 22.08 | 65.73
2021-01-02 06:40 | 0.92877 | 0.4269 | 0.094078 | 0.74845 | 24.031 |  | 1.7224 | 0.11628 | 455.4173 | 22.11 | 65.95
2021-01-02 06:45 | 0.69971 | 0.41868 | 0.11079 | 0.75466 | 15.877 |  | 1.7295 | 0.094468 | 457.1133 | 22.08 | 65.79
2021-01-02 06:50 | 0.7505 | 0.42954 | 0.10033 | 0.76083 | 23.4461 |  | 1.7365 | 0.094456 | 455.5867 | 22.06 | 65.4
2021-01-02 06:55 | 0.67423 | 0.38866 | 0.10452 | 0.70027 | 21.7789 |  | 1.7367 | 0.065398 | 457.1045 | 22.1 | 65.53
2021-01-02 07:00 | 0.52157 | 0.2932 | 0.083614 | 0.53513 | 23.2849 |  | 1.7439 | 0.065397 | 456.6007 | 22.08 | 65.58
2021-01-02 07:05 | 0.72527 | 0.29054 | 0.085723 | 0.53107 | 21.4781 |  | 1.7588 | 0.065412 | 457.0392 | 22.08 | 66.39
2021-01-02 07:10 | 0.8909 | 0.32062 | 0.09411 | 0.58557 | 9.8355 |  | 1.7665 | 0.079967 | 455.7884 | 22.12 | 67.14
2021-01-02 07:15 | 0.75093 | 0.29335 | 0.07529 | 0.52494 | 18.5518 |  | 1.7666 | 0.09451 | 456.8174 | 22.14 | 67.19
2021-01-02 07:20 | 0.76374 | 0.35478 | 0.069024 | 0.61285 | 14.1547 |  | 1.7668 | 0.10906 | 456.213 | 22.15 | 67.56
2021-01-02 07:25 | 0.76382 | 0.41214 | 0.052296 | 0.68403 | 4.1755 |  | 1.767 | 0.10907 | 456.6583 | 22.18 | 67.81
2021-01-02 07:30 | 0.85302 | 0.31255 | 0.08159 | 0.56067 | 12.5279 |  | 1.7672 | 0.10181 | 457.0562 | 22.24 | 67.94
2021-01-02 07:35 | 0.78947 | 0.34671 | 0.092063 | 0.62352 | 9.1884 |  | 1.7601 | 0.080006 | 454.2446 | 22.28 | 68.27
2021-01-02 07:40 | 1.2602 | 0.38208 | 0.089942 | 0.67561 | 15.4584 |  | 1.7596 | 0.10179 | 456.511 | 22.3 | 67.01
2021-01-02 07:45 | 1.5275 | 0.35205 | 0.094122 | 0.63375 | 22.8507 |  | 1.745 | 0.087248 | 457.0041 | 22.34 | 66.71
2021-01-02 07:50 | 1.3747 | 0.38615 | 0.11085 | 0.70066 | 16.2923 |  | 1.7304 | 0.094515 | 456.9583 | 22.38 | 66.42
2021-01-02 07:55 | 1.1073 | 0.36566 | 0.096205 | 0.65879 | 19.4275 |  | 1.723 | 0.11632 | 454.7701 | 22.42 | 66.07
2021-01-02 08:00 | 0.8273 | 0.40114 | 0.10666 | 0.72154 | 26.4533 |  | 1.7157 | 0.10905 | 455.7963 | 22.45 | 65.97
2021-01-02 08:05 | 0.78903 | 0.41883 | 0.11501 | 0.75492 | 11.7489 |  | 1.7155 | 0.079962 | 455.2809 | 22.47 | 65.47
2021-01-02 08:10 | 0.67446 | 0.41062 | 0.1171 | 0.74651 | 23.5169 |  | 1.7082 | 0.072689 | 454.1671 | 22.51 | 65.13
2021-01-02 08:15 | 0.77631 | 0.38882 | 0.12338 | 0.71937 | 20.0568 |  | 1.7083 | 0.072693 | 455.1364 | 22.56 | 65.16
2021-01-02 08:20 | 1.069 | 0.34652 | 0.098285 | 0.62944 | 20.9321 |  | 1.701 | 0.079962 | 455.1427 | 22.56 | 65.11
2021-01-02 08:25 | 1.5527 | 0.33562 | 0.11084 | 0.62739 | 23.1223 |  | 1.6938 | 0.10177 | 455.0726 | 22.59 | 65.18
2021-01-02 08:30 | 2.0235 | 0.38882 | 0.10874 | 0.70473 | 17.8983 |  | 1.6865 | 0.11631 | 455.0317 | 22.63 | 64.86
2021-01-02 08:35 | 1.8328 | 0.38886 | 0.096206 | 0.69227 | 25.9139 |  | 1.6867 | 0.11632 | 453.8416 | 22.67 | 65.13
2021-01-02 08:40 | 1.2474 | 0.30703 | 0.083666 | 0.55219 | 26.8125 |  | 1.6796 | 0.079979 | 454.32 | 22.68 | 65.43
2021-01-02 08:45 | 1.2219 | 0.37386 | 0.13385 | 0.70692 | 21.0979 |  | 1.6722 | 0.072702 | 454.88 | 22.69 | 65.09
2021-01-02 08:50 | 1.082 | 0.4585 | 0.14642 | 0.84923 | 28.7786 |  | 1.6723 | 0.079981 | 453.6951 | 22.73 | 65.32
2021-01-02 08:55 | 1.3239 | 0.50902 | 0.15061 | 0.93085 | 19.6042 |  | 1.6579 | 0.087257 | 454.7306 | 22.74 | 65.46
2021-01-02 09:00 | 1.5274 | 0.51168 | 0.1234 | 0.90981 | 19.5202 |  | 1.6359 | 0.087245 | 455.8174 | 22.77 | 64.88
2021-01-02 09:05 | 1.6297 | 0.46541 | 0.11088 | 0.82428 | 27.7654 |  | 1.629 | 0.10181 | 453.4579 | 22.83 | 65.58
2021-01-02 09:10 | 1.9484 | 0.47508 | 0.12765 | 0.85586 | 15.9643 |  | 1.6221 | 0.12366 | 453.8419 | 22.86 | 66.29
2021-01-02 09:15 | 2.2671 | 0.53932 | 0.1465 | 0.97319 | 29.1719 |  | 1.6151 | 0.12368 | 453.7148 | 22.9 | 66.64
2021-01-02 09:20 | 1.7581 | 0.53262 | 0.16119 | 0.97551 | 33.7751 |  | 1.6009 | 0.11643 | 452.9652 | 22.97 | 67.18
2021-01-02 09:25 | 1.7709 | 0.55724 | 0.15073 | 1.0049 | 26.1639 |  | 1.6083 | 0.14555 | 454.0036 | 22.97 | 67.44
2021-01-02 09:30 | 1.8218 | 0.49166 | 0.1256 | 0.87923 | 37.078 |  | 1.6009 | 0.12371 | 452.4878 | 22.98 | 67.15
2021-01-02 09:35 | 2.0257 | 0.49304 | 0.13189 | 0.88974 | 33.7365 |  | 1.601 | 0.12371 | 450.8326 | 23 | 67.21
2021-01-02 09:40 | 1.7455 | 0.50944 | 0.1298 | 0.9086 | 28.5799 |  | 1.5792 | 0.080052 | 452.3351 | 23.06 | 67.06
2021-01-02 09:45 | 1.567 | 0.52307 | 0.12979 | 0.93157 | 23.2173 |  | 1.55 | 0.087325 | 452.8518 | 23.09 | 66.73
2021-01-02 09:50 | 1.7961 | 0.62814 | 0.13396 | 1.0947 | 15.092 |  | 1.5352 | 0.10186 | 452.8584 | 23.13 | 66.05
2021-01-02 09:55 | 1.847 | 0.59671 | 0.14442 | 1.0612 | 31.8949 |  | 1.5133 | 0.13096 | 451.7272 | 23.18 | 65.73
2021-01-02 10:00 | 2.0128 | 0.46843 | 0.14235 | 0.85827 | 37.9942 |  | 1.4917 | 0.14554 | 452.6546 | 23.23 | 66.04
2021-01-02 10:05 | 1.7959 | 0.48199 | 0.16744 | 0.90625 | 26.33 |  | 1.4624 | 0.12368 | 451.6558 | 23.24 | 65.34
2021-01-02 10:10 | 2.2288 | 0.57207 | 0.18417 | 1.0611 | 24.2396 |  | 1.4477 | 0.16005 | 453.2584 | 23.26 | 65.05
2021-01-02 10:15 | 2.3311 | 0.57763 | 0.17164 | 1.055 | 24.2742 |  | 1.4334 | 0.1819 | 452.5874 | 23.3 | 65.46
2021-01-02 10:20 | 2.5351 | 0.63229 | 0.18002 | 1.1492 | 29.7589 |  | 1.4335 | 0.18919 | 454.1301 | 23.32 | 65.62
2021-01-02 10:25 | 2.5229 | 0.62286 | 0.21566 | 1.1683 | 33.8321 |  | 1.4265 | 0.16012 | 450.783 | 23.35 | 66.2
2021-01-02 10:30 | 2.1789 | 0.70755 | 0.21356 | 1.2981 | 21.8549 |  | 1.4192 | 0.16012 | 449.132 | 23.38 | 66.09
2021-01-02 10:35 | 2.1533 | 0.7608 | 0.20309 | 1.3693 | 29.54 |  | 1.4338 | 0.15284 | 449.5878 | 23.44 | 65.76
2021-01-02 10:40 | 2.4342 | 0.81427 | 0.23665 | 1.4848 | 27.9567 |  | 1.4268 | 0.16015 | 450.4242 | 23.52 | 66.28
2021-01-02 10:45 | 2.0649 | 0.70095 | 0.19897 | 1.2755 | 36.9943 |  | 1.4124 | 0.13105 | 450.3129 | 23.56 | 66.5
2021-01-02 10:50 | 1.7973 | 0.63951 | 0.21574 | 1.196 | 36.6906 |  | 1.398 | 0.12378 | 451.3087 | 23.59 | 66.58
2021-01-02 10:55 | 2.5231 | 0.60378 | 0.23033 | 1.1579 | 27.4632 |  | 1.3975 | 0.1019 | 451.4244 | 23.61 | 65.41
2021-01-02 11:00 | 3.0576 | 0.6173 | 0.23446 | 1.1807 | 20.9749 |  | 1.3899 | 0.10916 | 449.8632 | 23.65 | 64.49
2021-01-02 11:05 | 3.2489 | 0.64057 | 0.20517 | 1.1871 | 26.6438 |  | 1.39 | 0.131 | 450.2835 | 23.7 | 64.58
2021-01-02 11:10 | 2.7135 | 0.75522 | 0.19678 | 1.3544 | 31.6348 |  | 1.3753 | 0.13826 | 449.2199 | 23.73 | 64.09
2021-01-02 11:15 | 2.5738 | 0.80587 | 0.21356 | 1.4488 | 39.1826 |  | 1.3828 | 0.131 | 449.563 | 23.81 | 64.3
2021-01-02 11:20 | 2.0001 | 0.65008 | 0.21771 | 1.2142 | 31.0749 |  | 1.3753 | 0.15282 | 450.0967 | 23.85 | 63.7
2021-01-02 11:25 | 2.102 | 0.58315 | 0.18422 | 1.076 | 29.933 |  | 1.3753 | 0.20375 | 450.1257 | 23.89 | 63.44
2021-01-02 11:30 | 2.7774 | 0.76892 | 0.20307 | 1.3817 | 28.3955 |  | 1.3827 | 0.33475 | 450.0118 | 23.95 | 63.38
2021-01-02 11:35 | 2.5609 | 0.82085 | 0.22192 | 1.4801 | 30.3943 |  | 1.39 | 0.24744 | 449.3866 | 24 | 63.31
2021-01-02 11:40 | 2.5485 | 0.75813 | 0.21567 | 1.3778 | 38.2785 |  | 1.4048 | 0.23291 | 448.7462 | 24.03 | 63.65
2021-01-02 11:45 | 2.8412 | 0.73755 | 0.21564 | 1.3462 | 50.0874 |  | 1.4046 | 0.16011 | 448.7388 | 24.07 | 63.11
2021-01-02 11:50 | 3.8729 | 0.78666 | 0.26377 | 1.4696 | 40.9513 |  | 1.3972 | 0.1892 | 449.7812 | 24.11 | 62.69
2021-01-02 11:55 | 3.6822 | 0.76078 | 0.23449 | 1.4006 | 36.8475 |  | 1.3901 | 0.18194 | 448.0486 | 24.17 | 62.78
2021-01-02 12:00 | 3.2868 | 0.75932 | 0.22399 | 1.3879 | 36.1601 |  | 1.3753 | 0.18192 | 447.5107 | 24.21 | 62.23
2021-01-02 12:05 | 2.7774 | 0.87954 | 0.23656 | 1.5848 | 31.8402 |  | 1.3754 | 0.18921 | 447.4459 | 24.24 | 62.26
2021-01-02 12:10 | 3.0454 | 0.81686 | 0.21776 | 1.472 | 31.8052 |  | 1.3756 | 0.18196 | 448.3706 | 24.28 | 62.69
2021-01-02 12:15 | 3.6186 | 0.8933 | 0.21774 | 1.587 | 41.4969 |  | 1.3755 | 0.21834 | 448.385 | 24.29 | 62.44
2021-01-02 12:20 | 3.6447 | 0.91258 | 0.23663 | 1.6355 | 40.8005 |  | 1.3831 | 0.21838 | 447.7013 | 24.34 | 62.8
2021-01-02 12:25 | 3.428 | 0.82513 | 0.19056 | 1.4554 | 48.3339 |  | 1.3903 | 0.20382 | 447.2293 | 24.36 | 62.62
2021-01-02 12:30 | 2.6889 | 0.69262 | 0.20103 | 1.2627 | 53.7681 |  | 1.3685 | 0.16014 | 448.7924 | 24.38 | 62.56
2021-01-02 12:35 | 2.5488 | 0.71998 | 0.24292 | 1.3465 | 48.5503 |  | 1.3685 | 0.16743 | 446.662 | 24.37 | 62.73
2021-01-02 12:40 | 2.2937 | 0.60787 | 0.23032 | 1.1621 | 46.6988 |  | 1.3684 | 0.16741 | 447.7841 | 24.37 | 62.31
2021-01-02 12:45 | 2.2553 | 0.57231 | 0.21356 | 1.0887 | 37.8986 |  | 1.3683 | 0.16739 | 447.8322 | 24.36 | 62.11
2021-01-02 12:50 | 1.8856 | 0.63508 | 0.17376 | 1.1472 | 23.2076 |  | 1.3681 | 0.14554 | 447.3477 | 24.36 | 61.77
2021-01-02 12:55 | 1.8859 | 0.68847 | 0.17798 | 1.2333 | 17.7174 |  | 1.3757 | 0.14557 | 446.7162 | 24.37 | 62.34
2021-01-02 13:00 | 2.3198 | 0.72828 | 0.17593 | 1.2923 | 22.2394 |  | 1.3833 | 0.13833 | 447.0814 | 24.4 | 63.1
2021-01-02 13:05 | 2.7791 | 0.69696 | 0.17387 | 1.2443 | 31.1155 |  | 1.3835 | 0.28399 | 447.5445 | 24.4 | 63.59
2021-01-02 13:10 | 3.7098 | 0.77489 | 0.19482 | 1.3826 | 25.844 |  | 1.3836 | 0.34225 | 449.1046 | 24.41 | 63.69
2021-01-02 13:15 | 3.4802 | 0.76529 | 0.18853 | 1.3637 | 26.118 |  | 1.3835 | 0.34224 | 449.1729 | 24.38 | 63.64
2021-01-02 13:20 | 2.4351 | 0.61502 | 0.18645 | 1.1271 | 17.9305 |  | 1.3836 | 0.26217 | 447.0317 | 24.36 | 64.04
2021-01-02 13:25 | 1.9003 | 0.48261 | 0.1907 | 0.93046 | 19.2117 |  | 1.3768 | 0.13113 | 449.011 | 24.36 | 65.09
2021-01-02 13:30 | 1.8496 | 0.52782 | 0.20751 | 1.0166 | 18.7663 |  | 1.3698 | 0.11658 | 447.8796 | 24.35 | 65.73
2021-01-02 13:35 | 2.2323 | 0.72063 | 0.20541 | 1.31 | 25.9094 |  | 1.3698 | 0.13115 | 445.7571 | 24.35 | 65.71
2021-01-02 13:40 | 3.2918 | 0.78782 | 0.22014 | 1.4277 | 39.3177 |  | 1.3847 | 0.17491 | 447.7271 | 24.38 | 66.38
2021-01-02 13:45 | 3.305 | 0.6744 | 0.22227 | 1.256 | 41.2021 |  | 1.3776 | 0.16036 | 448.2047 | 24.37 | 66.91
2021-01-02 13:50 | 3.0116 | 0.57866 | 0.21179 | 1.0967 | 34.1791 |  | 1.3703 | 0.16036 | 447.6969 | 24.35 | 67.04
2021-01-02 13:55 | 2.6928 | 0.50757 | 0.19293 | 0.97306 | 24.3199 |  | 1.3705 | 0.1458 | 448.2121 | 24.33 | 67.45
2021-01-02 14:00 | 2.1313 | 0.50894 | 0.18874 | 0.96887 | 8.1577 |  | 1.3778 | 0.11664 | 447.7236 | 24.3 | 67.59
2021-01-02 14:05 | 2.8081 | 0.613 | 0.22442 | 1.164 | 18.8498 |  | 1.378 | 0.13852 | 448.199 | 24.3 | 67.99
2021-01-02 14:10 | 3.3068 | 0.59948 | 0.22658 | 1.1455 | 17.7212 |  | 1.3783 | 0.16773 | 448.0765 | 24.3 | 68.87
2021-01-02 14:15 | 3.1922 | 0.69536 | 0.24549 | 1.3114 | 30.1549 |  | 1.3712 | 0.16046 | 448.0583 | 24.28 | 69.3
2021-01-02 14:20 | 2.669 | 0.66807 | 0.21404 | 1.236 | 18.7675 |  | 1.3641 | 0.15318 | 448.5321 | 24.28 | 69.71
2021-01-02 14:25 | 2.5415 | 0.59144 | 0.20566 | 1.1122 | 20.9651 |  | 1.3641 | 0.1386 | 446.962 | 24.25 | 70
2021-01-02 14:30 | 2.1965 | 0.55992 | 0.18047 | 1.0387 | 31.6606 |  | 1.3641 | 0.16048 | 447.529 | 24.24 | 69.89
2021-01-02 14:35 | 1.8897 | 0.64468 | 0.20141 | 1.1896 | 25.516 |  | 1.3638 | 0.15316 | 448.2375 | 24.23 | 69.28
2021-01-02 14:40 | 2.4899 | 0.74875 | 0.20562 | 1.3533 | 32.0653 |  | 1.3566 | 0.19693 | 446.577 | 24.26 | 69.33
2021-01-02 14:45 | 2.9254 | 0.85727 | 0.21411 | 1.5282 | 19.3153 |  | 1.3645 | 0.20431 | 448.951 | 24.31 | 70.57
2021-01-02 14:50 | 2.5937 | 0.82045 | 0.18686 | 1.4445 | 24.8284 |  | 1.3794 | 0.19705 | 446.7306 | 24.32 | 71.14
2021-01-02 14:55 | 2.7591 | 0.6655 | 0.18051 | 1.2006 | 32.8337 |  | 1.379 | 0.18241 | 448.4671 | 24.3 | 70.39
2021-01-02 15:00 | 3.7425 | 0.597 | 0.1742 | 1.0893 | 21.3767 |  | 1.3789 | 0.1751 | 447.9369 | 24.32 | 70.09
2021-01-02 15:05 | 4.6994 | 0.67216 | 0.18676 | 1.2171 | 33.1409 |  | 1.3786 | 0.22612 | 446.4301 | 24.33 | 69.34
2021-01-02 15:10 | 4.4574 | 0.61749 | 0.17209 | 1.1186 | 26.0853 |  | 1.3788 | 0.22615 | 446.3218 | 24.36 | 69.67
2021-01-02 15:15 | 3.0645 | 0.51193 | 0.15736 | 0.94206 | 25.7414 |  | 1.3566 | 0.15316 | 446.9842 | 24.35 | 68.87
2021-01-02 15:20 | 2.4507 | 0.5008 | 0.16569 | 0.93544 | 20.2183 |  | 1.3561 | 0.14582 | 447.6419 | 24.37 | 67.66
2021-01-02 15:25 | 2.0805 | 0.51175 | 0.15311 | 0.93753 | 27.989 |  | 1.3561 | 0.14582 | 447.0376 | 24.42 | 67.45
2021-01-02 15:30 | 2.1446 | 0.48991 | 0.15103 | 0.90198 | 38.4192 |  | 1.3563 | 0.175 | 448.0296 | 24.43 | 67.79
2021-01-02 15:35 | [9 empty] | 24.43 | 67.58
2021-01-02 15:40 | 2.8852 | 0.57205 | 0.15314 | 1.0279 | 29.3931 |  | 1.3563 | 0.18959 | 446.4662 | 24.45 | 67.82
2021-01-02 15:45 | 3.0127 | 0.55697 | 0.15103 | 1.0048 | 19.0053 |  | 1.349 | 0.21146 | 446.4915 | 24.45 | 67.64
2021-01-02 15:50 | 2.553 | 0.60621 | 0.20137 | 1.1306 | 28.5939 |  | 1.3489 | 0.1677 | 445.4312 | 24.46 | 67.5
2021-01-02 15:55 | 2.0167 | 0.6171 | 0.22652 | 1.1724 | 28.2135 |  | 1.3415 | 0.13123 | 445.9714 | 24.48 | 67.13
2021-01-02 16:00 | 1.9784 | 0.50628 | 0.19086 | 0.9669 | 30.736 |  | 1.3415 | 0.13853 | 445.9372 | 24.5 | 67.08
2021-01-02 16:05 | 1.8123 | 0.46792 | 0.19084 | 0.90598 | 27.0572 |  | 1.3487 | 0.1458 | 445.9821 | 24.5 | 66.76
2021-01-02 16:10 | 1.6464 | 0.48161 | 0.18456 | 0.92278 | 21.1153 |  | 1.3487 | 0.10935 | 446.517 | 24.49 | 66.87
2021-01-02 16:15 | 1.787 | 0.55417 | 0.15101 | 1.0005 | 33.9627 |  | 1.3488 | 0.10936 | 447.526 | 24.5 | 67.08
2021-01-02 16:20 | 2.004 | 0.61437 | 0.18457 | 1.1263 | 22.1788 |  | 1.3561 | 0.11665 | 445.424 | 24.49 | 67.11
2021-01-02 16:25 | 2.0037 | 0.56231 | 0.17616 | 1.0381 | 25.6273 |  | 1.3559 | 0.11664 | 446.5788 | 24.46 | 66.87
2021-01-02 16:30 | 2.5407 | 0.57211 | 0.17833 | 1.0553 | 29.0895 |  | 1.3492 | 0.15315 | 446.3925 | 24.47 | 68.05
2021-01-02 16:35 | 2.4267 | 0.62297 | 0.18678 | 1.1417 | 22.8669 |  | 1.3496 | 0.1532 | 445.7377 | 24.45 | 69.24
2021-01-02 16:40 | 2.3245 | 0.55451 | 0.17629 | 1.0263 | 31.0821 |  | 1.3424 | 0.1532 | 446.3238 | 24.41 | 69.43
2021-01-02 16:45 | 3.0531 | 0.70251 | 0.20151 | 1.2804 | 35.3696 |  | 1.3426 | 0.2189 | 446.244 | 24.41 | 70
2021-01-02 16:50 | 2.9127 | 0.6998 | 0.18053 | 1.2511 | 40.7467 |  | 1.3499 | 0.20432 | 445.7117 | 24.4 | 70.17
2021-01-02 16:55 | 3.1683 | 0.63136 | 0.17844 | 1.1462 | 28.9648 |  | 1.3427 | 0.21162 | 446.2159 | 24.4 | 70.35
2021-01-02 17:00 | 2.4273 | 0.54096 | 0.17844 | 1.0076 | 31.4275 |  | 1.3427 | 0.14595 | 447.2509 | 24.42 | 70.22
2021-01-02 17:05 | 2.2356 | 0.47247 | 0.15324 | 0.87536 | 20.1743 |  | 1.3427 | 0.10946 | 446.7356 | 24.42 | 70.12
2021-01-02 17:10 | 2.4533 | 0.4671 | 0.14278 | 0.85876 | 18.0014 |  | 1.3503 | 0.12408 | 447.1499 | 24.43 | 70.79
2021-01-02 17:15 | 2.4028 | 0.51379 | 0.17851 | 0.96606 | 30.3978 |  | 1.3506 | 0.14601 | 448.1055 | 24.43 | 71.52
2021-01-02 17:20 | 2.186 | 0.5413 | 0.14494 | 0.97467 | 26.4668 |  | 1.3509 | 0.17525 | 446.4104 | 24.44 | 72.14
2021-01-02 17:25 | 2.0071 | 0.56464 | 0.14915 | 1.0146 | 33.9961 |  | 1.3436 | 0.13875 | 446.3936 | 24.43 | 72.41
2021-01-02 17:30 | 2.3902 | 0.62072 | 0.14912 | 1.1006 | 36.5056 |  | 1.3507 | 0.13872 | 446.5184 | 24.4 | 71.97
2021-01-02 17:35 | 3.0926 | 0.59592 | 0.11969 | 1.0331 | 23.5343 |  | 1.3504 | 0.16789 | 448.2194 | 24.39 | 71.31
2021-01-02 17:40 | 3.0534 | 0.48072 | 0.14065 | 0.87751 | 32.0927 |  | 1.35 | 0.17514 | 448.3569 | 24.38 | 70.48
2021-01-02 17:45 | 2.5934 | 0.48618 | 0.11756 | 0.86279 | 20.8596 |  | 1.3427 | 0.18973 | 448.3556 | 24.39 | 70.34
2021-01-02 17:50 | 2.5039 | 0.4437 | 0.12175 | 0.80187 | 28.8914 |  | 1.3499 | 0.17513 | 447.7973 | 24.37 | 70.34
2021-01-02 17:55 | 2.6059 | 0.39712 | 0.13434 | 0.74516 | 30.3 |  | 1.3572 | 0.17512 | 448.9118 | 24.35 | 70.25
2021-01-02 18:00 | 2.3248 | 0.46009 | 0.15322 | 0.85637 | 23.0127 |  | 1.3425 | 0.14592 | 448.4321 | 24.33 | 70.19
2021-01-02 18:05 | 1.6349 | 0.3697 | 0.12803 | 0.69472 | 24.8407 |  | 1.3424 | 0.10214 | 449.544 | 24.31 | 70.12
2021-01-02 18:10 | 1.6094 | 0.35875 | 0.098648 | 0.64856 | 9.6055 |  | 1.3352 | 0.080257 | 448.6115 | 24.27 | 70.31
2021-01-02 18:15 | 1.8904 | 0.38614 | 0.10704 | 0.69683 | 7.8376 |  | 1.3425 | 0.094848 | 447.6163 | 24.23 | 70.45
2021-01-02 18:20 | 2.5675 | 0.48063 | 0.11124 | 0.84797 | 14.4697 |  | 1.3498 | 0.14592 | 448.6801 | 24.22 | 70.57
2021-01-02 18:25 | 2.772 | 0.37521 | 0.10285 | 0.678 | 17.9657 |  | 1.3572 | 0.11675 | 449.6017 | 24.24 | 70.76
2021-01-02 18:30 | 1.7116 | 0.23141 | 0.081858 | 0.43657 | 35.704 |  | 1.3425 | 0.09485 | 449.1934 | 24.18 | 70.79
2021-01-02 18:35 | 1.8137 | 0.31218 | 0.10074 | 0.57926 | 26.4135 |  | 1.3424 | 0.11673 | 449.2984 | 24.13 | 70.79
2021-01-02 18:40 | 2.7075 | 0.37239 | 0.079747 | 0.65057 | 13.7114 |  | 1.3496 | 0.1459 | 447.8044 | 24.09 | 70.69
2021-01-02 18:45 | 2.9628 | 0.39154 | 0.10912 | 0.70928 | 20.1162 |  | 1.3495 | 0.14589 | 448.9408 | 24.06 | 70.6
2021-01-02 18:50 | 2.5414 | 0.41345 | 0.1343 | 0.76805 | 10.9114 |  | 1.3422 | 0.1386 | 448.948 | 24.05 | 70.7
2021-01-02 18:55 | 1.8134 | 0.37921 | 0.14689 | 0.72816 | 16.8776 |  | 1.3349 | 0.10942 | 449.5333 | 24.02 | 70.76
2021-01-02 19:00 | 1.9538 | 0.35729 | 0.13639 | 0.68406 | 15.2115 |  | 1.3421 | 0.13129 | 449.6481 | 23.96 | 70.84
2021-01-02 19:05 | 1.9921 | 0.3395 | 0.11121 | 0.63161 | 5.9253 |  | 1.3348 | 0.10941 | 450.2059 | 23.94 | 70.95
2021-01-02 19:10 | 1.5324 | 0.23956 | 0.077639 | 0.44485 | 15.1604 |  | 1.3348 | 0.080236 | 449.2216 | 23.89 | 71.15
2021-01-02 19:15 | 1.4557 | 0.29021 | 0.052457 | 0.4973 | 11.9727 |  | 1.3275 | 0.094822 | 448.7634 | 23.85 | 71.23
2021-01-02 19:20 | 1.3664 | 0.23684 | 0.090233 | 0.45326 | 13.5264 |  | 1.3349 | 0.080239 | 449.2942 | 23.83 | 71.54
2021-01-02 19:25 | 1.0728 | 0.23 | 0.096533 | 0.44909 | 16.1631 |  | 1.335 | 0.058359 | 450.8785 | 23.82 | 71.76
2021-01-02 19:30 | 0.85565 | 0.25601 | 0.081842 | 0.47217 | 7.8873 |  | 1.3349 | 0.043768 | 450.3855 | 23.8 | 71.79
2021-01-02 19:35 | 1.06 | 0.30668 | 0.094439 | 0.56453 | 15.3362 |  | 1.335 | 0.072952 | 450.9206 | 23.78 | 72.07
2021-01-02 19:40 | 1.009 | 0.30258 | 0.10913 | 0.57294 | 3.2288 |  | 1.3351 | 0.080249 | 450.4072 | 23.76 | 72.25
2021-01-02 19:45 | 1.0345 | 0.30396 | 0.090245 | 0.55616 | 10.9943 |  | 1.3351 | 0.08025 | 451.0727 | 23.72 | 72.39
2021-01-02 19:50 | 1.0984 | 0.27657 | 0.083947 | 0.50788 | 12.7412 |  | 1.335 | 0.094839 | 449.0361 | 23.67 | 72.53
2021-01-02 19:55 | 1.3283 | 0.23823 | 0.088144 | 0.45331 | 6.6005 |  | 1.335 | 0.080248 | 451.2207 | 23.63 | 72.7
2021-01-02 20:00 | 1.2261 | 0.19715 | 0.077648 | 0.37985 | 9.5019 |  | 1.3277 | 0.07295 | 451.2813 | 23.6 | 72.72
2021-01-02 20:05 | 1.1622 | 0.30669 | 0.090243 | 0.56035 | 7.1727 |  | 1.335 | 0.065658 | 450.202 | 23.6 | 72.85
2021-01-02 20:10 | 0.81744 | 0.29301 | 0.10704 | 0.55618 | 18.2391 |  | 1.3351 | 0.043774 | 449.0888 | 23.62 | 72.92
2021-01-02 20:15 | 0.88128 | 0.27247 | 0.083949 | 0.5016 | 22.8162 |  | 1.3351 | 0.043773 | 450.7078 | 23.61 | 72.88
2021-01-02 20:20 | 1.0218 | 0.30532 | 0.075553 | 0.54356 | 20.9562 |  | 1.3277 | 0.051067 | 450.7473 | 23.59 | 72.9
2021-01-02 20:25 | 0.95788 | 0.25055 | 0.056664 | 0.44072 | 21.62 |  | 1.335 | 0.051066 | 451.3308 | 23.56 | 72.98
2021-01-02 20:30 | 1.0473 | 0.23139 | 0.069257 | 0.42394 | 12.5779 |  | 1.3351 | 0.072954 | 449.7258 | 23.56 | 73.07
2021-01-02 20:35 | 1.0345 | 0.18758 | 0.071356 | 0.36098 | 16.9001 |  | 1.3278 | 0.051068 | 449.7389 | 23.55 | 73.13
2021-01-02 20:40 | 1.1366 | 0.15607 | 0.07345 | 0.31269 | 20.7609 |  | 1.3277 | 0.058359 | 449.8325 | 23.51 | 73.06
2021-01-02 20:45 | 1.0983 | 0.21084 | 0.069252 | 0.39243 | 10.4008 |  | 1.3277 | 0.051064 | 451.4573 | 23.49 | 73.14
2021-01-02 20:50 | 0.91941 | 0.16427 | 0.060851 | 0.31265 | 13.9138 |  | 1.3275 | 0.043764 | 451.0871 | 23.42 | 73.04
2021-01-02 20:55 | 0.91939 | 0.22586 | 0.056653 | 0.40286 | 7.4471 |  | 1.3275 | 0.0072938 | 451.1739 | 23.37 | 73.18
2021-01-02 21:00 | 0.83007 | 0.22314 | 0.058756 | 0.4008 | 33.5911 |  | 1.3203 | -0.029178 | 414.4731 | 23.37 | 73.45
2021-01-02 21:05 | 0.90669 | 0.23273 | 0.056657 | 0.41129 | 239.6021 |  | 1.2911 | 0 | 351.5798 | 23.38 | 73.48
2021-01-02 21:10 | 0.77895 | 0.2026 | 0.065048 | 0.3756 | 159.3552 |  | 1.2765 | 0.007294 | 351.6219 | 23.36 | 73.39
2021-01-02 21:15 | 0.79178 | 0.2341 | 0.071348 | 0.43019 | 79.9952 |  | 1.2766 | 0.021884 | 352.6116 | 23.4 | 73.47
2021-01-02 21:20 | 0.85567 | 0.25328 | 0.05876 | 0.44699 | 47.4987 |  | 1.2766 | 0.051064 | 351.4842 | 23.44 | 73.45
2021-01-02 21:25 | 0.98337 | 0.23959 | 0.058759 | 0.426 | 22.6201 |  | 1.2839 | 0.058359 | 351.4648 | 23.46 | 73.32
2021-01-02 21:30 | 1.1494 | 0.22589 | 0.05666 | 0.40292 | 19.1668 |  | 1.2766 | 0.043769 | 351.9976 | 23.46 | 73.31
2021-01-02 21:35 | 1.0728 | 0.22043 | 0.058762 | 0.39455 | 21.4769 |  | 1.2767 | 0.065657 | 350.3838 | 23.46 | 73.49
2021-01-02 21:40 | 1.0218 | 0.19854 | 0.056667 | 0.36309 | 30.4291 |  | 1.2767 | 0.051069 | 351.958 | 23.46 | 73.69
2021-01-02 21:45 | 0.81746 | 0.16431 | 0.056669 | 0.30853 | 24.6976 |  | 1.2768 | 0.043775 | 351.4272 | 23.45 | 73.84
2021-01-02 21:50 | 0.76642 | 0.2054 | 0.06087 | 0.37572 | 27.0904 |  | 1.2842 | 0.036482 | 351.6075 | 23.43 | 74.07
2021-01-02 21:55 | 0.83035 | 0.19446 | 0.058776 | 0.35685 | 28.8299 |  | 1.277 | 0.021891 | 351.0608 | 23.42 | 74.38
2021-01-02 22:00 | 0.77927 | 0.21912 | 0.054579 | 0.38835 | 9.3717 |  | 1.277 | 0.043782 | 351.5959 | 23.41 | 74.5
2021-01-02 22:05 | 0.81768 | 0.27803 | 0.060882 | 0.48916 | 8.5958 |  | 1.2771 | 0.051084 | 350.4522 | 23.45 | 74.65
2021-01-02 22:10 | 0.88154 | 0.17668 | 0.048285 | 0.317 | 15.9035 |  | 1.2844 | 0.043786 | 350.9895 | 23.45 | 74.59
2021-01-02 22:15 | 0.76652 | 0.15475 | 0.060878 | 0.29809 | 9.6479 |  | 1.2843 | 0.029189 | 350.5604 | 23.38 | 74.72
2021-01-02 22:20 | 0.88154 | 0.2342 | 0.052483 | 0.41357 | -0.36795 |  | 1.2771 | 0.043786 | 350.5428 | 23.38 | 74.89
2021-01-02 22:25 | 0.8432 | 0.19585 | 0.050383 | 0.35058 | 4.0269 |  | 1.2771 | 0.051083 | 350.583 | 23.35 | 74.98
2021-01-02 22:30 | 1.0477 | 0.27256 | 0.058785 | 0.47868 | 7.5536 |  | 1.2845 | 0.094875 | 350.0137 | 23.36 | 75.19
2021-01-02 22:35 | 0.83052 | 0.23148 | 0.04619 | 0.39891 | 2.811 |  | 1.2918 | 0.072983 | 349.989 | 23.37 | 75.27
2021-01-02 22:40 | 0.85612 | 0.28218 | 0.054591 | 0.48712 | 4.7636 |  | 1.2919 | 0.15327 | 350.4994 | 23.37 | 75.47
2021-01-02 22:45 | 0.79219 | 0.21642 | 0.067186 | 0.40102 | 14.331 |  | 1.3137 | 0.12407 | 350.5645 | 23.33 | 75.48
2021-01-02 22:50 | 0.75385 | 0.21504 | 0.062986 | 0.39261 | 15.0769 |  | 1.3356 | 0.094877 | 351.6682 | 23.3 | 75.56
2021-01-02 22:55 | 0.81777 | 0.32326 | 0.062988 | 0.5585 | 6.2866 |  | 1.3429 | 0.080284 | 351.1226 | 23.3 | 75.7
2021-01-02 23:00 | 0.80502 | 0.28218 | 0.088187 | 0.52072 | 15.6301 |  | 1.3357 | 0.036494 | 351.0626 | 23.34 | 75.64
2021-01-02 23:05 | 1.0988 | 0.21505 | 0.067186 | 0.39682 | 16.9477 |  | 1.321 | 0.051088 | 350.5665 | 23.33 | 75.46
2021-01-02 23:10 | 0.99657 | 0.17942 | 0.039889 | 0.31492 | 1.8398 |  | 1.3209 | 0.058384 | 351.139 | 23.31 | 75.38
2021-01-02 23:15 | 0.72829 | 0.20956 | 0.054587 | 0.37371 | 0.071551 |  | 1.3137 | 0.065684 | 351.1287 | 23.31 | 75.48
2021-01-02 23:20 | 0.81777 | 0.24382 | 0.052491 | 0.42623 | 17.2039 |  | 1.3211 | 0.05109 | 351.0843 | 23.33 | 75.59
2021-01-02 23:25 | 0.6645 | 0.2411 | 0.058795 | 0.42836 | 15.6311 |  | 1.3285 | 0.036496 | 350.4498 | 23.39 | 75.63
2021-01-02 23:30 | 0.48558 | 0.20137 | 0.039895 | 0.34856 | 3.3428 |  | 1.3284 | 0.029196 | 350.9829 | 23.4 | 75.45
2021-01-02 23:35 | 0.58776 | 0.21916 | 0.031494 | 0.36742 | 9.8436 |  | 1.3283 | 0.029194 | 350.5397 | 23.35 | 75.4
2021-01-02 23:40 | 0.56218 | 0.21093 | 0.048288 | 0.37161 | 14.0749 |  | 1.3283 | 0.029192 | 351.6516 | 23.32 | 75.4
2021-01-02 23:45 | 0.80487 | 0.14106 | 0.027291 | 0.24352 | 9.2598 |  | 1.3281 | 0.043785 | 351.2351 | 23.25 | 75.41
2021-01-02 23:50 |  | 0.14792 | 0.029391 | 0.25612 | 2.6472 |  | 1.3355 | 0.036489 | 350.738 | 23.21 | 75.72
2021-01-02 23:55 | 0.72829 | 0.18765 | 0.037792 | 0.32543 | 9.1893 |  | 1.3283 | 0.036491 | 350.2039 | 23.19 | 76.07
2021-01-03 | 0.72836 | 0.22739 | 0.052493 | 0.40105 | 7.7896 |  | 1.3284 | 0.029196 | 351.2235 | 23.2 | 76.33
2021-01-03 00:05 | 0.56227 | 0.18904 | 0.044096 | 0.33387 | 7.9842 |  | 1.3285 | 0.029197 | 350.6654 | 23.21 | 76.43
2021-01-03 00:10 | 0.6006 | 0.15206 | 0.037796 | 0.27087 | 4.4777 |  | 1.3285 | 0.021898 | 351.2342 | 23.18 | 76.55
2021-01-03 00:15 | 0.56227 | 0.13836 | 0.035697 | 0.24778 | 4.7946 |  | 1.3285 | 0.029197 | 351.8084 | 23.14 | 76.78
2021-01-03 00:20 | 0.57506 | 0.13562 | 0.033598 | 0.24148 | 5.8579 |  | 1.3285 | 0.021898 | 350.256 | 23.1 | 77.02
2021-01-03 00:25 | 0.74124 | 0.16029 | 0.0399 | 0.2856 | 3.8033 |  | 1.3286 | 0.0292 | 351.4733 | 23.1 | 77.18
2021-01-03 00:30 | 0.76679 | 0.14522 | 0.0462 | 0.2667 | 14.477 |  | 1.3286 | 0.029199 | 350.7786 | 23.09 | 77.27
2021-01-03 00:35 | 0.62621 | 0.15755 | 0.0525 | 0.294 | 8.6597 |  | 1.3359 | 0.0219 | 351.2965 | 23.1 | 77.24
2021-01-03 00:40 | 0.46006 | 0.11371 | 0.041998 | 0.21419 | 3.5782 |  | 1.3358 | 0.021899 | 350.4268 | 23.1 | 77.03
2021-01-03 00:45 | 0.47281 | 0.084933 | 0.037796 | 0.16798 | 3.3736 |  | 1.3358 | 0.014598 | 352.0736 | 23.07 | 76.99
2021-01-03 00:50 | 0.62611 | 0.10136 | 0.037794 | 0.19317 | 1.4413 |  | 1.3357 | 0.036493 | 350.5528 | 23.03 | 76.93
2021-01-03 00:55 | 0.58776 | 0.13286 | 0.04829 | 0.25195 | 12.4196 |  | 1.3429 | 0.029194 | 351.0846 | 23.04 | 76.76
2021-01-03 01:00 | 0.5111 | 0.1315 | 0.031494 | 0.23096 | 21.2822 |  | 1.3429 | 0.029194 | 350.0068 | 23.05 | 76.75
2021-01-03 01:05 |  |  |  |  | 25.3302 |  |  |  | 350.5255 | 23.06 | 76.71
2021-01-03 01:10 |  |  |  |  | 13.0011 |  |  |  | 350.0756 | 23.02 | 76.56
2021-01-03 01:15 |  |  |  |  | 6.8169 |  |  |  | 351.2123 | 22.98 | 76.48
2021-01-03 01:20 |  |  |  |  | 14.3592 |  |  |  | 350.2025 | 22.94 | 76.61
2021-01-03 01:25 |  |  |  |  | 2.5039 |  |  |  | 350.788 | 22.9 | 76.73
2021-01-03 01:30 |  |  |  |  | 1.7067 |  |  |  | 350.821 | 22.88 | 76.73
2021-01-03 01:35 |  |  |  |  | 14.3386 |  |  |  | 352.0259 | 22.9 | 76.68
2021-01-03 01:40 |  |  |  |  | 10.5873 |  |  |  | 350.4896 | 22.87 | 76.61
2021-01-03 01:45 |  |  |  |  | -0.66425 |  |  |  | 350.0084 | 22.83 | 76.77
2021-01-03 01:50 |  |  |  |  | 4.9159 |  |  |  | 351.5265 | 22.87 | 76.86
2021-01-03 01:55 |  |  |  |  | 14.1849 |  |  |  | 350.491 | 22.86 | 76.76
2021-01-03 02:00 |  |  |  |  | 2.4833 |  |  |  | 351.0562 | 22.84 | 76.75
2021-01-03 02:05 |  |  |  |  | -0.87887 |  |  |  | 351.0426 | 22.85 | 76.72
2021-01-03 02:10 | 0.44711 | 0.11914 | 0.037784 | 0.22041 | 9.5861 |  | 1.3791 | -0.036484 | 351.0211 | 22.86 | 76.77
2021-01-03 02:15 | 0.38323 | 0.080796 | 0.04618 | 0.16793 | 6.6223 |  | 1.3572 | -0.0072968 | 350.5295 | 22.83 | 76.87
2021-01-03 02:20 | 0.38324 | 0.079429 | 0.031487 | 0.15324 | -2.8922 |  | 1.3572 | 0 | 351.6058 | 22.81 | 77.06
2021-01-03 02:25 | 0.38326 | 0.10682 | 0.02729 | 0.19103 | 6.7863 |  | 1.35 | 0.0072973 | 351.5762 | 22.82 | 77.19
2021-01-03 02:30 | 0.45993 | 0.067108 | 0.035688 | 0.13855 | 17.5385 |  | 1.3427 | 0 | 351.5692 | 22.82 | 77.26
2021-01-03 02:35 | 0.44715 | 0.057522 | 0.03149 | 0.11966 | 5.7645 |  | 1.3355 | 0.0072976 | 350.5271 | 22.8 | 77.39
2021-01-03 02:40 | 0.39608 | 0.075332 | 0.020995 | 0.13647 | 3.3833 |  | 1.3428 | 0.014596 | 349.9595 | 22.81 | 77.59
2021-01-03 02:45 | 0.49837 | 0.13151 | 0.044096 | 0.24568 | 20.8549 |  | 1.3431 | 0.021898 | 351.4153 | 22.88 | 77.8
2021-01-03 02:50 | 0.39617 | 0.1096 | 0.037799 | 0.2079 | 18.597 |  | 1.3359 | 0.0146 | 349.737 | 22.93 | 77.83
2021-01-03 02:55 | 0.46013 | 0.16716 | 0.031504 | 0.28983 | 2.587 |  | 1.3433 | 0.0073008 | 350.1364 | 23 | 77.98
2021-01-03 03:00 | [9 empty] | 23.04 | 77.99
2021-01-03 03:05 | 0.38345 | 0.068511 | 0.033605 | 0.13862 | 19.6635 |  | 1.3361 | 0.014602 | 351.1642 | 23.02 | 77.98
2021-01-03 03:10 | 0.34511 | 0.13154 | 0.039906 | 0.24364 | 6.7284 |  | 1.3434 | 0.014602 | 350.6684 | 22.99 | 78.13
2021-01-03 03:15 | 0.3451 | 0.071249 | 0.033604 | 0.14492 | 8.0779 |  | 1.336 | 0.0073008 | 350.1816 | 22.96 | 78.19
2021-01-03 03:20 | 0.33232 | 0.063028 | 0.033604 | 0.13232 | 13.4462 |  | 1.336 | 0.014602 | 350.2289 | 22.92 | 78.38
2021-01-03 03:25 | 0.38347 | 0.057551 | 0.037807 | 0.12602 | 6.8104 |  | 1.3434 | 0.0073012 | 350.7531 | 22.91 | 78.61
2021-01-03 03:30 | 0.34514 | 0.049332 | 0.033608 | 0.10922 | -0.3886 |  | 1.3362 | 0.0073016 | 350.2169 | 22.9 | 78.83
2021-01-03 03:35 | 0.33239 | 0.057559 | 0.037812 | 0.12394 | 14.1648 |  | 1.3363 | 0.021907 | 350.7017 | 22.91 | 79.12
2021-01-03 03:40 | 0.33242 | 0.075383 | 0.035715 | 0.15126 | 15.7619 |  | 1.3365 | 0.021909 | 351.6904 | 22.94 | 79.34
2021-01-03 03:45 | 0.42196 | 0.12062 | 0.03782 | 0.22272 | 8.3676 |  | 1.3439 | 0.021911 | 349.4869 | 22.98 | 79.49
2021-01-03 03:50 | 0.44755 | 0.12337 | 0.042024 | 0.23113 | 9.5342 |  | 1.3513 | 0.021912 | 350.4964 | 23.01 | 79.5
2021-01-03 03:55 | 0.44759 | 0.1604 | 0.052534 | 0.29629 | 12.5428 |  | 1.3587 | 0.014609 | 350.4194 | 23.05 | 79.6
2021-01-03 04:00 | 0.38366 | 0.14395 | 0.037826 | 0.25637 | 6.2715 |  | 1.3514 | 0.01461 | 350.3763 | 23.08 | 79.53
2021-01-03 04:05 | 0.38365 | 0.1412 | 0.037825 | 0.25427 | 9.627 |  | 1.3514 | 0.021914 | 350.3981 | 23.07 | 79.48
2021-01-03 04:10 | 0.43481 | 0.14669 | 0.027318 | 0.25217 | 20.8298 |  | 1.3514 | 0.021914 | 349.8397 | 23.09 | 79.43
2021-01-03 04:15 | 0.51151 | 0.1083 | 0.035722 | 0.19962 | 12.2148 |  | 1.344 | 0.0073044 | 349.3521 | 23.07 | 79.34
2021-01-03 04:20 | 0.44758 | 0.10007 | 0.035723 | 0.18912 | 5.4733 |  | 1.3513 | 0.014609 | 349.8604 | 23.08 | 79.39
2021-01-03 04:25 | 0.54991 | 0.11242 | 0.052535 | 0.22275 | 6.0567 |  | 1.3587 | 0.021914 | 350.3541 | 23.1 | 79.42
2021-01-03 04:30 | 0.51156 | 0.11379 | 0.048334 | 0.22276 | 17.076 |  | 1.3441 | 0.021915 | 349.775 | 23.13 | 79.41
2021-01-03 04:35 | 0.44763 | 0.11654 | 0.056742 | 0.23537 | 6.9677 |  | 1.3442 | 0.0073053 | 349.7542 | 23.14 | 79.45
2021-01-03 04:40 | 0.5244 | 0.13163 | 0.060949 | 0.26271 | 11.7875 |  | 1.337 | 0.014612 | 349.6959 | 23.17 | 79.53
2021-01-03 04:45 | 0.52439 | 0.10283 | 0.065151 | 0.22488 | 20.4948 |  | 1.3296 | 0.0073057 | 350.2309 | 23.17 | 79.48
2021-01-03 04:50 | 0.53718 | 0.082265 | 0.046236 | 0.17233 | 12.2681 |  | 1.3223 | 0.0073056 | 349.7157 | 23.16 | 79.5
2021-01-03 04:55 | 0.48602 | 0.097347 | 0.046236 | 0.19545 | 5.2183 |  | 1.3296 | 0.021917 | 349.1848 | 23.16 | 79.51
2021-01-03 05:00 | 0.53719 | 0.11792 | 0.044135 | 0.22488 | 14.5705 |  | 1.3369 | 0.021917 | 350.7693 | 23.16 | 79.56
2021-01-03 05:05 | 0.58839 | 0.1714 | 0.065157 | 0.32789 | 21.1003 |  | 1.3517 | 0.036532 | 349.6229 | 23.21 | 79.59
2021-01-03 05:10 | 0.71632 | 0.19472 | 0.056751 | 0.35522 | 14.7152 |  | 1.3444 | 0.0073065 | 349.581 | 23.24 | 79.51
2021-01-03 05:15 | 0.58837 | 0.15905 | 0.033628 | 0.27743 | 20.598 |  | 1.3297 | 0.021918 | 350.1438 | 23.23 | 79.35
2021-01-03 05:20 | 0.67784 | 0.14122 | 0.03993 | 0.25639 | 25.0982 |  | 1.3296 | 0.029222 | 350.5497 | 23.21 | 79.23
2021-01-03 05:25 | 0.79295 | 0.15356 | 0.044133 | 0.27951 | 12.4825 |  | 1.3369 | 0.029221 | 350.7412 | 23.2 | 79.18
2021-01-03 05:30 | 0.83132 | 0.17549 | 0.056742 | 0.32574 | 17.936 |  | 1.3442 | 0.029221 | 350.1862 | 23.22 | 79.1
2021-01-03 05:35 | 1.2022 | 0.17686 | 0.039929 | 0.31102 | 23.9616 |  | 1.3368 | 0.02922 | 349.6802 | 23.21 | 79.03
2021-01-03 05:40 | 1.3301 | 0.20154 | 0.046235 | 0.35517 | 16.2071 |  | 1.3515 | 0.051138 | 349.6407 | 23.23 | 79.09
2021-01-03 05:45 | 0.95927 | 0.16042 | 0.060949 | 0.30474 | 14.3148 |  | 1.3516 | 0.043835 | 350.4838 | 23.25 | 79.22
2021-01-03 05:50 | 0.80583 | 0.14946 | 0.065156 | 0.29215 | 19.1761 |  | 1.3516 | 0.029225 | 350.9595 | 23.28 | 79.26
2021-01-03 05:55 | 0.93372 | 0.18922 | 0.054646 | 0.34679 | 19.2168 |  | 1.3662 | 0.051143 | 348.8546 | 23.27 | 79.27
2021-01-03 06:00 | 1.0618 | 0.28661 | 0.067265 | 0.50659 | 12.5568 |  | 1.3737 | 0.065762 | 350.3459 | 23.32 | 79.42
2021-01-03 06:05 | 0.81881 | 0.28116 | 0.067273 | 0.49824 | 15.7928 |  | 1.3739 | 0.043847 | 348.8069 | 23.39 | 79.45
2021-01-03 06:10 | 0.56294 | 0.23316 | 0.052558 | 0.40995 | 21.7089 |  | 1.3593 | 0.021924 | 348.7682 | 23.42 | 79.34
2021-01-03 06:15 | 0.47335 | 0.18377 | 0.060964 | 0.34266 | 10.1118 |  | 1.3592 | 0.036538 | 350.2095 | 23.41 | 79.28
2021-01-03 06:20 | 0.49893 | 0.19063 | 0.067269 | 0.35947 | 11.6673 |  | 1.3665 | 0.02923 | 350.2378 | 23.39 | 79.33
2021-01-03 06:25 | 0.55014 | 0.13166 | 0.052557 | 0.25438 | 23.7557 |  | 1.3593 | 0.029231 | 349.6642 | 23.41 | 79.43
2021-01-03 06:30 | 0.81891 | 0.20987 | 0.086205 | 0.4079 | 16.931 |  | 1.3814 | 0.043853 | 350.1019 | 23.45 | 79.67
2021-01-03 06:35 | 0.83181 | 0.2387 | 0.069393 | 0.43528 | 10.0329 |  | 1.3596 | 0.021929 | 348.9296 | 23.51 | 79.79
2021-01-03 06:40 | 0.71666 | 0.23185 | 0.067293 | 0.42268 | 17.8961 |  | 1.3597 | 0.03655 | 349.4224 | 23.53 | 79.82
2021-01-03 06:45 | 0.84468 | 0.26479 | 0.048369 | 0.45425 | 17.0267 |  | 1.3597 | 0.065793 | 350.4529 | 23.54 | 79.93
2021-01-03 06:50 | 0.88305 | 0.28536 | 0.0715 | 0.50891 | 9.153 |  | 1.3597 | 0.058481 | 350.4845 | 23.52 | 79.95
2021-01-03 06:55 | 0.81911 | 0.24285 | 0.067298 | 0.43954 | 13.9249 |  | 1.3671 | 0.051174 | 348.5135 | 23.53 | 80.02
2021-01-03 07:00 | 0.92153 | 0.2305 | 0.084125 | 0.43745 | 14.8264 |  | 1.3598 | 0.058486 | 348.48 | 23.55 | 80.02
2021-01-03 07:05 | 1.3311 | 0.23874 | 0.069405 | 0.43536 | 13.045 |  | 1.3452 | 0.073109 | 349.5071 | 23.57 | 79.99
2021-01-03 07:10 | 1.5615 | 0.21816 | 0.079919 | 0.41221 | 20.1097 |  | 1.3379 | 0.065797 | 348.9983 | 23.56 | 79.96
2021-01-03 07:15 | 1.843 | 0.16601 | 0.063091 | 0.31756 | 31.5763 |  | 1.3378 | 0.065794 | 348.4956 | 23.55 | 79.87
2021-01-03 07:20 | 1.9197 | 0.23461 | 0.079915 | 0.43953 | 26.815 |  | 1.3451 | 0.058483 | 349.0518 | 23.53 | 79.93
2021-01-03 07:25 | 1.7021 | 0.20168 | 0.067296 | 0.37643 | 22.9342 |  | 1.3378 | 0 | 350.102 | 23.54 | 79.84
2021-01-03 07:30 | 1.5231 | 0.27852 | 0.069402 | 0.49633 | 34.7307 |  | 1.3013 | 0.043864 | 347.969 | 23.54 | 80.01
2021-01-03 07:35 | 1.3441 | 0.34993 | 0.069414 | 0.60579 | 37.6348 |  | 1.2796 | 0.073119 | 348.8618 | 23.63 | 80.14
2021-01-03 07:40 | 1.1778 | 0.36093 | 0.067315 | 0.62056 | 20.1142 |  | 1.2797 | 0.073124 | 349.3083 | 23.68 | 80.12
2021-01-03 07:45 | 1.0499 | 0.36371 | 0.084152 | 0.64166 | 23.8035 |  | 1.2798 | 0.14626 | 349.7534 | 23.72 | 80.27
2021-01-03 07:50 | 1.2931 | 0.36509 | 0.067323 | 0.62694 | 30.7996 |  | 1.2798 | 0.15358 | 348.6799 | 23.73 | 80.27
2021-01-03 07:55 | 1.5749 | 0.37608 | 0.077845 | 0.65642 | 15.0778 |  | 1.2799 | 0.12433 | 348.6662 | 23.73 | 80.4
2021-01-03 08:00 | 1.4341 | 0.39396 | 0.071539 | 0.67542 | 15.4478 |  | 1.2727 | 0.10971 | 348.6008 | 23.76 | 80.54
2021-01-03 08:05 | 1.4596 | 0.41589 | 0.063118 | 0.70061 | 26.8985 |  | 1.2726 | 0.13164 | 348.663 | 23.73 | 80.43
2021-01-03 08:10 | 1.3062 | 0.40084 | 0.067335 | 0.68176 | 23.3061 |  | 1.28 | 0.1024 | 350.1568 | 23.77 | 80.65
2021-01-03 08:15 | 1.4599 | 0.43381 | 0.08838 | 0.75333 | 21.0838 |  | 1.2801 | 0.10972 | 347.4793 | 23.79 | 80.68
2021-01-03 08:20 | 2.062 | 0.42288 | 0.079973 | 0.72818 | 25.0108 |  | 1.2803 | 0.16095 | 348.9715 | 23.83 | 80.91
2021-01-03 08:25 | 2.1261 | 0.38718 | 0.075764 | 0.67135 | 27.2137 |  | 1.2949 | 0.13168 | 349.4995 | 23.83 | 80.91
2021-01-03 08:30 | 1.8828 | 0.44486 | 0.069453 | 0.75135 | 23.2595 |  | 1.2949 | 0.10974 | 349.4529 | 23.86 | 80.87
2021-01-03 08:35 | 2.0493 | 0.49429 | 0.10944 | 0.86501 | 30.504 |  | 1.3023 | 0.11706 | 348.887 | 23.89 | 80.75
2021-01-03 08:40 | 2.3697 | 0.42019 | 0.086298 | 0.73038 | 52.8769 |  | 1.3024 | 0.11707 | 347.7302 | 23.95 | 80.75
2021-01-03 08:45 | 2.4597 | 0.46694 | 0.10315 | 0.81889 | 47.6982 |  | 1.3172 | 0.10245 | 348.6205 | 24.05 | 80.71
2021-01-03 08:50 | 2.7163 | 0.60573 | 0.096849 | 1.0253 | 47.254 |  | 1.3027 | 0.15369 | 347.9733 | 24.11 | 80.88
2021-01-03 08:55 | 2.4347 | 0.68135 | 0.11792 | 1.1623 | 48.93 |  | 1.2956 | 0.19031 | 346.812 | 24.17 | 80.93
2021-01-03 09:00 | 1.8965 | 0.63876 | 0.10739 | 1.0865 | 36.3408 |  | 1.2955 | 0.17567 | 348.3503 | 24.21 | 80.7
2021-01-03 09:05 | 2.0503 | 0.58794 | 0.11581 | 1.0149 | 31.1847 |  | 1.2809 | 0.14639 | 347.2701 | 24.23 | 80.63
2021-01-03 09:10 | 2.3066 | 0.46295 | 0.12003 | 0.82965 | 39.8793 |  | 1.2883 | 0.17567 | 348.2879 | 24.25 | 80.65
2021-01-03 09:15 | 1.8196 | 0.39699 | 0.12002 | 0.73065 | 29.8518 |  | 1.2955 | 0.12443 | 347.7877 | 24.24 | 80.56
2021-01-03 09:20 | 1.9349 | 0.49313 | 0.11791 | 0.87169 | 27.0317 |  | 1.3028 | 0.10979 | 347.8007 | 24.24 | 80.44
2021-01-03 09:25 | 2.2936 | 0.44505 | 0.1158 | 0.798 | 34.9454 |  | 1.3101 | 0.12443 | 348.3046 | 24.26 | 80.34
2021-01-03 09:30 | 1.8963 | 0.45739 | 0.11159 | 0.81269 | 28.9776 |  | 1.3174 | 0.10978 | 347.8213 | 24.24 | 80.25
2021-01-03 09:35 | 2.1654 | 0.53157 | 0.10948 | 0.9243 | 21.6491 |  | 1.3174 | 0.1171 | 346.7368 | 24.26 | 80.22
2021-01-03 09:40 | 2.332 | 0.62361 | 0.14317 | 1.1012 | 26.0368 |  | 1.3321 | 0.10247 | 347.7143 | 24.32 | 79.99
2021-01-03 09:45 | 2.5624 | 0.62216 | 0.14316 | 1.0989 | 38.7737 |  | 1.3392 | 0.073181 | 347.71 | 24.36 | 79.41
2021-01-03 09:50 | 2.5494 | 0.63997 | 0.14946 | 1.1304 | 41.3944 |  | 1.3318 | 0.10245 | 346.6132 | 24.42 | 78.88
2021-01-03 09:55 | 3.1514 | 0.84321 | 0.12841 | 1.4209 | 51.4683 |  | 1.3245 | 0.13903 | 348.1036 | 24.5 | 78.47
2021-01-03 10:00 | 3.0235 | 1.1179 | 0.14105 | 1.8547 | 62.9502 |  | 1.3245 | 0.16099 | 347.4642 | 24.58 | 78.27
2021-01-03 10:05 | 2.8318 | 0.97527 | 0.13896 | 1.6318 | 62.4585 |  | 1.3394 | 0.16102 | 348.3527 | 24.67 | 78.38
2021-01-03 10:10 | 2.8323 | 0.78723 | 0.12214 | 1.3288 | 55.8365 |  | 1.3616 | 0.15373 | 347.1317 | 24.76 | 78.53
2021-01-03 10:15 | 2.9221 | 0.69381 | 0.13478 | 1.2004 | 52.4743 |  | 1.3689 | 0.15373 | 348.144 | 24.79 | 78.43
2021-01-03 10:20 | 3.1016 | 0.67322 | 0.13268 | 1.1646 | 51.1733 |  | 1.3763 | 0.16106 | 347.0493 | 24.82 | 78.36
2021-01-03 10:25 | 3.2811 | 0.64027 | 0.13479 | 1.1162 | 47.6478 |  | 1.3837 | 0.1757 | 347.0144 | 24.84 | 78.37
2021-01-03 10:30 | 3.7428 | 0.6568 | 0.17271 | 1.1816 | 39.9093 |  | 1.3911 | 0.21964 | 348.5205 | 24.88 | 78.4
2021-01-03 10:35 | 4.2429 | 0.68569 | 0.21274 | 1.2638 | 31.9743 |  | 1.4058 | 0.24162 | 346.3525 | 24.92 | 78.38
2021-01-03 10:40 | 4.2429 | 0.73104 | 0.22327 | 1.3438 | 41.6345 |  | 1.4131 | 0.2343 | 346.8409 | 24.95 | 78.26
2021-01-03 10:45 | 4.1278 | 0.80118 | 0.23171 | 1.4598 | 47.0933 |  | 1.4279 | 0.24164 | 346.2332 | 25 | 78.24
2021-01-03 10:50 | 3.4997 | 0.90838 | 0.20433 | 1.5967 | 43.0735 |  | 1.4279 | 0.20503 | 347.2345 | 25.04 | 78.08
2021-01-03 10:55 | 2.9614 | 1.0307 | 0.20223 | 1.78 | 52.4893 |  | 1.4279 | 0.15378 | 345.6047 | 25.08 | 77.96
2021-01-03 11:00 | 2.91 | 1.1365 | 0.20433 | 1.9464 | 50.8066 |  | 1.4133 | 0.16842 | 346.0774 | 25.13 | 77.68
2021-01-03 11:05 | 2.9486 | 1.028 | 0.21698 | 1.7927 | 46.5209 |  | 1.406 | 0.19039 | 345.999 | 25.19 | 77.48
2021-01-03 11:10 | 3.2559 | 0.86434 | 0.20432 | 1.5292 | 53.4072 |  | 1.4058 | 0.21966 | 346.0244 | 25.2 | 77.11
2021-01-03 11:15 | 2.9991 | 0.73231 | 0.19586 | 1.3184 | 50.805 |  | 1.3983 | 0.20498 | 345.0267 | 25.2 | 76.65
2021-01-03 11:20 | 2.9604 | 0.8353 | 0.2148 | 1.4931 | 55.6919 |  | 1.4055 | 0.19033 | 346.6029 | 25.22 | 76.35
2021-01-03 11:25 | 3.0887 | 0.87791 | 0.2127 | 1.5584 | 69.3914 |  | 1.4055 | 0.17569 | 347.0943 | 25.24 | 76.35
2021-01-03 11:30 | 3.294 | 0.99064 | 0.23799 | 1.7544 | 76.2761 |  | 1.4056 | 0.15374 | 345.6505 | 25.26 | 76.38
2021-01-03 11:35 | 3.7043 | 0.93986 | 0.26328 | 1.7039 | 72.5898 |  | 1.3911 | 0.13179 | 346.6409 | 25.29 | 76.45
2021-01-03 11:40 | 3.653 | 0.99754 | 0.21483 | 1.7439 | 68.2912 |  | 1.3691 | 0.16107 | 345.5792 | 25.31 | 76.27
2021-01-03 11:45 | 3.832 | 1.0483 | 0.2485 | 1.8575 | 57.5702 |  | 1.3616 | 0.18301 | 346.6504 | 25.32 | 75.93
2021-01-03 11:50 | 4.3449 | 0.99613 | 0.20639 | 1.7312 | 60.752 |  | 1.3617 | 0.22695 | 345.5477 | 25.35 | 75.96
2021-01-03 11:55 | 5.1785 | 0.94125 | 0.20431 | 1.645 | 62.3264 |  | 1.3545 | 0.23429 | 346.5419 | 25.37 | 76.14
2021-01-03 12:00 | 5.0123 | 0.97569 | 0.23171 | 1.7294 | 63.7266 |  | 1.3546 | 0.25628 | 345.9643 | 25.39 | 76.31
2021-01-03 12:05 | 4.1401 | 0.97146 | 0.26328 | 1.7524 | 65.7906 |  | 1.3471 | 0.27822 | 345.4794 | 25.39 | 75.97
2021-01-03 12:10 | 3.7926 | 1.0961 | 0.29686 | 1.977 | 60.1995 |  | 1.3393 | 0.27811 | 345.5893 | 25.41 | 74.73
2021-01-03 12:15 | 3.254 | 0.97371 | 0.26525 | 1.7578 | 49.2975 |  | 1.3391 | 0.21221 | 345.0377 | 25.47 | 74.1
2021-01-03 12:20 | 3.0361 | 0.93522 | 0.22524 | 1.6588 | 40.7996 |  | 1.3391 | 0.21221 | 346.0643 | 25.5 | 73.86
2021-01-03 12:25 | 3.164 | 0.87748 | 0.22523 | 1.5703 | 37.3022 |  | 1.3317 | 0.21951 | 344.5037 | 25.51 | 73.61
2021-01-03 12:30 | 3.3054 | 0.83502 | 0.24631 | 1.5263 | 42.9235 |  | 1.3319 | 0.19758 | 344.3912 | 25.57 | 73.72
2021-01-03 12:35 | 3.5875 | 0.88041 | 0.2358 | 1.5832 | 45.7453 |  | 1.332 | 0.30006 | 345.9152 | 25.59 | 73.85
2021-01-03 12:40 | 3.5493 | 0.89696 | 0.26108 | 1.636 | 41.7614 |  | 1.3247 | 0.21225 | 345.3293 | 25.62 | 73.95
2021-01-03 12:45 | 4.2923 | 0.83237 | 0.24423 | 1.5201 | 46.1061 |  | 1.332 | 0.51231 | 346.3662 | 25.64 | 73.76
2021-01-03 12:50 | 3.8953 | 0.74312 | 0.1916 | 1.3307 | 42.9608 |  | 1.3321 | 0.51965 | 345.2824 | 25.66 | 73.78
2021-01-03 12:55 | 3.6391 | 0.73901 | 0.19371 | 1.3265 | 41.1884 |  | 1.3394 | 0.54162 | 345.7753 | 25.68 | 73.76
2021-01-03 13:00 | 3.6136 | 1.136 | 0.23583 | 1.9793 | 54.9576 |  | 1.3614 | 0.46113 | 344.6906 | 25.7 | 73.79
2021-01-03 13:05 | 3.5497 | 1.1333 | 0.24637 | 1.9836 | 65.6325 |  | 1.3615 | 0.29279 | 345.687 | 25.73 | 73.8
2021-01-03 13:10 | 3.6397 | 0.93972 | 0.22744 | 1.6679 | 69.1237 |  | 1.3616 | 0.24889 | 344.7536 | 25.76 | 73.83
2021-01-03 13:15 | 4.1654 | 0.94938 | 0.26325 | 1.7185 | 64.0312 |  | 1.347 | 0.23426 | 345.2254 | 25.79 | 73.84
2021-01-03 13:20 | 4.345 | 0.92057 | 0.30328 | 1.7144 | 61.1116 |  | 1.3544 | 0.22695 | 345.1644 | 25.83 | 73.79
2021-01-03 13:25 | 4.3833 | 0.87109 | 0.26115 | 1.5943 | 51.6669 |  | 1.3544 | 0.23427 | 344.1029 | 25.85 | 73.64
2021-01-03 13:30 | 3.9859 | 0.77627 | 0.22745 | 1.4173 | 47.9028 |  | 1.3543 | 0.23426 | 345.157 | 25.85 | 73.57
2021-01-03 13:35 | 3.5761 | 0.62381 | 0.18955 | 1.1457 | 58.2525 |  | 1.3471 | 0.19035 | 345.6083 | 25.89 | 73.61
2021-01-03 13:40 | 3.5377 | 0.66643 | 0.2022 | 1.2216 | 48.2158 |  | 1.3398 | 0.1684 | 344.5148 | 25.92 | 73.59
2021-01-03 13:45 | 4.1402 | 0.70491 | 0.20431 | 1.2848 | 44.4836 |  | 1.3179 | 0.19768 | 344.5005 | 25.93 | 73.57
2021-01-03 13:50 | 5.0376 | 0.76127 | 0.20852 | 1.3754 | 43.2645 |  |  |  | 343.9337 | 25.96 | 73.52
2021-01-03 13:55 | 4.704 | 0.77084 | 0.22115 | 1.4027 | 49.4244 |  | 1.3105 | 0.23428 | 345.0244 | 25.94 | 73.42
2021-01-03 14:00 | 5.0245 | 0.83818 | 0.238 | 1.5249 | 46.2155 |  | 1.3105 | 0.22697 | 345.0197 | 25.94 | 73.46
2021-01-03 14:05 | 4.3582 | 0.85194 | 0.24222 | 1.5481 | 44.2379 |  | 1.3179 | 0.23429 | 343.9396 | 25.96 | 73.47
2021-01-03 14:10 | 3.8967 | 0.98935 | 0.25907 | 1.7756 | 48.1343 |  | 1.3252 | 0.26358 | 343.9194 | 25.98 | 73.36
2021-01-03 14:15 | 4.4221 | 0.99206 | 0.25274 | 1.7734 | 41.9186 |  | 1.3398 | 0.3075 | 343.9087 | 26 | 73.17
2021-01-03 14:20 | 5.2681 | 1.1419 | 0.22747 | 1.9799 | 52.2148 |  | 1.3325 | 0.34411 | 343.367 | 26.01 | 73.19
2021-01-03 14:25 | 4.7041 | 1.0031 | 0.23379 | 1.7713 | 55.4749 |  | 1.3179 | 0.29286 | 343.86 | 26.04 | 73.02
2021-01-03 14:30 | 4.3964 | 0.95359 | 0.22326 | 1.6828 | 57.587 |  | 1.3179 | 0.29286 | 344.3493 | 26.07 | 72.88
2021-01-03 14:35 | 4.3964 | 0.95358 | 0.23589 | 1.6976 | 53.1464 |  | 1.3178 | 0.27089 | 343.9832 | 26.09 | 72.69
2021-01-03 14:40 | 3.8707 | 0.95216 | 0.23588 | 1.6954 | 60.5262 |  | 1.3251 | 0.24159 | 343.9894 | 26.1 | 72.5
2021-01-03 14:45 | 3.3451 | 0.92054 | 0.24009 | 1.649 | 69.8554 |  | 1.3324 | 0.27819 | 342.9408 | 26.11 | 72.4
2021-01-03 14:50 | 3.4478 | 0.82026 | 0.23799 | 1.4932 | 73.477 |  | 1.3251 | 0.22695 | 342.9194 | 26.12 | 72.44
2021-01-03 14:55 | 3.1915 | 0.87524 | 0.2401 | 1.5817 | 74.2167 |  | 1.3105 | 0.20499 | 343.4117 | 26.14 | 72.41
2021-01-03 15:00 | 2.7556 | 0.85461 | 0.26958 | 1.5796 | 68.3707 |  | 1.2958 | 0.16838 | 344.4391 | 26.16 | 72.27
2021-01-03 15:05 | 2.7809 | 0.88336 | 0.26955 | 1.6236 | 58.5715 |  | 1.2883 | 0.17568 | 343.4481 | 26.15 | 71.97
2021-01-03 15:10 | 4.2033 | 0.98085 | 0.26322 | 1.7688 | 44.4007 |  | 1.2956 | 0.23423 | 344.0211 | 26.12 | 71.96
2021-01-03 15:15 | 4.5494 | 0.88885 | 0.26744 | 1.6299 | 43.7874 |  | 1.303 | 0.23424 | 345.0507 | 26.12 | 72.08
2021-01-03 15:20 | 4.4726 | 0.90534 | 0.27165 | 1.6594 | 30.0289 |  | 1.303 | 0.21228 | 344.5287 | 26.12 | 72.08
2021-01-03 15:25 | 3.8318 | 0.95205 | 0.27376 | 1.7352 | 27.5274 |  | 1.2957 | 0.19032 | 343.4834 | 26.12 | 72.09
2021-01-03 15:30 | 3.4604 | 1.15 | 0.30326 | 2.066 | 39.7511 |  | 1.2958 | 0.16105 | 343.9341 | 26.16 | 72.13
2021-01-03 15:35 | 2.8581 | 1.1679 | 0.29695 | 2.0892 | 53.1429 |  | 1.2958 | 0.1391 | 343.3696 | 26.19 | 72.07
2021-01-03 15:40 | 2.6658 | 1.0538 | 0.30115 | 1.9164 | 49.5017 |  | 1.2958 | 0.13177 | 342.8562 | 26.19 | 72
2021-01-03 15:45 | 2.7939 | 0.99745 | 0.2843 | 1.8132 | 51.1313 |  | 1.3031 | 0.16105 | 343.3593 | 26.21 | 71.88
2021-01-03 15:50 | 4.0242 | 0.99194 | 0.28851 | 1.809 | 58.3589 |  | 1.303 | 0.23426 | 343.8624 | 26.23 | 71.76
2021-01-03 15:55 | 4.8313 | 1.0317 | 0.27375 | 1.8552 | 57.0323 |  | 1.3103 | 0.24156 | 344.9185 | 26.24 | 71.52
2021-01-03 16:00 | 4.1135 | 0.94102 | 0.26743 | 1.7098 | 61.1111 |  | 1.3176 | 0.22691 | 343.8834 | 26.24 | 71.45
2021-01-03 16:05 | 3.0241 | 0.78847 | 0.24846 | 1.455 | 53.07 |  | 1.3102 | 0.21958 | 344.4295 | 26.24 | 71.25
2021-01-03 16:10 | 3.024 | 0.93681 | 0.25266 | 1.6886 | 58.8403 |  | 1.3101 | 0.24153 | 343.9019 | 26.25 | 71.16
2021-01-03 16:15 | 4.1388 | 1.1346 | 0.27372 | 2.0129 | 60.378 |  | 1.3101 | 0.26349 | 342.8466 | 26.26 | 71.12
2021-01-03 16:20 | 3.7668 | 1.0328 | 0.26316 | 1.8442 | 52.5092 |  | 1.31 | 0.31469 | 343.9549 | 26.24 | 70.86
2021-01-03 16:25 | 3.3439 | 0.91607 | 0.22526 | 1.6294 | 47.9262 |  | 1.3099 | 0.24881 | 344.4983 | 26.23 | 70.82
2021-01-03 16:30 | 3.5746 | 0.91061 | 0.22737 | 1.6232 | 39.5947 |  | 1.31 | 0.2415 | 343.4317 | 26.24 | 70.87
2021-01-03 16:35 | 3.152 | 0.93127 | 0.26318 | 1.6907 | 34.9537 |  | 1.2954 | 0.24152 | 343.5628 | 26.26 | 70.89
2021-01-03 16:40 | 2.9342 | 0.93676 | 0.26528 | 1.7033 | 37.9981 |  | 1.2881 | 0.2342 | 343.3761 | 26.27 | 70.92
2021-01-03 16:45 | 2.6651 | 0.91343 | 0.25687 | 1.657 | 41.7095 |  | 1.2954 | 0.21225 | 343.8802 | 26.28 | 70.93
2021-01-03 16:50 | 3.088 | 0.92443 | 0.23582 | 1.6528 | 46.2309 |  | 1.2955 | 0.17566 | 344.3842 | 26.29 | 70.94
2021-01-03 16:55 | 3.562 | 0.87219 | 0.22949 | 1.5664 | 33.1698 |  | 1.3027 | 0.19029 | 344.9453 | 26.27 | 70.89
2021-01-03 17:00 | 3.69 | 0.91474 | 0.24211 | 1.6443 | 34.5217 |  | 1.3027 | 0.1976 | 343.9359 | 26.25 | 70.88
2021-01-03 17:05 | 3.8948 | 0.81994 | 0.22737 | 1.4842 | 36.3447 |  | 1.3099 | 0.21223 | 343.4624 | 26.22 | 70.89
2021-01-03 17:10 | 4.2024 | 0.83644 | 0.22316 | 1.5053 | 48.7987 |  | 1.31 | 0.23418 | 344.512 | 26.21 | 70.98
2021-01-03 17:15 | 4.1768 | 0.79525 | 0.22106 | 1.44 | 46.7805 |  | 1.31 | 0.18296 | 343.9828 | 26.21 | 71.04
2021-01-03 17:20 | 3.3952 | 0.66201 | 0.16632 | 1.1811 | 41.4804 |  | 1.3027 | 0.13905 | 342.9578 | 26.2 | 71.02
2021-01-03 17:25 | 2.7544 | 0.5974 | 0.18314 | 1.0989 | 34.9588 |  | 1.3025 | 0.13904 | 344.053 | 26.18 | 70.87
2021-01-03 17:30 | 2.6901 | 0.66326 | 0.16418 | 1.1809 | 33.8178 |  | 1.2951 | 0.14634 | 344.1325 | 26.14 | 70.76
2021-01-03 17:35 | 2.6901 | 0.77452 | 0.18524 | 1.3724 | 39.3325 |  | 1.2951 | 0.11708 | 343.5982 | 26.14 | 70.86
2021-01-03 17:40 | 2.293 | 0.69212 | 0.16208 | 1.223 | 43.4114 |  | 1.2732 | 0.11708 | 343.5865 | 26.15 | 70.82
2021-01-03 17:45 | 2.0751 | 0.62754 | 0.18102 | 1.1429 | 50.5408 |  | 1.2585 | 0.13902 | 343.6316 | 26.13 | 70.72
2021-01-03 17:50 | 2.3313 | 0.7113 | 0.19996 | 1.2903 | 48.3683 |  | 1.2585 | 0.18292 | 344.6878 | 26.12 | 70.76
2021-01-03 17:55 | 2.7924 | 0.77446 | 0.21469 | 1.4018 | 52.6209 |  | 1.2658 | 0.1756 | 345.2113 | 26.12 | 70.75
2021-01-03 18:00 | 2.4722 | 0.67421 | 0.21679 | 1.2481 | 61.2685 |  | 1.2658 | 0.1756 | 344.6963 | 26.12 | 70.69
2021-01-03 18:05 | 2.1005 | 0.57117 | 0.17258 | 1.0481 | 47.9019 |  | 1.2583 | 0.13169 | 345.3062 | 26.07 | 70.65
2021-01-03 18:10 | 1.6522 | 0.44484 | 0.16836 | 0.85023 | 40.8199 |  | 1.2583 | 0.10973 | 343.799 | 26.03 | 70.7
2021-01-03 18:15 | 1.4856 | 0.40363 | 0.15783 | 0.77653 | 25.921 |  | 1.2582 | 0.10973 | 343.8509 | 26 | 70.68
2021-01-03 18:20 | 1.4597 | 0.42276 | 0.16411 | 0.81213 | 16.1025 |  | 1.258 | 0.11702 | 344.8159 | 25.98 | 70.23
2021-01-03 18:25 | 1.344 | 0.36637 | 0.15985 | 0.72144 | 24.1051 |  | 1.2576 | 0.12429 | 345.4714 | 25.96 | 69.4
2021-01-03 18:30 | 1.7153 | 0.42265 | 0.16196 | 0.80982 | 22.7344 |  | 1.2576 | 0.13161 | 345.9733 | 25.96 | 69.58
2021-01-03 18:35 | 1.856 | 0.3897 | 0.17878 | 0.77612 | 20.0603 |  | 1.2649 | 0.11698 | 346.0299 | 25.93 | 69.52
2021-01-03 18:40 | 2.4322 | 0.45696 | 0.17248 | 0.87293 | 23.062 |  | 1.2796 | 0.16086 | 347.0906 | 25.9 | 69.82
2021-01-03 18:45 | 2.3172 | 0.47347 | 0.1725 | 0.89825 | 25.9114 |  | 1.2797 | 0.19013 | 345.9985 | 25.91 | 70.06
2021-01-03 18:50 | 2.2146 | 0.48991 | 0.18721 | 0.93817 | 29.781 |  | 1.2942 | 0.21205 | 345.4953 | 25.91 | 69.89
2021-01-03 18:55 | 2.0096 | 0.36637 | 0.16406 | 0.72564 | 26.7777 |  | 1.3087 | 0.1316 | 346.6238 | 25.87 | 69.76
2021-01-03 19:00 | 1.6509 | 0.34984 | 0.13879 | 0.67503 | 15.8486 |  | 1.3158 | 0.10965 | 346.2466 | 25.8 | 69.5
2021-01-03 19:05 | 3.4042 | 0.46919 | 0.143 | 0.86219 | 16.0226 |  | 1.3304 | 0.1462 | 345.7227 | 25.8 | 69.5
2021-01-03 19:10 | 3.4798 | 0.47452 | 0.15346 | 0.88083 | 22.4448 |  | 1.33 | 0.15346 | 347.454 | 25.76 | 68.71
2021-01-03 19:15 | 3.4414 | 0.42926 | 0.16187 | 0.81986 | 15.3213 |  | 1.3227 | 0.20461 | 345.8609 | 25.78 | 68.61
2021-01-03 19:20 | 3.2881 | 0.44849 | 0.14296 | 0.83042 | 21.0848 |  | 1.3154 | 0.19732 | 346.9215 | 25.75 | 68.92
2021-01-03 19:25 | 3.1348 | 0.41972 | 0.14507 | 0.78843 | 22.1509 |  | 1.3155 | 0.19002 | 344.8355 | 25.72 | 69.25
2021-01-03 19:30 | 3.0584 | 0.44858 | 0.13668 | 0.82428 | 17.6083 |  | 1.3157 | 0.12426 | 346.3864 | 25.7 | 69.71
2021-01-03 19:35 | 2.5722 | 0.35668 | 0.12407 | 0.6708 | 25.1949 |  | 1.2938 | 0.11695 | 345.3758 | 25.66 | 69.95
2021-01-03 19:40 | 2.2267 | 0.34296 | 0.10724 | 0.63084 | 23.4954 |  | 1.2865 | 0.1535 | 345.9469 | 25.62 | 70.11
2021-01-03 19:45 | 1.8941 | 0.43902 | 0.11566 | 0.78861 | 15.3575 |  | 1.2939 | 0.19006 | 346.4582 | 25.61 | 70.36
2021-01-03 19:50 | 1.5487 | 0.38556 | 0.11988 | 0.71088 | 20.4995 |  | 1.316 | 0.12429 | 347.4321 | 25.64 | 70.57
2021-01-03 19:55 | 1.4975 | 0.37183 | 0.11357 | 0.68143 | 14.2737 |  | 1.3233 | 0.1316 | 345.9001 | 25.61 | 70.65
2021-01-03 20:00 | 1.5616 | 0.40478 | 0.11778 | 0.73825 | 12.4209 |  | 1.3306 | 0.12429 | 346.4196 | 25.6 | 70.83
2021-01-03 20:05 | 1.4847 | 0.35537 | 0.10726 | 0.64988 | 14.9085 |  | 1.3306 | 0.12428 | 347.0075 | 25.56 | 70.85
2021-01-03 20:10 | 1.3695 | 0.29499 | 0.096743 | 0.55102 | 24.6251 |  | 1.3379 | 0.09504 | 345.488 | 25.52 | 70.96
2021-01-03 20:15 | 1.5872 | 0.39517 | 0.12199 | 0.72983 | 25.968 |  | 1.3379 | 0.058489 | 347.5985 | 25.49 | 71.27
2021-01-03 20:20 | 1.2799 | 0.34714 | 0.11357 | 0.64568 | 34.4152 |  | 1.3087 | 0.087733 | 347.1039 | 25.47 | 71.3
2021-01-03 20:25 | 1.2031 | 0.33889 | 0.1346 | 0.65406 | 35.5599 |  | 1.3013 | 0.087727 | 347.1713 | 25.43 | 71.29
2021-01-03 20:30 | 1.1007 | 0.29911 | 0.11778 | 0.57627 | 21.9328 |  | 1.294 | 0.08042 | 346.6555 | 25.41 | 71.5
2021-01-03 20:35 | 1.408 | 0.27169 | 0.098856 | 0.51531 | 19.5176 |  | 1.2941 | 0.10236 | 346.1413 | 25.38 | 71.84
2021-01-03 20:40 | 1.2928 | 0.24974 | 0.098858 | 0.48167 | 17.8591 |  | 1.2868 | 0.087739 | 346.1809 | 25.34 | 72.07
2021-01-03 20:45 | 1.3442 | 0.30054 | 0.10728 | 0.57007 | 12.2486 |  | 1.2797 | 0.117 | 347.7317 | 25.33 | 72.41
2021-01-03 20:50 | 2.0358 | 0.40764 | 0.090466 | 0.71531 | 22.1654 |  | 1.2945 | 0.17552 | 346.6102 | 25.35 | 72.75
2021-01-03 20:55 | 1.4211 | 0.34174 | 0.1115 | 0.63533 | 23.5979 |  | 1.3163 | 0.11701 | 347.1446 | 25.36 | 72.52
2021-01-03 21:00 | 1.2929 | 0.36776 | 0.10097 | 0.66469 | 18.9556 |  | 1.3234 | 0.080431 | 346.2017 | 25.31 | 72.32
2021-01-03 21:05 | 1.7793 | 0.43501 | 0.11569 | 0.78249 | 24.7213 |  | 1.3235 | 0.1243 | 345.6856 | 25.3 | 72.39
2021-01-03 21:10 | 1.3696 | 0.29364 | 0.092545 | 0.54265 | 17.6332 |  | 1.316 | 0.11698 | 346.2737 | 25.27 | 72.27
2021-01-03 21:15 | 1.2799 | 0.33616 | 0.11778 | 0.63306 | 12.6254 |  | 1.3233 | 0.11698 | 347.3956 | 25.22 | 72.36
2021-01-03 21:20 | 1.2416 | 0.30324 | 0.12199 | 0.5868 | 18.3903 |  | 1.3233 | 0.10967 | 346.3557 | 25.21 | 72.42
2021-01-03 21:25 | 1.3567 | 0.27578 | 0.10936 | 0.53208 | 18.2254 |  | 1.3305 | 0.11697 | 346.936 | 25.18 | 72.37
2021-01-03 21:30 | 1.2669 | 0.22086 | 0.086213 | 0.42476 | 6.7669 |  | 1.3376 | 0.10964 | 346.0211 | 25.11 | 72.2
2021-01-03 21:35 | 1.2156 | 0.20027 | 0.071489 | 0.37847 | 5.3026 |  | 1.3448 | 0.095016 | 346.1167 | 25.05 | 72.23
2021-01-03 21:40 | 1.3691 | 0.18381 | 0.077795 | 0.35954 | 17.5146 |  | 1.3521 | 0.10232 | 346.6932 | 25.01 | 72.36
2021-01-03 21:45 | 1.8555 | 0.21811 | 0.0778 | 0.41003 | 5.9785 |  | 1.3595 | 0.13888 | 346.6848 | 25 | 72.58
2021-01-03 21:50 | 2.2267 | 0.22772 | 0.073598 | 0.42266 | 8.016 |  | 1.3742 | 0.14619 | 346.1448 | 25 | 72.71
2021-01-03 21:55 | 1.3949 | 0.12895 | 0.073598 | 0.27336 | 10.0738 |  | 1.3888 | 0.11695 | 346.6689 | 25 | 72.72
2021-01-03 22:00 | 1.3693 | 0.16325 | 0.058879 | 0.30911 | 13.0326 |  | 1.3888 | 0.10965 | 347.727 | 24.99 | 72.8
2021-01-03 22:05 | 1.0621 | 0.13032 | 0.06098 | 0.26074 | 11.3123 |  | 1.3888 | 0.087714 | 346.1831 | 24.97 | 72.81
2021-01-03 22:10 | 0.99811 | 0.11386 | 0.050464 | 0.22499 | 11.793 |  | 1.3814 | 0.065783 | 346.758 | 24.94 | 72.81
2021-01-03 22:15 | 0.94692 | 0.18107 | 0.065183 | 0.34273 | 2.723 |  | 1.3741 | 0.043855 | 346.2578 | 24.92 | 72.88
2021-01-03 22:20 | 0.87009 | 0.18518 | 0.058872 | 0.34272 | 7.2986 |  | 1.3594 | 0.021926 | 347.3496 | 24.9 | 72.81
2021-01-03 22:25 | 0.98525 | 0.18106 | 0.060974 | 0.33851 | 12.253 |  | 1.3448 | 0.036544 | 346.8591 | 24.87 | 72.94
2021-01-03 22:30 | 0.63978 | 0.15637 | 0.058872 | 0.29856 | 4.0229 |  | 1.3375 | 0.05847 | 346.847 | 24.88 | 72.9
2021-01-03 22:35 | 0.58857 | 0.12893 | 0.056767 | 0.2544 | 10.6046 |  | 1.3375 | 0.080394 | 347.9444 | 24.85 | 72.93
2021-01-03 22:40 | 0.55022 | 0.13717 | 0.05677 | 0.26703 | 7.8412 |  | 1.3522 | 0.051162 | 346.8994 | 24.83 | 73.17
2021-01-03 22:45 | 0.56304 | 0.17696 | 0.069388 | 0.34063 | 3.1632 |  | 1.3522 | 0.043855 | 346.8969 | 24.82 | 73.34
2021-01-03 22:50 | 0.52463 | 0.1262 | 0.056771 | 0.25021 | 10.8407 |  | 1.3522 | 0.029236 | 346.9398 | 24.79 | 73.4
2021-01-03 22:55 | 0.58863 | 0.107 | 0.067286 | 0.23129 | 12.6632 |  | 1.3522 | 0.021928 | 345.8806 | 24.79 | 73.47
2021-01-03 23:00 | 0.43503 | 0.098757 | 0.060972 | 0.21235 | 0.42991 |  | 1.3521 | 0.021926 | 346.9886 | 24.77 | 73.26
2021-01-03 23:05 | 0.42218 | 0.058972 | 0.04835 | 0.13874 | 1.9855 |  | 1.3519 | 0.021923 | 347.0946 | 24.72 | 73.05
2021-01-03 23:10 | 0.49888 | 0.076792 | 0.044141 | 0.16185 | 8.6166 |  | 1.3517 | 0.04384 | 347.2015 | 24.66 | 72.98
2021-01-03 23:15 | 0.52451 | 0.14674 | 0.056757 | 0.28168 | 2.6916 |  | 1.3591 | 0.043844 | 346.6389 | 24.67 | 73.16
2021-01-03 23:20 | 0.52456 | 0.12755 | 0.052558 | 0.24807 | 0.9007 |  | 1.3593 | 0.03654 | 347.1184 | 24.68 | 73.43
2021-01-03 23:25 | 0.51179 | 0.10699 | 0.050459 | 0.21235 | 6.2746 |  | 1.3667 | 0.036542 | 346.6065 | 24.65 | 73.75
2021-01-03 23:30 | 0.53743 | 0.1358 | 0.03995 | 0.24811 | -0.90083 |  | 1.3668 | 0.036545 | 346.5788 | 24.65 | 74
2021-01-03 23:35 | 0.48626 | 0.16324 | 0.050465 | 0.30279 | 1.9348 |  | 1.3668 | 0.036546 | 346.5887 | 24.63 | 74.21
2021-01-03 23:40 | 0.51187 | 0.16462 | 0.056775 | 0.30701 | 15.131 |  | 1.3669 | 0.029238 | 347.6404 | 24.62 | 74.36
2021-01-03 23:45 | 0.56306 | 0.11523 | 0.048363 | 0.225 | 2.6003 |  | 1.3596 | 0.021928 | 347.6781 | 24.59 | 74.47
2021-01-03 23:50 |  | 0.10289 | 0.046261 | 0.20186 | 3.7469 |  | 1.3596 | 0.021928 | 346.6504 | 24.57 | 74.55
2021-01-03 23:55 | 0.56304 | 0.11249 | 0.048362 | 0.21868 | 8.763 |  | 1.3595 | 0.036546 | 346.6703 | 24.56 | 74.52
2021-01-04 | 0.48627 | 0.12895 | 0.044158 | 0.24182 | 0.31736 |  | 1.3596 | 0.051166 | 347.7025 | 24.57 | 74.55
2021-01-04 00:05 | 0.33271 | 0.089166 | 0.04626 | 0.18504 | 5.5076 |  | 1.3522 | 0.0073093 | 347.3705 | 24.56 | 74.46
2021-01-04 00:10 | 0.47342 | 0.085042 | 0.037845 | 0.1661 | 9.0692 |  | 1.3448 | 0.021926 | 347.9769 | 24.52 | 74.33
2021-01-04 00:15 | 0.33266 | 0.1015 | 0.060971 | 0.21445 | -1.8015 |  | 1.3301 | 0.0073084 | 346.4352 | 24.5 | 74.31
2021-01-04 00:20 | 0.40942 | 0.075435 | 0.054661 | 0.17029 | 4.739 |  | 1.3228 | 0.03654 | 347.5242 | 24.48 | 74.27
2021-01-04 00:25 | 0.67805 | 0.087773 | 0.058862 | 0.1934 | 16.0583 |  | 1.3227 | 0.043846 | 346.5288 | 24.45 | 74.21
2021-01-04 00:30 | 0.6908 | 0.086396 | 0.05045 | 0.18288 | 9.3641 |  | 1.3226 | 0.073071 | 347.1031 | 24.43 | 74.07
2021-01-04 00:35 | 0.51168 | 0.067194 | 0.050447 | 0.15344 | 3.7045 |  | 1.3371 | 0.073068 | 347.6443 | 24.43 | 73.93
2021-01-04 00:40 | 0.57562 | 0.071305 | 0.048344 | 0.15764 | 9.8239 |  | 1.3517 | 0.073065 | 347.1426 | 24.42 | 73.86
2021-01-04 00:45 | 0.33256 | 0.069931 | 0.067258 | 0.17445 | 6.3136 |  | 1.3516 | 0.043837 | 347.695 | 24.41 | 73.77
2021-01-04 00:50 | 0.39647 | 0.053469 | 0.050437 | 0.1324 | -1.238 |  | 1.3588 | 0.043831 | 348.8508 | 24.36 | 73.58
2021-01-04 00:55 | 0.35807 | 0.053465 | 0.04623 | 0.12818 | 2.6293 |  | 1.3587 | 0.029219 | 346.8074 | 24.33 | 73.47
2021-01-04 01:00 | 0.3197 | 0.052093 | 0.044127 | 0.12398 | -9.0436 |  | 1.344 | 0.036522 | 347.883 | 24.32 | 73.41
2021-01-04 01:05 |  |  |  |  | -1.0026 |  |  |  | 347.8864 | 24.31 | 73.53
2021-01-04 01:10 |  |  |  |  | 2.5576 |  |  |  | 347.9305 | 24.28 | 73.58
2021-01-04 01:15 |  |  |  |  | 2.8031 |  |  |  | 347.9415 | 24.27 | 73.63
2021-01-04 01:20 |  |  |  |  | -3.9385 |  |  |  | 346.9591 | 24.22 | 73.74
2021-01-04 01:25 |  |  |  |  | 7.2837 |  |  |  | 345.9335 | 24.2 | 73.79
2021-01-04 01:30 |  |  |  |  | 6.2195 |  |  |  | 346.5215 | 24.16 | 73.83
2021-01-04 01:35 |  |  |  |  | -0.94119 |  |  |  | 347.5301 | 24.17 | 74.09
2021-01-04 01:40 |  |  |  |  | 6.4451 |  |  |  | 347.5423 | 24.16 | 74.13
2021-01-04 01:45 |  |  |  |  | 6.0456 |  |  |  | 347.609 | 24.13 | 73.97
2021-01-04 01:50 |  |  |  |  | -3.4269 |  |  |  | 346.7863 | 24.08 | 74.16
2021-01-04 01:55 |  |  |  |  | -0.92068 |  |  |  | 347.3759 | 24.02 | 74.49
2021-01-04 02:00 |  |  |  |  | 5.9842 |  |  |  | 346.9424 | 23.95 | 74.7
2021-01-04 02:05 |  |  |  |  | -1.5549 |  |  |  | 346.427 | 23.94 | 74.75
2021-01-04 02:10 | 0.43477 | 0.16587 | 0.054632 | 0.30888 | 6.5472 |  | 1.4535 | 0.0073042 | 348.4913 | 23.96 | 74.83
2021-01-04 02:15 | 0.31964 | 0.082237 | 0.035716 | 0.16177 | 16.478 |  | 1.4314 | 0.014606 | 347.5263 | 23.93 | 74.47
2021-01-04 02:20 | 0.38355 | 0.072639 | 0.029412 | 0.14076 | 1.3092 |  | 1.424 | 0.029211 | 347.588 | 23.89 | 74.51
2021-01-04 02:25 | 0.31965 | 0.090464 | 0.023111 | 0.16178 | 3.13 |  | 1.4169 | 0.036517 | 348.646 | 23.86 | 74.93
2021-01-04 02:30 | 0.31967 | 0.10692 | 0.031517 | 0.19541 | 12.2754 |  | 1.4169 | 0.036519 | 347.5725 | 23.86 | 75.12
2021-01-04 02:35 | 0.34527 | 0.13982 | 0.060937 | 0.27527 | 6.803 |  | 1.417 | 0.043826 | 346.9901 | 23.89 | 75.18
2021-01-04 02:40 | 0.29413 | 0.093221 | 0.042027 | 0.18492 | 4.4912 |  | 1.4171 | 0.036523 | 347.4997 | 23.89 | 75.34
2021-01-04 02:45 | 0.31973 | 0.16589 | 0.050437 | 0.30472 | 12.9122 |  | 1.4245 | 0.043832 | 347.9953 | 23.89 | 75.63
2021-01-04 02:50 | 0.33252 | 0.23033 | 0.050436 | 0.40349 | 5.9342 |  | 1.4245 | 0.043831 | 347.4752 | 23.89 | 75.57
2021-01-04 02:55 | 0.33249 | 0.28926 | 0.07775 | 0.52113 | 2.6395 |  | 1.4244 | 0.058437 | 348.0294 | 23.89 | 75.31
2021-01-04 03:00 | 0.52432 | 0.292 | 0.054636 | 0.50223 | 17.0546 |  | 1.4317 | 0.058438 | 347.976 | 23.93 | 75.19
2021-01-04 03:05 | 0.6138 | 0.34545 | 0.042025 | 0.57154 | 20.0713 |  | 1.4316 | 0.058434 | 347.473 | 23.93 | 74.97
2021-01-04 03:10 | 0.39635 | 0.19325 | 0.039917 | 0.33824 | 11.4455 |  | 1.4241 | 0.051121 | 348.1274 | 23.87 | 74.7
2021-01-04 03:15 | 0.3324 | 0.2275 | 0.042015 | 0.39074 | 5.7889 |  | 1.4313 | 0.051118 | 348.2077 | 23.82 | 74.72
2021-01-04 03:20 | 0.35799 | 0.23026 | 0.050422 | 0.40127 | 12.9286 |  | 1.4387 | 0.058424 | 347.6587 | 23.82 | 74.93
2021-01-04 03:25 | 0.44751 | 0.24124 | 0.058828 | 0.42861 | 13.0112 |  | 1.4388 | 0.073034 | 347.6743 | 23.79 | 75.25
2021-01-04 03:30 | 0.42197 | 0.44961 | 0.046226 | 0.73751 | 8.2041 |  | 1.4389 | 0.065735 | 348.1655 | 23.8 | 75.43
2021-01-04 03:35 | 0.47314 | 0.32626 | 0.079848 | 0.57995 | 12.8388 |  | 1.439 | 0.073043 | 347.5972 | 23.82 | 75.51
2021-01-04 03:40 | 0.5499 | 0.292 | 0.065143 | 0.51274 | 14.8243 |  | 1.4609 | 0.073047 | 347.5669 | 23.83 | 75.64
2021-01-04 03:45 | 0.58826 | 0.35918 | 0.063041 | 0.6136 | 12.1336 |  | 1.4755 | 0.080352 | 348.0823 | 23.84 | 75.59
2021-01-04 03:50 | 0.53707 | 0.33448 | 0.058834 | 0.57153 | 15.8052 |  | 1.4535 | 0.065737 | 346.5045 | 23.86 | 75.26
2021-01-04 03:55 | 0.66493 | 0.37833 | 0.077743 | 0.65556 | 27.487 |  | 1.4535 | 0.087647 | 347.5561 | 23.87 | 75.12
2021-01-04 04:00 | 0.93353 | 0.39344 | 0.079851 | 0.68293 | 20.8496 |  | 1.439 | 0.094959 | 346.3941 | 23.94 | 75.06
2021-01-04 04:05 | 0.92087 | 0.50181 | 0.07776 | 0.84696 | 22.4283 |  | 1.4538 | 0.094972 | 345.7133 | 24.03 | 75.12
2021-01-04 04:10 | 1.0232 | 0.59095 | 0.071458 | 0.9794 | 31.6382 |  | 1.4466 | 0.080364 | 347.2089 | 24.09 | 74.97
2021-01-04 04:15 | 1.2278 | 0.46066 | 0.079858 | 0.78597 | 24.7292 |  | 1.4391 | 0.080357 | 346.6785 | 24.12 | 74.55
2021-01-04 04:20 | 1.2021 | 0.37975 | 0.077753 | 0.65985 | 26.4879 |  | 1.4245 | 0.087659 | 346.6935 | 24.12 | 74.41
2021-01-04 04:25 | 1.3939 | 0.47434 | 0.092461 | 0.81954 | 30.9888 |  | 1.439 | 0.12418 | 347.2272 | 24.12 | 74.34
2021-01-04 04:30 | 1.1253 | 0.44139 | 0.11346 | 0.79004 | 30.6685 |  | 1.4316 | 0.10956 | 345.6612 | 24.14 | 73.92
2021-01-04 04:35 | 1.0997 | 0.55519 | 0.13238 | 0.98339 | 31.3963 |  | 1.4536 | 0.13148 | 347.5266 | 24.18 | 73.97
2021-01-04 04:40 | 1.0615 | 0.66081 | 0.17442 | 1.1873 | 34.5609 |  | 1.461 | 0.1388 | 346.9069 | 24.23 | 74.07
2021-01-04 04:45 | 1.3428 | 1.0077 | 0.16181 | 1.7064 | 34.5399 |  | 1.4902 | 0.12418 | 347.3802 | 24.28 | 73.8
2021-01-04 04:50 | 1.5729 | 1.0405 | 0.1744 | 1.7693 | 30.7823 |  | 1.4828 | 0.12417 | 348.9322 | 24.33 | 73.29
2021-01-04 04:55 | 1.573 | 1.63 | 0.23325 | 2.7318 | 36.3087 |  | 1.5048 | 0.1534 | 347.2742 | 24.38 | 73.26
2021-01-04 05:00 | 1.7518 | 1.8505 | 0.20802 | 3.0467 | 50.6573 |  | 1.5192 | 0.20451 | 348.2913 | 24.44 | 72.68
2021-01-04 05:05 | 1.7646 | 1.6984 | 0.25004 | 2.8534 | 57.5318 |  | 1.5484 | 0.20451 | 347.6359 | 24.55 | 72.21
2021-01-04 05:10 | 2.0714 | 1.738 | 0.25212 | 2.9162 | 71.6637 |  | 1.5337 | 0.23371 | 348.6324 | 24.62 | 71.67
2021-01-04 05:15 | 2.6335 | 1.8843 | 0.26888 | 3.1594 | 89.0263 |  | 1.5334 | 0.29208 | 347.5626 | 24.69 | 70.8
2021-01-04 05:20 | 3.3876 | 1.9556 | 0.3382 | 3.3378 | 96.6132 |  | 1.5407 | 0.31399 | 346.4238 | 24.77 | 70.41
2021-01-04 05:25 | 3.9765 | 1.945 | 0.36767 | 3.349 | 99.1377 |  | 1.541 | 0.32865 | 346.7668 | 24.87 | 70.58
2021-01-04 05:30 | 5.1921 | 2.0536 | 0.36984 | 3.5177 | 109.8062 |  | 1.5413 | 0.36524 | 347.1231 | 24.96 | 70.77
2021-01-04 05:35 | 5.0903 | 2.5995 | 0.35517 | 4.3398 | 108.1912 |  | 1.5415 | 0.35066 | 347.0274 | 25.01 | 70.89
2021-01-04 05:40 | 3.8502 | 2.9564 | 0.45821 | 4.9919 | 101.2454 |  | 1.549 | 0.30687 | 346.427 | 25.04 | 71.12
2021-01-04 05:45 | 3.6968 | 3.0278 | 0.46033 | 5.1014 | 119.496 |  | 1.5782 | 0.34341 | 345.2582 | 25.13 | 70.87
2021-01-04 05:50 | 2.7115 | 2.4776 | 0.47918 | 4.2769 | 133.1592 |  | 1.5707 | 0.3872 | 345.7858 | 25.17 | 70.27
2021-01-04 05:55 | 3.0442 | 2.6272 | 0.43507 | 4.4621 | 121.5228 |  | 1.6146 | 0.42375 | 344.657 | 25.22 | 70.25
2021-01-04 06:00 | 3.7226 | 2.6714 | 0.35314 | 4.4479 | 126.2253 |  | 1.6149 | 0.32151 | 345.0569 | 25.29 | 70.34
2021-01-04 06:05 | 3.3896 | 2.6053 | 0.42247 | 4.418 | 138.9418 |  | 1.6585 | 0.35801 | 344.5339 | 25.32 | 69.9
2021-01-04 06:10 | 2.8011 | 2.6271 | 0.44767 | 4.4725 | 138.4147 |  | 1.6585 | 0.33608 | 345.5261 | 25.38 | 69.54
2021-01-04 06:15 | 2.878 | 2.7424 | 0.49393 | 4.6997 | 145.4283 |  | 1.6366 | 0.27033 | 345.9707 | 25.44 | 69.38
2021-01-04 06:20 | 2.9291 | 2.416 | 0.40775 | 4.1112 | 161.8215 |  | 1.6804 | 0.67217 | 345.3997 | 25.48 | 69.22
2021-01-04 06:25 | 3.0316 | 2.0898 | 0.34051 | 3.5438 | 158.3073 |  | 2.7984 | 0.73065 | 345.3752 | 25.49 | 69.29
2021-01-04 06:30 | 4.2343 | 2.1064 | 0.33633 | 3.5651 | 140.4301 |  | 2.309 | -0.036535 | 344.8256 | 25.49 | 69.51
2021-01-04 06:35 | 5.2836 | 2.1778 | 0.34686 | 3.683 | 134.2767 |  | 1.8488 | 0.27038 | 345.8081 | 25.53 | 69.51
2021-01-04 06:40 | 5.0154 | 2.3947 | 0.37843 | 4.0513 | 132.9898 |  | 1.6736 | 0.32156 | 346.2407 | 25.58 | 69.59
2021-01-04 06:45 | 4.5556 | 2.638 | 0.42476 | 4.4662 | 137.3136 |  | 1.6227 | 0.34354 | 345.015 | 25.68 | 69.71
2021-01-04 06:50 | 5.0673 | 2.2359 | 0.35955 | 3.7869 | 156.6245 |  | 1.608 | 0.29967 | 345.4615 | 25.76 | 69.25
2021-01-04 06:55 | 5.0029 | 2.1905 | 0.38896 | 3.7467 | 140.8695 |  | 1.586 | 0.32889 | 344.964 | 25.76 | 69.03
2021-01-04 07:00 | 3.7109 | 2.4335 | 0.42054 | 4.1507 | 125.9047 |  | 1.5496 | 0.29237 | 344.8658 | 25.82 | 69.03
2021-01-04 07:05 | 2.9306 | 2.5298 | 0.45002 | 4.3277 | 124.0333 |  | 1.5058 | 0.29971 | 343.7048 | 25.89 | 69.03
2021-01-04 07:10 | 2.9821 | 2.7481 | 0.42482 | 4.6372 | 113.9171 |  | 1.5133 | 0.32897 | 345.1886 | 25.94 | 69.06
2021-01-04 07:15 | 3.4812 | 2.7357 | 0.45636 | 4.6519 | 99.2641 |  | 1.5571 | 0.32897 | 344.1125 | 25.97 | 68.9
2021-01-04 07:20 | 5.0043 | 2.7372 | 0.42903 | 4.6247 | 116.8363 |  | 1.5572 | 0.36553 | 344.5587 | 26.03 | 68.72
2021-01-04 07:25 | 4.4157 | 2.7729 | 0.37225 | 4.6227 | 118.2117 |  | 1.5572 | 0.32168 | 344.4912 | 26.08 | 68.6
2021-01-04 07:30 | 3.6351 | 2.4328 | 0.35124 | 4.0803 | 99.6318 |  | 1.528 | 0.30707 | 344.9415 | 26.13 | 68.52
2021-01-04 07:35 | 4.7356 | 2.8031 | 0.43114 | 4.7299 | 119.0088 |  | 1.5133 | 0.37285 | 344.9492 | 26.14 | 68.32
2021-01-04 07:40 | 4.7612 | 2.2529 | 0.34912 | 3.8024 | 130.6306 |  | 1.5206 | 0.38016 | 344.948 | 26.14 | 68.33
2021-01-04 07:45 | 5.5808 | 2.1529 | 0.35545 | 3.6555 | 126.9445 |  | 1.5573 | 0.46792 | 344.9435 | 26.12 | 68.64
2021-01-04 07:50 | 5.3 | 1.9694 | 0.34499 | 3.3637 | 129.341 |  | 1.5795 | 0.4095 | 344.3422 | 26.14 | 69.02
2021-01-04 07:55 | 3.9179 | 1.7857 | 0.34714 | 3.0843 | 120.4973 |  | 1.5431 | 0.3291 | 345.3087 | 26.17 | 69.26
2021-01-04 08:00 | 3.8923 | 1.8831 | 0.35556 | 3.2421 | 118.3972 |  | 1.5504 | 0.33642 | 343.7196 | 26.19 | 69.17
2021-01-04 08:05 | 3.956 | 1.9749 | 0.36394 | 3.3912 | 129.3867 |  | 1.5796 | 0.33639 | 344.2838 | 26.18 | 68.96
2021-01-04 08:10 | 3.6486 | 2.1245 | 0.3471 | 3.6036 | 129.7424 |  | 1.6453 | 0.41682 | 344.8018 | 26.19 | 68.86
2021-01-04 08:15 | 3.6485 | 2.2109 | 0.39127 | 3.7801 | 116.2914 |  | 1.6087 | 0.35099 | 344.2556 | 26.22 | 68.65
2021-01-04 08:20 | 3.3026 | 2.0378 | 0.3681 | 3.4917 | 121.4646 |  | 1.594 | 0.29979 | 344.2694 | 26.23 | 68.4
2021-01-04 08:25 | 2.8033 | 1.7441 | 0.34706 | 3.0226 | 107.1361 |  | 1.5208 | 0.27785 | 343.73 | 26.25 | 68.27
2021-01-04 08:30 | 2.7012 | 1.7772 | 0.36392 | 3.086 | 108.1496 |  | 1.5137 | 0.26325 | 345.2424 | 26.27 | 68.45
2021-01-04 08:35 | 2.65 | 1.7621 | 0.34288 | 3.0439 | 124.1463 |  | 1.499 | 0.29249 | 343.6421 | 26.3 | 68.32
2021-01-04 08:40 | 2.2015 | 1.8249 | 0.35544 | 3.1527 | 116.1068 |  | 1.4841 | 0.24858 | 343.7143 | 26.29 | 67.86
2021-01-04 08:45 | 2.7517 | 1.8975 | 0.31967 | 3.2283 | 117.7286 |  | 1.4841 | 0.2705 | 344.2435 | 26.3 | 67.67
2021-01-04 08:50 | 3.4048 | 1.7125 | 0.26502 | 2.8899 | 108.5959 |  | 1.5061 | 0.29977 | 344.7086 | 26.32 | 67.87
2021-01-04 08:55 | 4.1472 | 1.7578 | 0.3155 | 3.0098 | 97.7008 |  | 1.5208 | 0.31439 | 344.7074 | 26.32 | 67.88
2021-01-04 09:00 | 3.1491 | 1.6344 | 0.33235 | 2.8376 | 102.3677 |  | 1.499 | 0.31442 | 344.1136 | 26.36 | 67.93
2021-01-04 09:05 | 2.8677 | 1.5906 | 0.33448 | 2.7705 | 94.2134 |  | 1.4552 | 0.28519 | 344.5615 | 26.4 | 68
2021-01-04 09:10 | 2.5734 | 1.5427 | 0.38499 | 2.7497 | 84.9095 |  | 1.4114 | 0.30715 | 344.5037 | 26.43 | 68.07
2021-01-04 09:15 | 2.074 | 1.2736 | 0.345 | 2.2972 | 72.7573 |  | 1.426 | 0.27057 | 342.9254 | 26.46 | 67.77
2021-01-04 09:20 | 2.3169 | 1.6302 | 0.38912 | 2.8879 | 64.2475 |  | 1.4696 | 0.27784 | 343.485 | 26.47 | 67.33
2021-01-04 09:25 | 2.138 | 1.4534 | 0.31765 | 2.5454 | 61.9011 |  | 1.4698 | 0.21938 | 344.9443 | 26.52 | 67.53
2021-01-04 09:30 | 1.882 | 1.2668 | 0.30505 | 2.2448 | 60.8196 |  | 1.4261 | 0.21208 | 343.8886 | 26.51 | 67.76
2021-01-04 09:35 | 2.0354 | 1.2776 | 0.32184 | 2.2802 | 72.9073 |  | 1.3966 | 0.2413 | 343.4302 | 26.49 | 67.51
2021-01-04 09:40 | 2.6246 | 1.4507 | 0.38289 | 2.6066 | 76.9816 |  | 1.3895 | 0.28521 | 343.8682 | 26.53 | 67.66
2021-01-04 09:45 | 2.8298 | 1.4948 | 0.38294 | 2.6743 | 92.8487 |  | 1.3897 | 0.27062 | 343.778 | 26.57 | 67.86
2021-01-04 09:50 | 2.9969 | 1.653 | 0.38301 | 2.9147 | 90.7254 |  | 1.3899 | 0.25604 | 344.7083 | 26.61 | 68.24
2021-01-04 09:55 | 2.8437 | 1.7535 | 0.36414 | 3.052 | 84.0095 |  | 1.3975 | 0.2634 | 343.5676 | 26.64 | 68.63
2021-01-04 10:00 | 2.5367 | 1.5945 | 0.36841 | 2.8125 | 65.9848 |  | 1.3904 | 0.30004 | 343.9741 | 26.69 | 68.89
2021-01-04 10:05 | 2.9214 | 1.7788 | 0.46952 | 3.1961 | 74.4497 |  | 1.3833 | 0.32935 | 341.8129 | 26.72 | 69.11
2021-01-04 10:10 | 2.7807 | 1.5083 | 0.39796 | 2.7078 | 74.9777 |  | 1.376 | 0.29278 | 343.3063 | 26.76 | 69.14
2021-01-04 10:15 | [8 empty] | 343.846 | 26.76 | 68.99
2021-01-04 10:20 | [8 empty] | 342.8199 | 26.77 | 68.73
2021-01-04 10:25 | [8 empty] | 342.3776 | 26.76 | 68.23
2021-01-04 10:30 | [8 empty] | 342.4485 | 26.76 | 67.66
2021-01-04 10:35 | [8 empty] | 341.833 | 26.81 | 67.76
2021-01-04 10:40 | [8 empty] | 342.2836 | 26.85 | 67.8
2021-01-04 10:45 | [8 empty] | 342.7164 | 26.88 | 68.11
2021-01-04 10:50 | [8 empty] | 342.6545 | 26.91 | 68.21
2021-01-04 10:55 | [8 empty] | 342.5332 | 26.96 | 68.52
2021-01-04 11:00 | [8 empty] | 342.9854 | 26.98 | 68.8
2021-01-04 11:05 | [8 empty] | 342.9158 | 26.99 | 69.22
2021-01-04 11:10 | [8 empty] | 342.8903 | 27.01 | 69.16
2021-01-04 11:15 | [8 empty] | 341.8091 | 27.03 | 69.22
2021-01-04 11:20 | [8 empty] | 342.8304 | 27.05 | 69.11
2021-01-04 11:25 | [8 empty] | 342.2453 | 27.08 | 69.23
2021-01-04 11:30 | [8 empty] | 342.2707 | 27.07 | 69.16
2021-01-04 11:35 | [8 empty] | 342.7731 | 27.07 | 69.3
2021-01-04 11:40 | [8 empty] | 342.6942 | 27.09 | 69.66
2021-01-04 11:45 | [8 empty] | 341.588 | 27.12 | 69.79
2021-01-04 11:50 | [8 empty] | 343.2 | 27.11 | 69.51
2021-01-04 11:55 | [8 empty] | 341.3045 | 27.12 | 69.24
2021-01-04 12:00 | [8 empty] | 342.017 | 27.09 | 68.11
2021-01-04 12:05 | [8 empty] | 341.2089 | 27.09 | 66.28
2021-01-04 12:10 | [8 empty] | 341.8 | 27.09 | 65.72
2021-01-04 12:15 | [8 empty] | 342.7762 | 27.12 | 65.84
2021-01-04 12:20 | [8 empty] | 342.7372 | 27.14 | 65.89
2021-01-04 12:25 | [8 empty] | 341.8333 | 27.16 | 65.87
2021-01-04 12:30 | [8 empty] | 342.3045 | 27.17 | 66.12
2021-01-04 12:35 | [8 empty] | 340.6704 | 27.19 | 66.46
2021-01-04 12:40 | [8 empty] | 343.0451 | 27.2 | 66.78
2021-01-04 12:45 | [8 empty] | 341.4063 | 27.24 | 66.89
2021-01-04 12:50 | [8 empty] | 342.3781 | 27.26 | 67.16
2021-01-04 12:55 | [8 empty] | 341.7486 | 27.27 | 67.89
2021-01-04 13:00 | [8 empty] | 341.7116 | 27.28 | 68.05
2021-01-04 13:05 | [8 empty] | 341.3212 | 27.3 | 68.08
2021-01-04 13:10 | [8 empty] | 341.3377 | 27.29 | 68.08
2021-01-04 13:15 | [8 empty] | 341.8899 | 27.29 | 67.82
2021-01-04 13:20 | [8 empty] | 341.9387 | 27.29 | 67.44
2021-01-04 13:25 | [8 empty] | 341.4747 | 27.28 | 67.14
2021-01-04 13:30 | [8 empty] | 342.0701 | 27.26 | 66.8
2021-01-04 13:35 | [8 empty] | 342.165 | 27.26 | 66.06
2021-01-04 13:40 | [8 empty] | 341.7675 | 27.26 | 65.11
2021-01-04 13:45 | [8 empty] | 342.8607 | 27.27 | 64.56
2021-01-04 13:50 | [8 empty] | 342.8393 | 27.31 | 64.22
2021-01-04 13:55 | [8 empty] | 342.2743 | 27.35 | 64.07
2021-01-04 14:00 | [8 empty] | 342.7242 | 27.38 | 64.23
2021-01-04 14:05 | [8 empty] | 342.8491 | 27.42 | 65.5
2021-01-04 14:10 | [8 empty] | 342.6563 | 27.43 | 66.86
2021-01-04 14:15 | [8 empty] | 341.3263 | 27.39 | 66.89
2021-01-04 14:20 | [8 empty] | 341.917 | 27.38 | 66.46
2021-01-04 14:25 | [8 empty] | 341.3164 | 27.39 | 65.68
2021-01-04 14:30 | [8 empty] | 341.3581 | 27.4 | 65.23
2021-01-04 14:35 | [8 empty] | 341.8179 | 27.42 | 65.44
2021-01-04 14:40 | [8 empty] | 341.1966 | 27.45 | 65.85
2021-01-04 14:45 | [8 empty] | 341.5882 | 27.49 | 66.33
2021-01-04 14:50 | [8 empty] | 341.0445 | 27.49 | 66.52
2021-01-04 14:55 | [8 empty] | 341.5009 | 27.51 | 66.75
2021-01-04 15:00 | 7.0629 | 2.1395 | 0.4002 | 3.6797 | 116.5239 | 122.7998 | 1.3033 | 0.73218 | 340.8959 | 27.56 | 66.78
2021-01-04 15:05 | 7.1018 | 1.9899 | 0.39391 | 3.444 | 131.4734 | 121.1668 | 1.34 | 0.69562 | 341.3702 | 27.58 | 66.87
2021-01-04 15:10 | 5.9485 | 1.7838 | 0.32863 | 3.063 | 139.6457 | 80.6019 | 1.3327 | 0.58582 | 341.3368 | 27.59 | 67
2021-01-04 15:15 | 4.8711 | 1.5652 | 0.3307 | 2.7299 | 128.6386 | 102.5294 | 1.3253 | 0.41736 | 341.912 | 27.57 | 66.82
2021-01-04 15:20 | 5.5875 | 1.7241 | 0.35799 | 3.0008 | 141.2877 | 135.1055 | 1.3542 | 0.49777 | 341.5377 | 27.52 | 66.34
2021-01-04 15:25 | 5.742 | 1.8535 | 0.34118 | 3.1823 | 160.8573 | 143.3032 | 1.4422 | 0.54176 | 341.8205 | 27.54 | 66.63
2021-01-04 15:30 | 5.5878 | 1.6583 | 0.26956 | 2.8093 | 147.4883 | 137.4814 | 1.4348 | 0.44656 | 342.2192 | 27.51 | 66.66
2021-01-04 15:35 | 4.531 | 1.3543 | 0.21032 | 2.2862 | 130.1664 | 82.9719 | 1.3233 | 0.34362 | 341.883 | 27.28 | 64.1
2021-01-04 15:40 | 4.2234 | 1.3829 | 0.19289 | 2.3126 | 56.6317 |  | 1.2827 | 0.36441 | 344.3139 | 26.25 | 59.12
2021-01-04 15:45 | 4.8071 | 2.0449 | 0.25981 | 3.3943 | 38.987 | -16.3925 | 1.3256 | 0.63365 | 346.5916 | 25.39 | 60.18
2021-01-04 15:50 | 4.7807 | 2.4094 | 0.2451 | 3.9383 | 52.4931 | 121.3145 | 1.4054 | 0.63353 | 347.7188 | 25.08 | 60.67
2021-01-04 15:55 | 5.1637 | 2.303 | 0.28283 | 3.813 | 45.0425 | 101.0193 | 1.3983 | 0.64088 | 347.8458 | 24.94 | 61.5
2021-01-04 16:00 | 4.9618 | 2.1085 | 0.30181 | 3.5316 | 44.0309 | 70.1228 | 1.428 | 0.72129 | 347.6292 | 25.15 | 61.95
2021-01-04 16:05 | 4.452 | 1.946 | 0.2725 | 3.2553 | 69.2527 | 71.406 | 1.4282 | 0.8088 | 347.4175 | 25.3 | 61.72
2021-01-04 16:10 | 4.8225 | 1.8518 | 0.25366 | 3.0922 | 95.1035 | 41.4687 | 1.4356 | 0.5174 | 346.304 | 25.32 | 62
2021-01-04 16:15 | 4.8491 | 1.7264 | 0.23485 | 2.8832 | 81.0976 | 36.2918 | 1.3922 | 0.43734 | 346.3793 | 25.34 | 62.52
2021-01-04 16:20 | 4.6599 | 1.9297 | 0.24125 | 3.1971 | 68.5528 | 75.9883 | 1.4293 | 0.36462 | 346.0189 | 25.51 | 63.29
2021-01-04 16:25 | 4.3683 | 2.1333 | 0.28125 | 3.5492 | 104.4213 | 121.1487 | 1.4008 | 0.36479 | 344.9957 | 25.8 | 63.6
2021-01-04 16:30 | 4.536 | 1.9711 | 0.28765 | 3.309 | 138.8259 | 125.8745 | 1.394 | 0.42332 | 344.582 | 26.05 | 63.71
2021-01-04 16:35 | 4.013 | 1.7002 | 0.27301 | 2.8792 | 148.3959 | 124.3892 | 1.4308 | 0.32121 | 345.6335 | 26.28 | 63.54
2021-01-04 16:40 | 3.5282 | 1.6581 | 0.24576 | 2.7853 | 166.7443 | 161.5083 | 1.4165 | 0.31398 | 344.2836 | 26.48 | 63.41
2021-01-04 16:45 | 3.2987 | 1.7243 | 0.25002 | 2.893 | 175.2477 | 145.8198 | 1.3803 | 0.27022 | 344.9218 | 26.62 | 63.52
2021-01-04 16:50 | 4.0154 | 1.301 | 0.18912 | 2.1833 | 148.1868 | 85.403 | 1.3294 | 0.27757 | 345.3403 | 26.66 | 63.83
2021-01-04 16:55 | 4.0797 | 1.3134 | 0.19964 | 2.2129 | 92.5015 | 68.2225 | 1.3295 | 0.2849 | 344.3332 | 26.6 | 64.32
2021-01-04 17:00 | 3.9006 | 1.3806 | 0.21645 | 2.3327 | 80.0284 | 55.228 | 1.3587 | 0.27029 | 345.3929 | 26.59 | 64.32
2021-01-04 17:05 | 3.5934 | 1.46 | 0.19753 | 2.4354 | 86.9998 | 63.8483 | 1.3586 | 0.25566 | 345.7894 | 26.57 | 64.26
2021-01-04 17:10 | 3.555 | 1.5258 | 0.1702 | 2.5089 | 99.049 | 86.2203 | 1.3367 | 0.31409 | 346.8767 | 26.54 | 64.31
2021-01-04 17:15 | 2.9668 | 1.2228 | 0.1555 | 2.0299 | 81.9151 | 69.8125 | 1.3221 | 0.24835 | 346.3355 | 26.55 | 64.33
2021-01-04 17:20 | 2.34 | 0.88689 | 0.13868 | 1.5002 | 74.2062 | 66.8408 | 1.322 | 0.23373 | 345.3618 | 26.51 | 64.28
2021-01-04 17:25 | 2.3273 | 0.82384 | 0.12607 | 1.3889 | 69.6134 | 26.9042 | 1.322 | 0.25564 | 345.8943 | 26.5 | 64.33
2021-01-04 17:30 | 2.5701 | 0.86492 | 0.14497 | 1.4707 | 50.3069 | 36.917 | 1.322 | 0.18989 | 345.9491 | 26.47 | 64.28
2021-01-04 17:35 | 2.3015 | 1.0362 | 0.15548 | 1.7438 | 50.8786 | 57.1182 | 1.3146 | 0.17528 | 345.469 | 26.44 | 64.33
2021-01-04 17:40 | 2.1096 | 0.9841 | 0.14076 | 1.6492 | 70.8626 | 78.268 | 1.3146 | 0.18988 | 346.5881 | 26.39 | 64.39
2021-01-04 17:45 | 2.0457 | 0.7785 | 0.12605 | 1.3194 | 76.0173 | 36.9654 | 1.3146 | 0.17527 | 347.194 | 26.32 | 64.64
2021-01-04 17:50 | 2.0458 | 0.71138 | 0.13446 | 1.2228 | 58.0592 | 35.8523 | 1.3146 | 0.16798 | 346.7348 | 26.25 | 65.05
2021-01-04 17:55 | 2.0331 | 0.69772 | 0.10506 | 1.1746 | 52.0894 | 38.4942 | 1.3074 | 0.16069 | 347.0582 | 26.25 | 65.33
2021-01-04 18:00 | 1.445 | 0.61686 | 0.10926 | 1.0548 | 50.1674 | 40.1524 | 1.3001 | 0.13147 | 346.5731 | 26.21 | 65.55
2021-01-04 18:05 | 2.417 | 0.71014 | 0.1429 | 1.2314 | 30.9993 | 18.8349 | 1.3076 | 0.16801 | 347.1247 | 26.16 | 65.99
2021-01-04 18:10 | 2.3021 | 0.59915 | 0.1303 | 1.0487 | 26.0705 | 17.8851 | 1.315 | 0.15342 | 346.6373 | 26.1 | 66.5
2021-01-04 18:15 | 2.5967 | 0.59514 | 0.1093 | 1.0194 | 39.3681 | 44.6383 | 1.3225 | 0.15344 | 347.6855 | 26.05 | 67.17
2021-01-04 18:20 | 2.0341 | 0.45942 | 0.11772 | 0.81983 | 45.1844 | 44.5704 | 1.308 | 0.12422 | 347.2258 | 25.97 | 67.73
2021-01-04 18:25 | 2.2135 | 0.49104 | 0.11564 | 0.86622 | 40.5241 | 33.7377 | 1.3082 | 0.10963 | 347.763 | 25.91 | 68.44
2021-01-04 18:30 | 1.4589 | 0.50346 | 0.12827 | 0.9 | 44.7996 | 16.9022 | 1.3011 | 0.073096 | 346.6489 | 25.92 | 68.86
2021-01-04 18:35 | 0.9598 | 0.44174 | 0.090423 | 0.76964 | 36.457 | 8.9684 | 1.3011 | 0.065788 | 345.8255 | 25.87 | 69.07
2021-01-04 18:40 | 0.95974 | 0.48836 | 0.10093 | 0.8495 | 23.5968 | 17.3418 | 1.2938 | 0.051166 | 346.4742 | 25.78 | 69.26
2021-01-04 18:45 | 0.92132 | 0.48011 | 0.10513 | 0.84106 | 21.6203 | 19.143 | 1.2937 | 0.051164 | 346.5552 | 25.72 | 69.41
2021-01-04 18:50 | 0.83176 | 0.3937 | 0.10724 | 0.71071 | 25.4697 | 5.9579 | 1.2937 | 0.065783 | 346.6198 | 25.66 | 69.7
2021-01-04 18:55 | 0.87017 | 0.34158 | 0.086213 | 0.6098 | 22.5733 | -4.5863 | 1.3011 | 0.065785 | 347.2378 | 25.57 | 70.16
2021-01-04 19:00 | 0.99817 | 0.36628 | 0.098832 | 0.65818 | 12.7664 | 14.6706 | 1.3084 | 0.073097 | 345.748 | 25.49 | 70.59
2021-01-04 19:05 | 1.0495 | 0.53098 | 0.10515 | 0.91905 | 17.3245 | 17.734 | 1.3013 | 0.10966 | 345.6896 | 25.5 | 70.95
2021-01-04 19:10 | 1.2031 | 0.5049 | 0.088329 | 0.86225 | 20.6518 | 19.4948 | 1.294 | 0.10235 | 346.2548 | 25.47 | 71.02
2021-01-04 19:15 | 1.3694 | 0.51312 | 0.082017 | 0.86854 | 17.7332 | 9.5526 | 1.2939 | 0.13159 | 347.3808 | 25.41 | 71.2
2021-01-04 19:20 | 1.7535 | 0.53785 | 0.063094 | 0.88963 | 20.8061 | 9.8501 | 1.3013 | 0.15353 | 345.2986 | 25.38 | 71.51
2021-01-04 19:25 | 2.3039 | 0.40477 | 0.079922 | 0.70037 | 29.8382 | 23.2132 | 1.3087 | 0.33631 | 347.9283 | 25.36 | 71.71
2021-01-04 19:30 | 2.048 | 0.41577 | 0.071513 | 0.70882 | 29.8498 | 37.2227 | 1.3087 | 0.29246 | 346.7362 | 25.32 | 72.09
2021-01-04 19:35 | 2.0613 | 0.31292 | 0.082047 | 0.5617 | 20.8533 | 18.7434 | 1.309 | 0.30715 | 347.6992 | 25.33 | 72.69
2021-01-04 19:40 | 2.1895 | 0.4214 | 0.09468 | 0.74061 | 22.1054 | -5.3676 | 1.3092 | 0.373 | 347.1583 | 25.31 | 73.12
2021-01-04 19:45 | 1.4471 | 0.45714 | 0.082066 | 0.78279 | 25.161 | 19.0551 | 1.302 | 0.21944 | 345.5546 | 25.3 | 73.53
2021-01-04 19:50 | 1.0502 | 0.50664 | 0.14311 | 0.9197 | 21.0048 | 14.8263 | 1.3022 | 0.11705 | 347.0757 | 25.3 | 73.98
2021-01-04 19:55 | 0.81959 | 0.37752 | 0.13047 | 0.70915 | 18.8915 | 17.068 | 1.2947 | 0.087778 | 347.1799 | 25.25 | 73.8
2021-01-04 20:00 | 1.434 | 0.40214 | 0.09888 | 0.7174 | 24.746 | 8.9725 | 1.2944 | 0.15358 | 347.3633 | 25.16 | 73.51
2021-01-04 20:05 | 1.3188 | 0.31021 | 0.082055 | 0.55545 | 27.9846 | 30.7708 | 1.2945 | 0.10239 | 347.3854 | 25.12 | 73.9
2021-01-04 20:10 | 1.2292 | 0.30608 | 0.084157 | 0.55333 | 17.0445 | 23.5591 | 1.2872 | 0.080449 | 347.4505 | 25.07 | 74.06
2021-01-04 20:15 | 1.3572 | 0.35413 | 0.082054 | 0.62697 | 25.9459 | 22.5349 | 1.2945 | 0.13896 | 346.9586 | 25.04 | 74.21
2021-01-04 20:20 | 1.2418 | 0.25389 | 0.061006 | 0.45018 | 16.5404 | -6.6059 | 1.287 | 0.095064 | 348.0794 | 25.02 | 73.88
2021-01-04 20:25 | 0.97285 | 0.30326 | 0.082032 | 0.54688 | 5.5299 |  | 1.2869 | 0.095052 | 347.1295 | 24.97 | 73.73
2021-01-04 20:30 | 1.1264 | 0.3101 | 0.088336 | 0.56367 | 9.2362 | 7.2805 | 1.2868 | 0.080423 | 348.2169 | 24.96 | 73.55
2021-01-04 20:35 | 1.2283 | 0.26609 | 0.067279 | 0.47516 | 14.228 | 9.4068 | 1.2863 | 0.065776 | 347.5281 | 24.91 | 72.56
2021-01-04 20:40 | 1.2279 | 0.314 | 0.065156 | 0.54647 | 16.0858 | 23.0952 | 1.2859 | 0.087674 | 346.9611 | 24.89 | 71.74
2021-01-04 20:45 | 1.1767 | 0.3181 | 0.073559 | 0.56115 | 27.8621 | 18.5918 | 1.2858 | 0.073058 | 347.506 | 24.89 | 71.57
2021-01-04 20:50 | 1.0359 | 0.2317 | 0.071453 | 0.42661 | 26.4688 | 4.8804 | 1.2784 | 0.065747 | 349.1177 | 24.88 | 71.41
2021-01-04 20:55 | 1.3554 | 0.19739 | 0.058832 | 0.35929 | 22.4536 | 16.899 | 1.2782 | 0.09495 | 348.2523 | 24.78 | 71.22
2021-01-04 21:00 | 1.2014 | 0.2151 | 0.073504 | 0.40322 | 14.3349 | 14.1304 | 1.2849 | 0.087604 | 349.0496 | 24.69 | 70.12
2021-01-04 21:05 | 1.0857 | 0.24237 | 0.071364 | 0.44288 | 15.3895 | 31.4227 | 1.2841 | 0.072962 | 346.6371 | 24.67 | 68.43
2021-01-04 21:10 | 1.2004 | 0.1985 | 0.069246 | 0.37351 | 22.0869 | 0.7049 | 1.2765 | 0.065648 | 347.7863 | 24.67 | 67.57
2021-01-04 21:15 | 1.0852 | 0.26826 | 0.079723 | 0.48883 | 26.1685 | 30.7547 | 1.2763 | 0.058343 | 348.9272 | 24.65 | 67.08
2021-01-04 21:20 | 1.0723 | 0.31474 | 0.088099 | 0.57055 | 31.2801 | 35.508 | 1.2833 | 0.058332 | 348.4285 | 24.68 | 66.39
2021-01-04 21:25 | 1.1231 | 0.24626 | 0.098565 | 0.47605 | 41.6361 | 50.6004 | 1.283 | 0.072899 | 349.5971 | 24.65 | 65.8
2021-01-04 21:30 | 0.80387 | 0.23938 | 0.092255 | 0.46127 | 44.8535 | 21.7734 | 1.2901 | 0.043731 | 348.1315 | 24.61 | 65.33
2021-01-04 21:35 | 1.3524 | 0.33098 | 0.09434 | 0.60168 | 29.1399 | 16.2796 | 1.2899 | 0.072875 | 349.7573 | 24.61 | 64.94
2021-01-04 21:40 | 1.6329 | 0.38702 | 0.10272 | 0.69386 | 30.5559 | 25.9735 | 1.2825 | 0.043721 | 347.6666 | 24.62 | 64.62
2021-01-04 21:45 | 0.82914 | 0.27075 | 0.092227 | 0.50725 | 35.5127 | 24.9814 | 1.2605 | -0.014572 | 349.292 | 24.61 | 64.38
2021-01-04 21:50 | 1.0332 | 0.53193 | 0.11738 | 0.93274 | 25.0218 | 11.1333 | 1.2314 | 0.051003 | 347.7607 | 24.57 | 64.49
2021-01-04 21:55 | 0.86743 | 0.54015 | 0.11109 | 0.93906 | 20.257 | -1.4899 | 1.2314 | 0.072864 | 350.387 | 24.57 | 64.6
2021-01-04 22:00 | 0.76534 | 0.37194 | 0.12786 | 0.69798 | 15.6845 | 3.5002 | 1.2313 | 0.058289 | 348.8657 | 24.53 | 64.62
2021-01-04 22:05 | 0.82908 | 0.29945 | 0.11527 | 0.57428 | 11.5612 | 2.4184 | 1.2313 | 0.043714 | 348.404 | 24.49 | 64.6
2021-01-04 22:10 | 0.85455 | 0.22833 | 0.10269 | 0.45269 | 6.2344 | 13.2646 | 1.2239 | 0.043712 | 348.9958 | 24.45 | 64.6
2021-01-04 22:15 | 0.63766 | 0.11757 | 0.10478 | 0.285 | 1.9997 | -11.6412 | 1.2238 | 0.029139 | 349.0855 | 24.4 | 64.51
2021-01-04 22:20 | 0.70142 | 0.091598 | 0.10268 | 0.24309 | 9.6311 | -7.2336 | 1.2238 | 0.036423 | 348.5976 | 24.37 | 64.58
2021-01-04 22:25 | 0.676 | 0.097079 | 0.1027 | 0.2515 | -1.6326 | -5.6427 | 1.224 | 0.029142 | 348.0489 | 24.35 | 65.06
2021-01-04 22:30 | 0.53571 | 0.10665 | 0.09222 | 0.2557 | -4.2449 | -6.4898 | 1.224 | 0.036428 | 348.6021 | 24.32 | 65.27
2021-01-04 22:35 | 0.56113 | 0.15995 | 0.11316 | 0.35834 | 5.5297 | -3.0301 | 1.2311 | 0.094699 | 348.1178 | 24.33 | 64.72
2021-01-04 22:40 | 1.3644 | 0.1531 | 0.11734 | 0.34993 | 2.9686 | -19.6071 | 1.231 | 0.10926 | 347.6244 | 24.33 | 64.4
2021-01-04 22:45 | 1.1096 | 0.24337 | 0.14251 | 0.51556 | -3.3263 | 5.7037 | 1.2239 | 0.10199 | 348.6133 | 24.33 | 65.02
2021-01-04 22:50 | 1.0587 | 0.60712 | 0.17397 | 1.1025 | 10.2554 | 12.7555 | 1.2313 | 0.102 | 348.532 | 24.37 | 65.18
2021-01-04 22:55 | 0.75254 | 0.26116 | 0.12995 | 0.52817 | 9.4897 | -4.6122 | 1.2386 | 0.087428 | 349.2508 | 24.37 | 64.98
2021-01-04 23:00 | 0.63777 | 0.18323 | 0.14462 | 0.42548 | -3.5919 |  | 1.2386 | 0.058287 | 348.2892 | 24.28 | 65.44
2021-01-04 23:05 | 0.57415 | 0.21747 | 0.15095 | 0.48639 | -2.021 | -13.7183 | 1.2462 | 0.051015 | 348.2542 | 24.23 | 66.5
2021-01-04 23:10 | 0.5232 | 0.19015 | 0.15936 | 0.45292 | 4.9308 | 4.1039 | 1.2464 | 0.036445 | 348.7948 | 24.17 | 67.27
2021-01-04 23:15 | 0.67629 | 0.20655 | 0.15306 | 0.46758 | 16.2107 | 20.2531 | 1.2537 | 0.043732 | 349.2224 | 24.12 | 67.38
2021-01-04 23:20 | 1.4292 | 0.145 | 0.18871 | 0.41097 | -0.27563 | -14.5979 | 1.2537 | 0.051021 | 348.3036 | 24.15 | 67.23
2021-01-04 23:25 | 1.1228 | 0.1149 | 0.16983 | 0.34594 | -2.215 | -19.3739 | 1.2536 | 0.036441 | 347.8273 | 24.13 | 67.05
2021-01-04 23:30 | 0.53584 | 0.13813 | 0.19077 | 0.40251 | 5.1236 | 0.061239 | 1.2534 | 0.043724 | 348.3811 | 24.14 | 66.66
2021-01-04 23:35 | 0.39544 | 0.11213 | 0.20751 | 0.3794 | -9.2049 | -4.9902 | 1.2533 | 0.043718 | 348.9693 | 24.13 | 66.25
2021-01-04 23:40 | 0.39548 | 0.075218 | 0.20963 | 0.32493 | -11.5736 | -11.5838 | 1.2534 | 0.094732 | 349.5214 | 24.08 | 66.77
2021-01-04 23:45 | 0.45931 | 0.095741 | 0.23691 | 0.38576 | 0.27559 | -14.2285 | 1.2608 | 0.080166 | 348.491 | 24.03 | 67.28
2021-01-04 23:50 |  | 0.1149 | 0.26838 | 0.44451 | -8.3706 |  | 1.2682 | 0.065597 | 347.5739 | 24.03 | 67.57
2021-01-04 23:55 | 0.3573 | 0.069766 | 0.28727 | 0.39211 | -12.3525 | 0.36751 | 1.2829 | 0.058312 | 349.2293 | 23.95 | 68.09
2021-01-05 | 0.28072 | 0.072497 | 0.30822 | 0.41935 | 2.2049 | 11.5146 | 1.2901 | 0.043731 | 347.7056 | 23.92 | 67.99
2021-01-05 00:05 | 0.33173 | 0.076593 | 0.31238 | 0.42979 | 9.1659 | 22.3533 | 1.2972 | 0.029151 | 348.056 | 23.95 | 67.61
2021-01-05 00:10 | 0.39553 | 0.065653 | 0.29771 | 0.39835 | 6.1652 | -7.6248 | 1.29 | 0.03644 | 348.5874 | 23.94 | 67.73
2021-01-05 00:15 | 0.34453 | 0.051981 | 0.27678 | 0.35646 | 8.1259 | -9.504 | 1.2901 | 0.036444 | 348.5846 | 23.91 | 68.21
2021-01-05 00:20 | 0.33177 | 0.042405 | 0.11742 | 0.18242 | 14.1383 | 24.2138 | 1.2974 | 0.029155 | 348.109 | 23.87 | 68.32
2021-01-05 00:25 | 0.31896 | 0.056075 | 0.075471 | 0.16143 | 13.7687 | 4.6746 | 1.2972 | 0.036437 | 348.1996 | 23.84 | 67.92
2021-01-05 00:30 | 0.29344 | 0.051972 | 0.067086 | 0.14675 | 0.061239 | -16.4734 | 1.3117 | 0.036437 | 349.2682 | 23.83 | 67.96
2021-01-05 00:35 | 0.21692 | 0.028725 | 0.062901 | 0.10693 | 2.3172 |  | 1.3192 | 0.043731 | 349.2236 | 23.83 | 68.38
2021-01-05 00:40 | 0.37005 | 0.024622 | 0.060806 | 0.098548 | 13.1379 | 5.2674 | 1.3265 | 0.036443 | 349.2476 | 23.8 | 68.61
2021-01-05 00:45 | 0.3701 | 0.02873 | 0.062911 | 0.10695 | 8.0962 | 11.0468 | 1.3194 | 0.043738 | 349.1772 | 23.82 | 68.97
2021-01-05 00:50 | 0.34462 | 0.04789 | 0.056628 | 0.13003 | 3.7474 | -0.93941 | 1.3269 | 0.051034 | 349.6217 | 23.85 | 69.3
2021-01-05 00:55 | 0.29358 | 0.038314 | 0.065021 | 0.12165 | 7.8935 | -8.5266 | 1.327 | 0.043746 | 349.0756 | 23.85 | 69.47
2021-01-05 01:00 | 0.33187 | 0.043787 | 0.056631 | 0.12585 | 1.9402 | -13.132 | 1.327 | 0.036455 | 349.6505 | 23.81 | 69.64
2021-01-05 01:05 |  |  |  |  | -6.2598 | 8.6085 |  |  | 349.1606 | 23.77 | 69.89
2021-01-05 01:10 |  |  |  |  | 3.0739 | 3.5335 |  |  | 348.6362 | 23.75 | 70.16
2021-01-05 01:15 |  |  |  |  | 3.6562 | -4.463 |  |  | 348.1411 | 23.71 | 70.46
2021-01-05 01:20 |  |  |  |  | 3.1559 | 3.7892 |  |  | 348.6364 | 23.72 | 70.62
2021-01-05 01:25 |  |  |  |  | 10.705 | 17.365 |  |  | 347.9919 | 23.78 | 70.8
2021-01-05 01:30 |  |  |  |  | 14.6484 | 12.9936 |  |  | 348.5073 | 23.78 | 70.92
2021-01-05 01:35 | 0.332 | 0.082132 | 0.062947 | 0.18884 | 7.4981 | 7.4062 | 1.3494 | 0.043763 | 349.0489 | 23.76 | 71.1
2021-01-05 01:40 | 0.39586 | 0.078028 | 0.056655 | 0.17626 | 0.91942 | -18.0512 | 1.3421 | 0.043764 | 347.452 | 23.76 | 71.22
2021-01-05 01:45 | 0.42143 | 0.25053 | 0.092333 | 0.47426 | 12.4846 | 3.6575 | 1.3349 | 0.051062 | 348.4686 | 23.77 | 71.44
2021-01-05 01:50 | 0.38307 | 0.40107 | 0.092322 | 0.7071 | 7.7125 | 16.0584 | 1.342 | 0.043762 | 348.454 | 23.82 | 70.81
2021-01-05 01:55 | 0.33195 | 0.3627 | 0.083918 | 0.64197 | 3.8813 | 1.1337 | 1.3419 | 0.043756 | 347.9606 | 23.83 | 70.33
2021-01-05 02:00 | 0.30641 | 0.23814 | 0.071329 | 0.43636 | 7.9871 |  | 1.3345 | 0.043756 | 349.0579 | 23.8 | 70.4
2021-01-05 02:05 | 0.29361 | 0.2039 | 0.050344 | 0.3629 | 5.8212 | 4.4629 | 1.3417 | 0.043751 | 349.18 | 23.73 | 70.32
2021-01-05 02:10 | 0.34466 | 0.25727 | 0.054537 | 0.44678 | 0.55146 | -0.010212 | 1.3343 | 0.043749 | 349.1938 | 23.73 | 70.19
2021-01-05 02:15 | 0.49791 | 0.23266 | 0.060838 | 0.41747 | 3.3398 | 16.3927 | 1.3418 | 0.058339 | 348.5852 | 23.76 | 70.49
2021-01-05 02:20 | 0.90653 | 0.35587 | 0.094412 | 0.63781 | 9.3769 | -8.5188 | 1.3419 | 0.072931 | 348.4826 | 23.82 | 70.54
2021-01-05 02:25 | 0.49786 | 0.1738 | 0.092296 | 0.3587 | 9.467 | -6.1785 | 1.349 | 0.058334 | 348.5852 | 23.79 | 70.03
2021-01-05 02:30 | 0.44681 | 0.21486 | 0.11118 | 0.44262 | 5.8111 | 7.0469 | 1.3563 | 0.051044 | 349.1335 | 23.76 | 70.3
2021-01-05 02:35 | 0.53622 | 0.25457 | 0.13426 | 0.52447 | 5.4847 | 9.5804 | 1.3564 | 0.05834 | 349.084 | 23.78 | 70.46
2021-01-05 02:40 | 0.49784 | 0.13821 | 0.094391 | 0.30625 | 2.3692 | 4.0338 | 1.3489 | 0.065623 | 349.6881 | 23.76 | 70.05
2021-01-05 02:45 | 0.45954 | 0.12042 | 0.090195 | 0.27478 | -3.3598 | -13.5616 | 1.3489 | 0.05104 | 348.8568 | 23.72 | 70.13
2021-01-05 02:50 | 0.43406 | 0.1218 | 0.083911 | 0.26851 | 7.2207 | 2.635 | 1.349 | 0.051045 | 347.6242 | 23.69 | 70.66
2021-01-05 02:55 | 0.37023 | 0.10538 | 0.086011 | 0.24754 | 15.4426 | -1.6852 | 1.3491 | 0.051046 | 348.6604 | 23.7 | 70.7
2021-01-05 03:00 | 0.383 | 0.1177 | 0.088107 | 0.26852 | 11.7656 | 23.8479 | 1.3564 | 0.043753 | 348.6296 | 23.73 | 70.53
2021-01-05 03:05 | 0.44689 | 0.13414 | 0.090218 | 0.29583 | 18.0901 | 6.5374 | 1.3565 | 0.058346 | 348.4872 | 23.81 | 70.65
2021-01-05 03:10 | 0.42139 | 0.069813 | 0.077636 | 0.18675 | 22.423 | -8.1315 | 1.3494 | 0.043763 | 349.5266 | 23.8 | 70.96
2021-01-05 03:15 | 0.42141 | 0.084874 | 0.086032 | 0.21613 | 13.5463 | 16.8767 | 1.3494 | 0.043765 | 348.5259 | 23.74 | 71.36
2021-01-05 03:20 | 0.33206 | 0.1328 | 0.10493 | 0.30849 | 7.1213 | 7.6935 | 1.3569 | 0.051065 | 347.4057 | 23.76 | 71.66
2021-01-05 03:25 | 0.37039 | 0.13144 | 0.090245 | 0.29172 | 15.9397 | 18.6474 | 1.357 | 0.051068 | 348.4285 | 23.77 | 71.82
2021-01-05 03:30 | 0.39599 | 0.17802 | 0.058772 | 0.33164 | 14.0716 |  | 1.3717 | 0.065667 | 348.3731 | 23.78 | 72.19
2021-01-05 03:35 | 0.4344 | 0.27941 | 0.081879 | 0.51017 | 12.6948 | 11.9895 | 1.3793 | 0.058384 | 348.2263 | 23.84 | 72.65
2021-01-05 03:40 | 0.35779 | 0.33013 | 0.098686 | 0.60472 | 11.0403 | 23.3074 | 1.3649 | 0.072989 | 348.0659 | 23.94 | 72.62
2021-01-05 03:45 | 0.52387 | 0.29586 | 0.069285 | 0.52279 | 29.7249 | 32.587 | 1.3648 | 0.065685 | 347.9037 | 23.95 | 72.4
2021-01-05 03:50 | 0.60051 | 0.3027 | 0.092377 | 0.55636 | 17.1925 | 0.22487 | 1.3647 | 0.080279 | 348.9935 | 23.93 | 72.39
2021-01-05 03:55 | 0.5749 | 0.26158 | 0.071376 | 0.47234 | 13.8692 | -1.3287 | 1.3719 | 0.065677 | 347.9936 | 23.91 | 72.17
2021-01-05 04:00 | 0.65153 | 0.28896 | 0.088166 | 0.53109 | 18.3756 | 15.0234 | 1.3719 | 0.072971 | 348.5618 | 23.89 | 72.1
2021-01-05 04:05 | 0.63875 | 0.29991 | 0.073471 | 0.53319 | 18.9682 | 20.399 | 1.3645 | 0.07297 | 348.0237 | 23.9 | 72.04
2021-01-05 04:10 | 0.75372 | 0.40947 | 0.067174 | 0.69693 | 19.4282 | 13.0202 | 1.3718 | 0.087565 | 347.9765 | 23.94 | 71.87
2021-01-05 04:15 | 0.85606 | 0.48076 | 0.10708 | 0.84401 | 30.9101 | 10.0581 | 1.394 | 0.065684 | 348.3315 | 24.04 | 71.96
2021-01-05 04:20 | 0.95833 | 0.46572 | 0.11338 | 0.82936 | 27.9066 | 13.1969 | 1.3867 | 0.080285 | 371.4569 | 24.1 | 71.89
2021-01-05 04:25 | 1.1499 | 0.63825 | 0.12177 | 1.1001 |  |  | 1.3939 | 0.094873 | 510.1736 | 24.16 | 71.31
2021-01-05 04:30 | 1.0348 | 0.61357 | 0.14695 | 1.0854 |  |  | 1.3938 | 0.12406 | 511.1324 | 24.23 | 70.86
2021-01-05 04:35 | 1.0988 | 0.62318 | 0.12806 | 1.0833 |  | 1.2367 | 1.4012 | 0.22623 | 510.0616 | 24.23 | 70.96
2021-01-05 04:40 | 2.0061 | 0.59585 | 0.10498 | 1.0183 | -13.1968 | 27.283 | 1.4159 | 0.34304 | 509.9868 | 24.24 | 71.28
2021-01-05 04:45 | 2.2491 | 0.71646 | 0.15749 | 1.2557 | 20.9678 | 25.2207 | 1.4161 | 0.33577 | 509.9007 | 24.26 | 71.52
2021-01-05 04:50 | 1.7123 | 0.77807 | 0.17848 | 1.3711 | 28.4191 | 20.4454 | 1.416 | 0.21167 | 508.2757 | 24.3 | 71.19
2021-01-05 04:55 | 0.99673 | 0.82877 | 0.22258 | 1.4929 | 46.8207 | 35.7595 | 1.416 | 0.15328 | 509.7299 | 24.37 | 70.94
2021-01-05 05:00 | 1.5715 | 0.8738 | 0.19524 | 1.5367 | 39.7387 | 49.2953 | 1.4231 | 0.15325 | 508.7572 | 24.38 | 70.28
2021-01-05 05:05 | 1.6352 | 0.98463 | 0.2519 | 1.7633 | 49.1162 | 26.5203 | 1.4302 | 0.20431 | 508.761 | 24.41 | 69.81
2021-01-05 05:10 | 1.7756 | 1.2708 | 0.27288 | 2.2208 | 57.9537 | 56.615 | 1.4301 | 0.24079 | 508.6982 | 24.46 | 69.46
2021-01-05 05:15 | 2.1846 | 1.5736 | 0.2918 | 2.7038 | 70.5714 | 78.3694 | 1.4303 | 0.24811 | 508.4939 | 24.55 | 69.4
2021-01-05 05:20 | 1.993 | 1.5764 | 0.3044 | 2.7207 | 85.0859 | 65.2683 | 1.4376 | 0.22622 | 508.3474 | 24.63 | 69.13
2021-01-05 05:25 | 2.0571 | 1.4573 | 0.30443 | 2.5383 | 87.8842 | 48.3475 | 1.4523 | 0.16786 | 507.145 | 24.69 | 69.17
2021-01-05 05:30 | 2.0698 | 1.7257 | 0.39259 | 3.0379 | 91.6023 | 85.4083 | 1.4304 | 0.18975 | 506.0031 | 24.75 | 68.84
2021-01-05 05:35 | 3.4369 | 1.9408 | 0.48497 | 3.4599 | 83.0778 | 63.3713 | 1.4158 | 0.29192 | 506.4283 | 24.81 | 68.59
2021-01-05 05:40 | 4.4975 | 2.3709 | 0.4367 | 4.0689 | 107.5616 | 99.5888 | 1.4013 | 0.36491 | 508.3267 | 24.92 | 68.26
2021-01-05 05:45 | 5.6211 | 2.2391 | 0.43454 | 3.8668 | 122.6427 | 129.4085 | 1.4084 | 0.41594 | 507.2053 | 25 | 67.53
2021-01-05 05:50 | 4.4582 | 2.176 | 0.4492 | 3.7846 | 129.6028 | 100.1912 | 1.4229 | 0.4305 | 508.1439 | 25.09 | 66.93
2021-01-05 05:55 | 4.0239 | 2.2869 | 0.4576 | 3.9631 | 126.9461 | 109.0314 | 1.4229 | 0.4378 | 509.1091 | 25.14 | 66.74
2021-01-05 06:00 | 4.3819 | 2.3788 | 0.45343 | 4.0998 | 123.8879 | 114.9556 | 1.4375 | 0.40864 | 507.4316 | 25.18 | 66.77
2021-01-05 06:05 | 3.6794 | 1.9434 | 0.36948 | 3.3484 | 120.9092 | 39.7784 | 1.4668 | 0.38677 | 506.272 | 25.23 | 66.71
2021-01-05 06:10 | 2.9257 | 1.8188 | 0.317 | 3.1049 | 118.3367 | 96.5561 | 1.4522 | 0.3065 | 507.2083 | 25.29 | 66.55
2021-01-05 06:15 | 2.3506 | 1.6982 | 0.34637 | 2.9494 | 95.4864 | 78.2553 | 1.4521 | 0.32837 | 507.7017 | 25.33 | 66.18
2021-01-05 06:20 | 1.827 | 1.7175 | 0.3296 | 2.9622 | 99.6734 | 64.8715 | 1.5106 | 0.24812 | 509.1273 | 25.39 | 66.22
2021-01-05 06:25 | 2.1204 | 1.4255 | 0.33163 | 2.5166 | 96.5376 | 76.0487 | 1.5103 | 0.1897 | 507.6614 | 25.39 | 65.58
2021-01-05 06:30 | 2.593 | 1.4008 | 0.31904 | 2.4663 | 85.1741 | 79.4822 | 1.4374 | 0.197 | 506.5768 | 25.41 | 65.5
2021-01-05 06:35 | 2.9251 | 1.4665 | 0.29385 | 2.5397 | 98.0995 | 70.2638 | 1.4155 | 0.23348 | 508.0273 | 25.48 | 65.25
2021-01-05 06:40 | 3.2197 | 1.6025 | 0.31492 | 2.7713 | 106.0871 | 97.9509 | 1.4304 | 0.29192 | 506.2013 | 25.55 | 65.74
2021-01-05 06:45 | 3.5523 | 1.7451 | 0.33595 | 3.0088 | 117.9043 | 90.3347 | 1.4379 | 0.31385 | 507.5754 | 25.64 | 65.68
2021-01-05 06:50 | 3.4503 | 1.7713 | 0.33807 | 3.0531 | 103.7327 | 72.3072 | 1.4452 | 0.37956 | 506.3728 | 25.71 | 65.6
2021-01-05 06:55 | 3.3993 | 1.9508 | 0.29609 | 3.2885 | 100.9677 | 64.2959 | 1.4745 | 0.40148 | 506.8538 | 25.72 | 65.72
2021-01-05 07:00 | 3.8725 | 2.2606 | 0.35071 | 3.8179 | 95.8428 | 88.2052 | 1.4746 | 0.37961 | 508.2886 | 25.78 | 65.71
2021-01-05 07:05 | 3.5528 | 2.0988 | 0.3486 | 3.5658 | 111.0721 | 84.5923 | 1.4965 | 0.31389 | 506.0587 | 25.87 | 65.23
2021-01-05 07:10 | 2.8241 | 1.8959 | 0.27087 | 3.177 | 108.0768 | 82.9795 | 1.5401 | 0.35036 | 505.4956 | 25.92 | 64.77
2021-01-05 07:15 | 3.0795 | 1.6095 | 0.26036 | 2.7275 | 90.8269 | 64.8822 | 1.5474 | 0.32845 | 506.0415 | 25.92 | 64.65
2021-01-05 07:20 | 3.4369 | 1.6765 | 0.33381 | 2.9036 | 99.433 | 63.1166 | 1.5034 | 0.27003 | 505.6088 | 25.9 | 64.39
2021-01-05 07:25 | 3.1943 | 2.4312 | 0.39261 | 4.1193 | 87.1299 | 67.2691 | 1.5035 | 0.28463 | 505.5216 | 25.94 | 64.35
2021-01-05 07:30 | 2.6068 | 2.1931 | 0.41785 | 3.7795 | 100.4688 | 104.5886 | 1.5182 | 0.27006 | 506.3697 | 26.03 | 64.29
2021-01-05 07:35 | 3.0411 | 1.9136 | 0.38004 | 3.3133 | 111.5562 | 78.5585 | 1.5327 | 0.29925 | 506.3044 | 26.08 | 63.99
2021-01-05 07:40 | 3.3604 | 2.0409 | 0.34433 | 3.4726 | 106.071 | 72.9117 | 1.4743 | 0.32842 | 506.316 | 26.09 | 63.79
2021-01-05 07:45 | 3.4119 | 1.8713 | 0.32337 | 3.1917 | 97.9056 | 73.1046 | 1.4671 | 0.33576 | 507.3037 | 26.09 | 64.14
2021-01-05 07:50 | 3.3469 | 1.5255 | 0.28758 | 2.626 | 103.0752 | 92.6103 | 1.4813 | 0.32836 | 507.5043 | 26.07 | 63.27
2021-01-05 07:55 | 2.9504 | 1.4965 | 0.36518 | 2.6591 | 95.7417 | 69.2773 | 1.4591 | 0.18968 | 506.5407 | 26.07 | 62.78
2021-01-05 08:00 | 2.504 | 1.3051 | 0.31069 | 2.3134 | 95.7433 | 43.8858 | 1.4157 | 0.19703 | 507.4395 | 26.09 | 63.37
2021-01-05 08:05 | 2.7978 | 1.2422 | 0.2876 | 2.1916 | 97.5222 | 60.7598 | 1.4449 | 0.23351 | 507.4195 | 26.1 | 63.35
2021-01-05 08:10 | 2.8105 | 1.5749 | 0.31908 | 2.7332 | 91.583 | 74.4642 | 1.4886 | 0.29919 | 505.8688 | 26.09 | 63.35
2021-01-05 08:15 | 3.1162 | 1.4362 | 0.27282 | 2.4763 | 84.567 | 62.8148 | 1.4517 | 0.24074 | 507.6804 | 26.04 | 62.67
2021-01-05 08:20 | 3.0144 | 1.1009 | 0.29803 | 1.9855 | 73.9187 | 60.3898 | 1.4227 | 0.22617 | 507.0316 | 26.08 | 62.84
2021-01-05 08:25 | 2.6308 | 1.1486 | 0.31897 | 2.0796 | 82.8467 | 39.1297 | 1.3933 | 0.18237 | 507.6358 | 26.08 | 62.39
2021-01-05 08:30 | 3.5115 | 1.2676 | 0.3483 | 2.2892 | 79.4648 | 72.406 | 1.3931 | 0.24799 | 505.6027 | 26.08 | 62.01
2021-01-05 08:35 | 3.1801 | 1.3335 | 0.32948 | 2.3735 | 77.3845 | 48.8277 | 1.4006 | 0.23344 | 504.9194 | 26.12 | 62.38
2021-01-05 08:40 | 3.538 | 1.4582 | 0.30013 | 2.5354 | 85.0968 | 58.08 | 1.4154 | 0.28453 | 506.9003 | 26.16 | 62.52
2021-01-05 08:45 | 3.9469 | 1.5377 | 0.33162 | 2.6887 | 80.5217 | 45.7073 | 1.4373 | 0.30643 | 505.2249 | 26.21 | 62.43
2021-01-05 08:50 | 2.8865 | 1.4157 | 0.3274 | 2.4975 | 74.1609 | 76.1227 | 1.4518 | 0.27723 | 504.6833 | 26.24 | 62.13
2021-01-05 08:55 | 2.5535 | 1.1428 | 0.31679 | 2.0686 | 76.0941 | 33.0933 | 1.4586 | 0.23337 | 505.906 | 26.25 | 61.02
2021-01-05 09:00 | 3.1149 | 1.207 | 0.31885 | 2.169 | 78.382 | 65.4324 | 1.4729 | 0.24063 | 506.937 | 26.3 | 60.47
2021-01-05 09:05 | 2.7072 | 1.3607 | 0.33783 | 2.4214 | 82.2364 | 46.5836 | 1.4588 | 0.21153 | 506.142 | 26.37 | 61.07
2021-01-05 09:10 | 1.9283 | 1.4347 | 0.30637 | 2.5055 | 82.0779 | 67.0804 | 1.437 | 0.16048 | 505.553 | 26.39 | 61.17
2021-01-05 09:15 | 2.1325 | 1.247 | 0.31684 | 2.2284 | 80.7431 | 52.0989 | 1.4296 | 0.14588 | 505.578 | 26.4 | 60.9
2021-01-05 09:20 | 2.2852 | 1.1838 | 0.31048 | 2.1251 | 72.494 | 34.8069 | 1.4293 | 0.17501 | 505.6692 | 26.41 | 60.26
2021-01-05 09:25 | 2.3104 | 1.159 | 0.30623 | 2.0828 | 59.5538 | 23.6806 | 1.4436 | 0.18957 | 506.2798 | 26.41 | 59.78
2021-01-05 09:30 | 2.3231 | 1.0454 | 0.26847 | 1.8709 | 62.0953 | 39.1606 | 1.4436 | 0.20415 | 507.3559 | 26.4 | 59.76
2021-01-05 09:35 | 2.3491 | 1.0702 | 0.30628 | 1.9468 | 55.0701 | 35.1133 | 1.4512 | 0.18231 | 506.1598 | 26.43 | 60.19
2021-01-05 09:40 | 1.8259 | 0.88695 | 0.27694 | 1.6365 | 52.4415 | 35.5977 | 1.4368 | 0.13857 | 506.0808 | 26.44 | 60.5
2021-01-05 09:45 | 1.8505 | 0.96998 | 0.31456 | 1.8014 | 52.876 | 36.908 | 1.4288 | 0.15308 | 506.7785 | 26.48 | 59.02
2021-01-05 09:50 | 2.4888 | 1.2437 | 0.35653 | 2.2629 | 46.1005 | 22.9226 | 1.4216 | 0.18955 | 505.6206 | 26.52 | 59.11
2021-01-05 09:55 | 2.8724 | 1.3384 | 0.40696 | 2.4585 | 58.1009 | 30.996 | 1.4146 | 0.21876 | 505.8944 | 26.6 | 59.47
2021-01-05 10:00 | 2.7699 | 1.5203 | 0.39433 | 2.7246 | 58.6458 | 56.8383 | 1.4145 | 0.22603 | 504.2611 | 26.67 | 58.91
2021-01-05 10:05 | 3.0494 | 1.51 | 0.40254 | 2.7171 | 57.7519 | 33.7753 | 1.4211 | 0.20406 | 507.0253 | 26.72 | 57.49
2021-01-05 10:10 | 2.9471 | 1.659 | 0.38783 | 2.9307 | 73.3324 | 52.9708 | 1.3773 | 0.18947 | 506.4727 | 26.76 | 57.14
2021-01-05 10:15 | 3.075 | 1.5566 | 0.38787 | 2.7738 | 66.073 | 39.7887 | 1.3556 | 0.26966 | 504.2177 | 26.82 | 57.25
2021-01-05 10:20 | 2.9732 | 1.1231 | 0.35855 | 2.08 | 66.4765 | 31.9928 | 1.3557 | 0.27697 | 503.5853 | 26.86 | 57.34
2021-01-05 10:25 | 3.1395 | 1.1355 | 0.35441 | 2.095 | 58.278 | 45.0256 | 1.3632 | 0.22599 | 505.012 | 26.9 | 57.63
2021-01-05 10:30 | 2.8326 | 1.1093 | 0.32498 | 2.0254 | 68.3509 | 16.2405 | 1.3702 | 0.21136 | 506.6574 | 26.92 | 56.98
2021-01-05 10:35 | 2.5007 | 1.0463 | 0.29771 | 1.9016 | 69.5815 | 63.1 | 1.3774 | 0.19677 | 505.5746 | 26.96 | 56.67
2021-01-05 10:40 | 2.7176 | 1.0983 | 0.32286 | 2.0063 | 76.8784 | 51.9123 | 1.3847 | 0.21134 | 505.0077 | 26.99 | 56.53
2021-01-05 10:45 | 3.3178 | 1.1682 | 0.31872 | 2.1094 | 84.8032 | 55.8923 | 1.3776 | 0.24054 | 506.4258 | 27.03 | 56.86
2021-01-05 10:50 | 3.3691 | 1.2039 | 0.30826 | 2.1558 | 84.6166 | 46.4738 | 1.3559 | 0.21869 | 505.3008 | 27.05 | 57.03
2021-01-05 10:55 | 3.1524 | 1.256 | 0.38169 | 2.3048 | 73.0336 | 44.4144 | 1.407 | 0.30618 | 503.173 | 27.05 | 57.21
2021-01-05 11:00 | 2.7818 | 1.0437 | 0.40049 | 1.9983 | 63.2417 | 27.1138 | 1.3995 | 0.2624 | 507.4589 | 27.05 | 56.7
2021-01-05 11:05 | 2.9733 | 1.0164 | 0.38373 | 1.9417 | 60.354 | 13.7103 | 1.363 | 0.24054 | 505.4056 | 27.02 | 56.86
2021-01-05 11:10 | 3.496 | 0.97524 | 0.35642 | 1.8492 | 63.5208 | 18.404 | 1.3337 | 0.20407 | 504.9298 | 27.03 | 56.48
2021-01-05 11:15 | 2.7555 | 1.0325 | 0.35636 | 1.939 | 60.4179 | 24.555 | 1.3262 | 0.19675 | 504.4572 | 27.05 | 55.96
2021-01-05 11:20 | 2.4747 | 1.0653 | 0.39617 | 2.027 | 65.3332 | 56.4854 | 1.3261 | 0.18945 | 504.4195 | 27.09 | 55.67
2021-01-05 11:25 | 2.5 | 1.2771 | 0.42129 | 2.3789 | 74.7053 | 38.817 | 1.326 | 0.204 | 503.8392 | 27.15 | 55.24
2021-01-05 11:30 | 3.0109 | 1.6097 | 0.4067 | 2.8762 | 68.9131 | 28.7002 | 1.319 | 0.24048 | 503.0794 | 27.23 | 55.53
2021-01-05 11:35 | 2.5411 | 1.6303 | 0.38607 | 2.8851 | 80.1083 | 28.6743 | 1.3129 | 0.24069 | 504.5431 | 27.34 | 57.52
2021-01-05 11:40 | 2.4157 | 1.3263 | 0.33184 | 2.3649 | 87.5078 | 46.075 | 1.3142 | 0.22633 | 504.4553 | 27.41 | 59.88
2021-01-05 11:45 | 2.3269 | 1.2842 | 0.34874 | 2.3172 | 75.165 | 46.353 | 1.3145 | 0.21908 | 502.6926 | 27.45 | 60.43
2021-01-05 11:50 | 2.6083 | 1.2898 | 0.32985 | 2.3068 | 66.8744 | 33.3144 | 1.3292 | 0.24101 | 503.6536 | 27.48 | 60.49
2021-01-05 11:55 | 3.0812 | 1.0073 | 0.30462 | 1.8487 | 71.1658 | 55.2818 | 1.3291 | 0.21178 | 504.241 | 27.46 | 60.39
2021-01-05 12:00 | 3.273 | 0.82507 | 0.30462 | 1.5693 | 60.2019 | 35.665 | 1.3218 | 0.2702 | 502.6729 | 27.46 | 60.41
2021-01-05 12:05 | 3.0681 | 1.1059 | 0.38651 | 2.0796 | 60.1958 | 24.4731 | 1.3144 | 0.29208 | 502.7242 | 27.46 | 60.14
2021-01-05 12:10 | 2.8245 | 1.2043 | 0.38642 | 2.2324 | 65.5905 | 35.7041 | 1.3068 | 0.27011 | 502.8084 | 27.48 | 59.45
2021-01-05 12:15 | 2.824 | 1.1027 | 0.36955 | 2.0598 | 64.5972 | 36.7097 | 1.3138 | 0.24087 | 503.9095 | 27.5 | 58.9
2021-01-05 12:20 | 3.4628 | 1.1575 | 0.38634 | 2.1606 | 77.2399 | 59.0544 | 1.3211 | 0.29195 | 503.3054 | 27.56 | 58.6
2021-01-05 12:25 | 2.8233 | 1.3846 | 0.37786 | 2.5002 | 66.9625 | 35.1267 | 1.3208 | 0.27 | 502.8401 | 27.59 | 57.94
2021-01-05 12:30 | 2.4914 | 1.1669 | 0.31701 | 2.1036 | 75.8814 | 43.8485 | 1.3209 | 0.22623 | 503.2322 | 27.64 | 58.01
2021-01-05 12:35 | 1.8402 | 1.5233 | 0.36327 | 2.6962 | 72.4717 | 18.0847 | 1.3212 | 0.18248 | 503.57 | 27.69 | 58.36
2021-01-05 12:40 | 1.7382 | 1.1303 | 0.32342 | 2.056 | 76.2037 | 49.1802 | 1.3141 | 0.13871 | 502.9081 | 27.74 | 58.5
2021-01-05 12:45 | 2.3259 | 0.95626 | 0.3234 | 1.7871 | 83.6315 | 61.4354 | 1.314 | 0.1387 | 502.9409 | 27.74 | 58.33
2021-01-05 12:50 | 2.2748 | 0.89733 | 0.32549 | 1.701 | 85.8176 | 42.8986 | 1.2993 | 0.1095 | 502.4143 | 27.75 | 58.24
2021-01-05 12:55 | 2.9269 | 0.96734 | 0.35704 | 1.8377 | 88.9995 | 57.2914 | 1.2995 | 0.16062 | 502.3605 | 27.74 | 58.64
2021-01-05 13:00 | 2.5309 | 0.82626 | 0.31506 | 1.5837 | 88.7393 | 51.3539 | 1.2996 | 0.16063 | 503.4059 | 27.71 | 58.97
2021-01-05 13:05 | 2.608 | 0.74966 | 0.2983 | 1.4474 | 81.8814 | 42.6692 | 1.2998 | 0.19717 | 502.8667 | 27.67 | 59.55
2021-01-05 13:10 | 2.48 | 0.77427 | 0.33399 | 1.5187 | 64.4901 | 23.0921 | 1.2997 | 0.20445 | 502.9522 | 27.64 | 59.47
2021-01-05 13:15 | 2.3649 | 1.1278 | 0.30878 | 2.0355 | 45.3454 | 15.4424 | 1.2997 | 0.23366 | 502.9875 | 27.62 | 59.53
2021-01-05 13:20 | 2.5698 | 1.2719 | 0.30253 | 2.2521 | 56.5825 | 30.5312 | 1.3072 | 0.22639 | 503.3866 | 27.65 | 59.8
2021-01-05 13:25 | 2.4423 | 1.0623 | 0.35089 | 1.9793 | 68.6808 | 45.9509 | 1.3074 | 0.21181 | 504.8527 | 27.67 | 60.06
2021-01-05 13:30 | 2.3017 | 0.87044 | 0.30467 | 1.6389 | 70.687 | 61.4599 | 1.3074 | 0.1826 | 503.7852 | 27.68 | 60.07
2021-01-05 13:35 | 2.5321 | 0.62513 | 0.24796 | 1.2062 | 71.2764 | 25.4946 | 1.3075 | 0.17531 | 502.6991 | 27.68 | 60.3
2021-01-05 13:40 | 3.0948 | 0.75812 | 0.2984 | 1.4605 | 67.1136 | 33.035 | 1.3149 | 0.19723 | 501.1776 | 27.66 | 60.35
2021-01-05 13:45 | 3.0176 | 1.0308 | 0.36139 | 1.9435 | 72.9551 | 40.2215 | 1.3147 | 0.16068 | 501.1995 | 27.69 | 59.87
2021-01-05 13:50 | 2.2377 | 1.098 | 0.3614 | 2.0444 | 70.1952 | 60.8147 | 1.3074 | 0.14608 | 500.0943 | 27.72 | 59.84
2021-01-05 13:55 | 2.251 | 1.3656 | 0.34467 | 2.44 | 69.3717 | 33.4274 | 1.3077 | 0.17533 | 502.5017 | 27.77 | 60.24
2021-01-05 14:00 | 2.9929 | 1.3218 | 0.3699 | 2.3981 | 66.2233 | 55.6738 | 1.3004 | 0.20456 | 501.389 | 27.8 | 60.25
2021-01-05 14:05 | 3.7356 | 1.259 | 0.34686 | 2.2767 | 78.3564 | 51.8897 | 1.308 | 0.31422 | 502.232 | 27.84 | 60.77
2021-01-05 14:10 | 3.8889 | 1.1615 | 0.34474 | 2.1273 | 82.5775 | 49.4196 | 1.3153 | 0.3142 | 502.8185 | 27.83 | 60.56
2021-01-05 14:15 | 4.4133 | 1.156 | 0.36365 | 2.1356 | 66.4578 | 39.6147 | 1.3445 | 0.24843 | 501.2349 | 27.85 | 60.44
2021-01-05 14:20 | 4.2597 | 1.1793 | 0.33631 | 2.144 | 68.9936 | 44.9656 | 1.3371 | 0.24843 | 502.7968 | 27.85 | 60.42
2021-01-05 14:25 | 3.3771 | 1.0984 | 0.29638 | 1.9801 | 62.0765 | 35.7661 | 1.3152 | 0.27035 | 500.2219 | 27.83 | 60.52
2021-01-05 14:30 | 2.7378 | 0.9271 | 0.32374 | 1.7448 | 66.7403 | 40.6726 | 1.3007 | 0.26307 | 501.1734 | 27.85 | 60.74
2021-01-05 14:35 | 2.7766 | 1.1179 | 0.35744 | 2.071 | 66.2093 | 62.8619 | 1.301 | 0.2485 | 501.5573 | 27.88 | 61.08
2021-01-05 14:40 | 2.2268 | 1.1853 | 0.3596 | 2.1765 | 74.3692 | 50.4326 | 1.3377 | 0.25585 | 501.4282 | 27.91 | 61.38
2021-01-05 14:45 | 2.3678 | 1.239 | 0.39119 | 2.2903 | 89.1841 | 48.1451 | 1.3817 | 0.24126 | 500.8814 | 27.89 | 61.76
2021-01-05 14:50 | 3.2644 | 1.2845 | 0.40388 | 2.3707 | 71.9234 | 37.1958 | 1.3528 | 0.19743 | 499.7838 | 27.87 | 62.3
2021-01-05 14:55 | 4.9667 | 1.2131 | 0.37441 | 2.2317 | 74.3164 | 66.6871 | 1.3161 | 0.27785 | 500.9308 | 27.82 | 62.36
2021-01-05 15:00 | 4.9536 | 1.331 | 0.3849 | 2.423 | 63.6001 | 50.1756 | 1.3233 | 0.30707 | 503.0769 | 27.81 | 62.15
2021-01-05 15:05 | 4.1464 | 1.2498 | 0.37642 | 2.2922 | 77.6458 | 67.807 | 1.3377 | 0.27047 | 501.6565 | 27.78 | 61.8
2021-01-05 15:10 | 3.0714 | 1.1908 | 0.35328 | 2.1807 | 74.6856 | 45.2209 | 1.3523 | 0.21199 | 501.7158 | 27.75 | 61.86
2021-01-05 15:15 | 3.1098 | 1.1579 | 0.33016 | 2.1029 | 74.4929 | 65.7086 | 1.4328 | 0.20468 | 502.76 | 27.74 | 61.96
2021-01-05 15:20 | 3.3281 | 1.2816 | 0.34075 | 2.3053 | 80.9498 | 82.3118 | 1.455 | 0.17548 | 501.5642 | 27.77 | 62.4
2021-01-05 15:25 | 4.6717 | 1.3872 | 0.31127 | 2.4376 | 84.803 | 51.9344 | 1.3818 | 0.55563 | 501.5748 | 27.79 | 62.1
2021-01-05 15:30 | 4.5297 | 1.5761 | 0.36795 | 2.7838 | 95.2612 | 78.7189 | 1.3156 | 0.67973 | 500.5775 | 27.85 | 61.15
2021-01-05 15:35 | 4.0572 | 1.6286 | 0.32177 | 2.8161 | 92.2129 | 53.4888 | 1.2794 | 0.5483 | 502.4329 | 27.91 | 61.57
2021-01-05 15:40 | 3.2386 | 1.4944 | 0.33655 | 2.6293 | 77.0811 | 64.2189 | 1.243 | 0.3071 | 500.2451 | 27.93 | 61.89
2021-01-05 15:45 | 3.0981 | 1.4396 | 0.33237 | 2.5412 | 75.2855 | 47.7358 | 1.2651 | 0.32175 | 501.6752 | 27.98 | 61.94
2021-01-05 15:50 | 3.2897 | 1.4065 | 0.34706 | 2.5009 | 93.9453 | 41.8422 | 1.2868 | 0.32171 | 501.1453 | 28.02 | 61.51
2021-01-05 15:55 | 3.3384 | 1.4836 | 0.36151 | 2.6357 | 102.8596 | 60.5165 | 1.3005 | 0.31417 | 500.9997 | 28.02 | 59.6
2021-01-05 16:00 | 3.1339 | 1.629 | 0.33 | 2.8271 | 99.7945 | 64.2033 | 1.3006 | 0.34341 | 500.3396 | 28.09 | 59.48
2021-01-05 16:05 | 3.6976 | 1.447 | 0.32377 | 2.5397 | 116.1013 | 76.5923 | 1.3082 | 0.24848 | 499.6596 | 28.12 | 59.94
2021-01-05 16:10 | 3.6585 | 1.2506 | 0.36154 | 2.2785 | 95.1505 | 27.1902 | 1.3225 | 0.24843 | 502.4206 | 28.09 | 59.47
2021-01-05 16:15 | 4.1052 | 1.3339 | 0.33833 | 2.3809 | 93.6857 | 58.1737 | 1.3222 | 0.26298 | 501.9559 | 28.12 | 58.83
2021-01-05 16:20 | 3.4416 | 1.329 | 0.34899 | 2.3861 | 87.7677 | 52.5378 | 1.2716 | 0.31424 | 500.6088 | 28.18 | 59.68
2021-01-05 16:25 | 4.1561 | 1.6423 | 0.36773 | 2.8872 | 107.1931 | 73.8218 | 1.3221 | 0.43096 | 499.8144 | 28.18 | 58.44
2021-01-05 16:30 | 3.3772 | 1.4372 | 0.35524 | 2.5582 | 133.2855 | 88.4511 | 1.3372 | 0.35073 | 501.1331 | 28.22 | 59.18
2021-01-05 16:35 | 3.8884 | 1.4164 | 0.42246 | 2.5936 | 132.0426 | 72.734 | 1.3224 | 0.33608 | 501.7254 | 28.21 | 58.93
2021-01-05 16:40 | 3.607 | 1.0394 | 0.33208 | 1.9252 | 120.1831 | 75.456 | 1.2932 | 0.29955 | 501.7079 | 28.22 | 58.9
2021-01-05 16:45 | 3.3012 | 1.0013 | 0.29645 | 1.8292 | 100.4784 | 45.3872 | 1.2936 | 0.30696 | 502.5758 | 28.22 | 59.76
2021-01-05 16:50 | 2.8273 | 1.008 | 0.30692 | 1.852 | 67.978 | 26.8453 | 1.33 | 0.23384 | 502.7217 | 28.18 | 59.5
2021-01-05 16:55 | 3.4031 | 1.0876 | 0.33005 | 1.9992 | 66.3325 | 35.6073 | 1.3373 | 0.21923 | 501.7159 | 28.15 | 59.69
2021-01-05 17:00 | 2.9683 | 0.95186 | 0.3553 | 1.8122 | 68.9155 | 47.3698 | 1.3374 | 0.16809 | 502.2409 | 28.13 | 59.9
2021-01-05 17:05 | 2.7249 | 0.93529 | 0.36367 | 1.7973 | 67.6688 | 49.9533 | 1.3299 | 0.15345 | 502.3686 | 28.09 | 59.73
2021-01-05 17:10 | 2.3533 | 0.82948 | 0.29422 | 1.5636 | 58.7909 | 36.9259 | 1.3223 | 0.18994 | 501.5742 | 28.02 | 59.32
2021-01-05 17:15 | 2.3524 | 0.85659 | 0.27731 | 1.5903 | 53.0215 | 26.6744 | 1.3291 | 0.18987 | 502.9967 | 27.9 | 58.8
2021-01-05 17:20 | 1.918 | 0.83752 | 0.29416 | 1.5779 | 44.4365 | 30.9541 | 1.3001 | 0.16068 | 503.0243 | 27.84 | 59.38
2021-01-05 17:25 | 2.2512 | 0.66503 | 0.26273 | 1.2821 | 31.333 | 26.9738 | 1.2932 | 0.20457 | 501.9648 | 27.75 | 60.57
2021-01-05 17:30 | 3.1472 | 0.60755 | 0.24386 | 1.1751 | 33.3242 | 30.786 | 1.3008 | 0.1973 | 503.0134 | 27.69 | 61.26
2021-01-05 17:35 | 2.5216 | 0.62708 | 0.22085 | 1.1821 | 29.2047 | 36.1679 | 1.3014 | 0.18279 | 503.3375 | 27.65 | 62.77
2021-01-05 17:40 | 2.5857 | 0.65454 | 0.21875 | 1.222 | 40.6539 | 14.0701 | 1.3015 | 0.22666 | 502.8903 | 27.6 | 63.01
2021-01-05 17:45 | 2.2925 | 1.0352 | 0.27568 | 1.8625 | 42.3659 | 42.5606 | 1.3021 | 0.18289 | 500.5627 | 27.59 | 64.43
2021-01-05 17:50 | 3.063 | 0.80233 | 0.22533 | 1.4552 | 53.8982 | 56.1333 | 1.3104 | 0.18301 | 501.8306 | 27.56 | 66.33
2021-01-05 17:55 | 2.7564 | 0.59646 | 0.19802 | 1.1102 | 49.1478 | 33.743 | 1.3035 | 0.13914 | 503.2811 | 27.52 | 67.4
2021-01-05 18:00 | 2.6416 | 0.65845 | 0.21071 | 1.22 | 35.3406 | 14.998 | 1.2965 | 0.13917 | 502.1797 | 27.49 | 68.11
2021-01-05 18:05 | 2.2696 | 0.76425 | 0.18331 | 1.3548 | 242.6192 | 528.1265 | 1.289 | 0.14648 | 358.2407 | 27.45 | 68.17
2021-01-05 18:10 | 2.6673 | 0.86332 | 0.22336 | 1.5467 | 250.895 | 165.8681 | 1.2892 | 0.19045 | 355.577 | 27.47 | 68.39
2021-01-05 18:15 | 2.0645 | 0.64332 | 0.18753 | 1.1736 | 136.1286 | 47.3219 | 1.2891 | 0.14649 | 355.588 | 27.48 | 68.18
2021-01-05 18:20 | 2.3464 | 0.7065 | 0.17487 | 1.2578 | 47.2359 | 68.0689 | 1.2963 | 0.17577 | 355.6531 | 27.45 | 68.08
2021-01-05 18:25 | 2.4362 | 0.68588 | 0.18962 | 1.241 | 40.1991 | 48.0461 | 1.2963 | 0.16845 | 355.6663 | 27.44 | 68.11
2021-01-05 18:30 | 2.6924 | 0.6226 | 0.20646 | 1.1608 | 41.7855 | 25.2518 | 1.3109 | 0.18308 | 357.2559 | 27.44 | 67.89
2021-01-05 18:35 | 2.3589 | 0.62257 | 0.21277 | 1.1671 | 42.1528 | 56.4089 | 1.3108 | 0.18307 | 356.232 | 27.44 | 67.77
2021-01-05 18:40 | 2.5762 | 0.61967 | 0.25063 | 1.1984 | 42.1836 | 49.5047 | 1.3032 | 0.19767 | 356.3784 | 27.39 | 67.32
2021-01-05 18:45 | 2.0759 | 0.62504 | 0.23373 | 1.1897 | 36.6494 | 48.8488 | 1.3029 | 0.16103 | 355.9774 | 27.35 | 66.94
2021-01-05 18:50 | 1.9594 | 0.66308 | 0.25673 | 1.2731 | 33.8494 | 56.4601 | 1.3021 | 0.19019 | 357.668 | 27.3 | 65.48
2021-01-05 18:55 | 1.5351 | 0.51152 | 0.1997 | 0.98587 | 43.2388 | 60.2069 | 1.2934 | 0.15345 | 357.1369 | 27.19 | 63.03
2021-01-05 19:00 | 1.8804 | 0.58964 | 0.20388 | 1.1077 | 37.4638 | 45.5787 | 1.2933 | 0.15344 | 357.2491 | 27.12 | 63.07
2021-01-05 19:05 | 1.6118 | 0.5554 | 0.22702 | 1.0784 | 38.06 | 75.3422 | 1.3007 | 0.14614 | 357.7822 | 27.09 | 63.37
2021-01-05 19:10 | 1.3943 | 0.41688 | 0.20389 | 0.845 | 40.5971 | 46.0619 | 1.3006 | 0.11691 | 358.3485 | 27.06 | 63.42
2021-01-05 19:15 | 1.0874 | 0.35656 | 0.19129 | 0.73784 | 31.0712 | 17.2959 | 1.2934 | 0.11692 | 357.3676 | 26.99 | 63.83
2021-01-05 19:20 | 0.94679 | 0.25923 | 0.18291 | 0.58026 | 9.3758 | 28.0454 | 1.2862 | 0.095007 | 357.3694 | 26.95 | 64.33
2021-01-05 19:25 | 0.88295 | 0.32648 | 0.1556 | 0.65604 | 5.2926 | 28.664 | 1.2864 | 0.095021 | 357.374 | 26.9 | 64.94
2021-01-05 19:30 | 1.0623 | 0.32517 | 0.14722 | 0.64354 | 5.5188 | 9.0001 | 1.294 | 0.080417 | 358.3666 | 26.89 | 65.47
2021-01-05 19:35 | 1.1134 | 0.34847 | 0.16193 | 0.69607 | 6.2658 | 10.8833 | 1.3012 | 0.080411 | 357.3817 | 26.86 | 65.4
2021-01-05 19:40 | 1.0366 | 0.3855 | 0.15561 | 0.74651 | 3.5423 | 28.9527 | 1.3012 | 0.080408 | 358.4293 | 26.87 | 65.25
2021-01-05 19:45 | 1.2029 | 0.36215 | 0.17242 | 0.72753 | 0 | 20.986 | 1.3084 | 0.073093 | 357.4364 | 26.85 | 65.11
2021-01-05 19:50 | 1.1388 | 0.32784 | 0.164 | 0.66652 | 8.22 | 27.0348 | 1.3083 | 0.073089 | 359.0563 | 26.82 | 65.1
2021-01-05 19:55 | 1.0234 | 0.37712 | 0.15135 | 0.72942 | 0.17398 | 24.4388 | 1.308 | 0.073071 | 359.3745 | 26.63 | 65.13
2021-01-05 20:00 | 1.3171 | 0.42906 | 0.14709 | 0.80477 | 13.9025 | 28.0709 | 1.3001 | 0.10956 | 360.4257 | 26.31 | 65.24
2021-01-05 20:05 | 1.4959 | 0.46464 | 0.14917 | 0.86138 | 26.7372 | 37.2009 | 1.3073 | 0.11685 | 360.695 | 26.13 | 65.52
2021-01-05 20:10 | 1.3926 | 0.46156 | 0.14696 | 0.85236 | 24.5715 | 23.9276 | 1.3136 | 0.10217 | 360.5556 | 25.59 | 65.52
2021-01-05 20:15 | 1.5833 | 0.55437 | 0.14477 | 0.99454 | 14.8527 | 18.3157 | 1.3201 | 0.1167 | 362.9127 | 24.69 | 67.29
2021-01-05 20:20 | 1.5836 | 0.69409 | 0.15948 | 1.2213 | -2.4111 | 4.9141 | 1.3203 | 0.10942 | 363.326 | 24.31 | 69.28
2021-01-05 20:25 | 1.9808 | 0.67126 | 0.17639 | 1.2053 | 17.7578 | 31.7432 | 1.3358 | 0.13869 | 362.4849 | 24.37 | 71.14
2021-01-05 20:30 | 1.8163 | 0.5759 | 0.14713 | 1.032 | 30.8109 | 32.0081 | 1.337 | 0.13882 | 361.8681 | 24.6 | 73.09
2021-01-05 20:35 | 2.0477 | 0.47333 | 0.12828 | 0.85381 | 13.3612 | 14.5387 | 1.3378 | 0.13159 | 363.0988 | 24.72 | 74.31
2021-01-05 20:40 | 2.3818 | 0.40908 | 0.13467 | 0.76172 | 17.4155 | -9.4863 | 1.3312 | 0.073145 | 360.5924 | 24.88 | 75.38
2021-01-05 20:45 | 2.2296 | 0.31731 | 0.13054 | 0.61693 | 10.251 | 17.4165 | 1.3028 | 0.073192 | 358.3988 | 25.2 | 75.91
2021-01-05 20:50 | 1.9223 | 0.31735 | 0.11582 | 0.60227 | 10.0678 | 22.309 | 1.2957 | 0.13176 | 360.1993 | 25.41 | 75.34
2021-01-05 20:55 | 1.3587 | 0.21299 | 0.11795 | 0.44443 | 22.3346 | 26.0673 | 1.2886 | 0.12447 | 359.8399 | 25.64 | 74.99
2021-01-05 21:00 | 1.2052 | 0.23228 | 0.11798 | 0.47403 | 14.883 | 16.719 | 1.2889 | 0.11718 | 359.7565 | 25.94 | 74.42
2021-01-05 21:05 | 1.0257 | 0.18693 | 0.11377 | 0.40241 | 11.283 | 19.7351 | 1.2817 | 0.087885 | 359.5665 | 26.09 | 73.84
2021-01-05 21:10 | 1.077 | 0.22542 | 0.11798 | 0.46351 | 18.1042 | 27.7256 | 1.289 | 0.087885 | 360.0051 | 26.16 | 73.54
2021-01-05 21:15 | 0.9873 | 0.40549 | 0.1833 | 0.80696 | 12.4631 | 19.8487 | 1.289 | 0.080564 | 359.3846 | 26.23 | 73.34
2021-01-05 21:20 | 0.78215 | 0.28178 | 0.14327 | 0.57519 | 20.1769 | 16.1251 | 1.2817 | 0.07324 | 358.874 | 26.22 | 73.38
2021-01-05 21:25 | 1.0001 | 0.35599 | 0.14748 | 0.69316 | 22.5252 | 24.9972 | 1.289 | 0.073238 | 358.4104 | 26.18 | 73.46
2021-01-05 21:30 | 0.94852 | 0.31741 | 0.14112 | 0.62766 | 20.6624 | 30.7116 | 1.2959 | 0.1025 | 359.7202 | 26.05 | 73.17
2021-01-05 21:35 | 0.9739 | 0.31183 | 0.11792 | 0.59591 | 28.2738 | 6.766 | 1.3102 | 0.10247 | 359.5806 | 25.81 | 73.44
2021-01-05 21:40 | 0.74309 | 0.14833 | 0.098946 | 0.32631 | 37.3389 | 6.7852 | 1.3246 | 0.065863 | 360.4073 | 25.62 | 73.67
2021-01-05 21:45 | 0.75537 | 0.18254 | 0.092565 | 0.37237 | 12.5263 | 30.6346 | 1.3163 | 0.087756 | 360.7285 | 25.13 | 73.7
2021-01-05 21:50 | 1.2281 | 0.14811 | 0.088289 | 0.31532 | 39.5246 | 41.725 | 1.3372 | 0.21922 | 362.7029 | 24.47 | 74.26
2021-01-05 21:55 | 0.95877 | 0.11511 | 0.079823 | 0.25627 | 27.8477 | 0.69543 | 1.3217 | 0.19715 | 364.3137 | 23.8 | 74.92
2021-01-05 22:00 | 1.1631 | 0.15483 | 0.10081 | 0.33814 | 12.0861 | 11.6259 | 1.3287 | 0.18252 | 364.4103 | 23.34 | 76.45
2021-01-05 22:05 | 1.7004 | 0.11924 | 0.081931 | 0.2668 | 18.4919 | 14.7689 | 1.3218 | 0.11684 | 362.9808 | 23.13 | 78.33
2021-01-05 22:10 | 2.3021 | 0.16041 | 0.086164 | 0.33205 | 22.6526 | 9.1265 | 1.3003 | 0.20455 | 364.0319 | 23.03 | 80.07
2021-01-05 22:15 | 1.5095 | 0.13028 | 0.081982 | 0.28378 | 3.0293 | -7.3379 | 1.2788 | 0.13884 | 364.5054 | 23 | 81.11
2021-01-05 22:20 | 1.1132 | 0.090526 | 0.069381 | 0.21024 | -0.27637 | 4.3093 | 1.2717 | 0.19002 | 363.9394 | 22.98 | 81.78
2021-01-05 22:25 | 1.3955 | 0.1743 | 0.061007 | 0.32818 | 13.2531 | 17.4932 | 1.3017 | 0.19013 | 364.0446 | 23.15 | 82.98
2021-01-05 22:30 | 1.4738 | 0.19371 | 0.069493 | 0.36853 | 2.1838 | 12.7951 | 1.303 | 0.13909 | 362.4807 | 23.69 | 83.73
2021-01-05 22:35 | 1.36 | 0.20493 | 0.084329 | 0.39845 | 19.7068 | 9.9355 | 1.3118 | 0.10993 | 361.6891 | 24.44 | 83.59
2021-01-05 22:40 | 1.2451 | 0.27797 | 0.05906 | 0.48303 | 15.4448 | 17.8991 | 1.3125 | 0.095318 | 360.363 | 24.95 | 82.63
2021-01-05 22:45 | 0.64175 | 0.16098 | 0.063271 | 0.30792 | 19.4681 | 14.4573 | 1.3123 | 0.058651 | 361.188 | 25.17 | 81.21
2021-01-05 22:50 | 0.74413 | 0.20905 | 0.071679 | 0.39212 | 22.991 | 1.7859 | 1.3118 | 0.058627 | 360.7599 | 25.21 | 79.8
2021-01-05 22:55 | 1.5259 | 0.20069 | 0.067423 | 0.37504 | 21.3672 | 12.3197 | 1.311 | 0.073241 | 359.7541 | 25.21 | 78.12
2021-01-05 23:00 | 1.1405 | 0.12776 | 0.071594 | 0.26743 | 7.3403 | -11.3179 | 1.3102 | 0.058558 | 362.1102 | 25.18 | 76.45
2021-01-05 23:05 | 1.0247 | 0.15105 | 0.063145 | 0.29468 | 2.6643 | 6.7428 | 1.3024 | 0.036583 | 360.7429 | 25.13 | 75.4
2021-01-05 23:10 | 1.1911 | 0.21418 | 0.073658 | 0.40196 | 5.4098 | 7.2336 | 1.2949 | 0 | 362.3775 | 25.13 | 74.94
2021-01-05 23:15 | 1.0757 | 0.17847 | 0.065235 | 0.3367 | 7.5712 | 3.1658 | 1.2728 | 0.01463 | 360.8222 | 25.13 | 74.73
2021-01-05 23:20 | 0.67833 | 0.17013 | 0.067299 | 0.32808 | 9.6246 | 5.4778 | 1.2574 | 0.043864 | 362.0193 | 24.76 | 74.49
2021-01-05 23:25 | 0.5757 | 0.15497 | 0.075679 | 0.31323 | 10.3677 | -4.5954 | 1.2569 | 0.051153 | 362.1045 | 24.38 | 74.87
2021-01-05 23:30 | 0.67773 | 0.16038 | 0.063036 | 0.31098 | 4.5011 | -4.6341 | 1.2563 | 0.051129 | 363.6377 | 24.13 | 74.48
2021-01-05 23:35 | 0.63911 | 0.13154 | 0.069312 | 0.27095 | 6.1559 | 3.6813 | 1.2485 | 0.029205 | 363.5777 | 24.3 | 72.42
2021-01-05 23:40 | 0.46009 | 0.068502 | 0.063001 | 0.1701 | 7.525 | 0.57255 | 1.2483 | 0.0219 | 362.8218 | 24.53 | 70.96
2021-01-05 23:45 | 0.40906 | 0.091814 | 0.067217 | 0.20795 | -5.6042 | -19.8396 | 1.234 | 0.029207 | 363.0454 | 24.71 | 70.94
2021-01-05 23:50 |  | 0.25764 | 0.077722 | 0.47264 | 3.743 | -2.8124 | 1.2413 | 0.029208 | 362.5859 | 24.78 | 70.66
2021-01-05 23:55 | 0.34513 | 0.35217 | 0.075617 | 0.61544 | -5.1233 | 13.8361 | 1.234 | 0.029206 | 363.5801 | 24.85 | 70.16
2021-01-06 | 0.20446 | 0.14794 | 0.060893 | 0.28767 | -8.0658 | -9.7015 | 1.2408 | 0.029196 | 362.1653 | 24.81 | 69.3
2021-01-06 00:05 | 0.20446 | 0.18493 | 0.067194 | 0.35277 | 8.8736 | -4.7128 | 1.2482 | 0.043795 | 361.6562 | 24.79 | 69.43
2021-01-06 00:10 | 0.23002 | 0.10411 | 0.071395 | 0.22889 | 4.6311 | 8.332 | 1.2555 | 0.094893 | 362.1737 | 24.79 | 69.52
2021-01-06 00:15 | 0.24281 | 0.075348 | 0.054598 | 0.17219 | 1.4824 | 0.82811 | 1.2774 | 0.051097 | 363.0564 | 24.79 | 69.67
2021-01-06 00:20 | 0.16615 | 0.11646 | 0.056703 | 0.23731 | 6.2369 | 4.3454 | 1.2921 | 0.029201 | 364.2806 | 24.76 | 70
2021-01-06 00:25 | 0.25562 | 0.087688 | 0.054605 | 0.18902 | -1.1861 | -11.3496 | 1.2922 | 0.014601 | 363.7748 | 24.73 | 70.25
2021-01-06 00:30 | 0.2556 | 0.038361 | 0.0525 | 0.1113 | -7.484 | -2.9241 | 1.2848 | 0.0146 | 362.8088 | 24.68 | 70.21
2021-01-06 00:35 | 0.20448 | 0.027401 | 0.042001 | 0.084001 | 3.1388 | -5.9198 | 1.2848 | 0.0146 | 363.8989 | 24.65 | 70.36
2021-01-06 00:40 | 0.19173 | 0.010962 | 0.037806 | 0.054609 | 1.7383 | 3.8653 | 1.285 | 0.014602 | 362.8392 | 24.61 | 70.98
2021-01-06 00:45 | 0.17897 | 0.0041112 | 0.03361 | 0.039912 | -8.4474 | 0.18408 | 1.2925 | 0.007302 | 363.3815 | 24.56 | 71.6
2021-01-06 00:50 | 0.16619 | 0.0041114 | 0.033611 | 0.039913 | -0.42954 | -15.4329 | 1.2852 | -0.036511 | 362.3614 | 24.52 | 71.88
2021-01-06 00:55 | 0.14062 | 0.0082225 | 0.039912 | 0.052516 | 2.9045 | -7.4964 | 1.2706 | 0 | 363.4384 | 24.51 | 71.85
2021-01-06 01:00 | 0.17892 | 0.0137 | 0.0441 | 0.063 | -5.8277 | -0.86904 | 1.2629 | 0.0146 | 362.476 | 24.52 | 70.88
2021-01-06 01:05 |  |  |  |  | -0.24537 | 4.2634 |  |  | 362.4681 | 24.53 | 70.8
2021-01-06 01:10 |  |  |  |  | 6.9318 | -2.4026 |  |  | 364.0056 | 24.57 | 70.62
2021-01-06 01:15 |  |  |  |  | -4.8448 | -15.4338 |  |  | 362.533 | 24.56 | 69.79
2021-01-06 01:20 |  |  |  |  | -4.7633 | -0.7053 |  |  | 361.9792 | 24.56 | 70.01
2021-01-06 01:25 |  |  |  |  | 8.1269 | 2.7703 |  |  | 362.5038 | 24.54 | 70.34
2021-01-06 01:30 |  |  |  |  | -0.081764 | 11.4266 |  |  | 362.0711 | 24.52 | 69.8
2021-01-06 01:35 |  |  |  |  | 2.7593 | 0.61317 |  |  | 362.5981 | 24.55 | 69.37
2021-01-06 01:40 |  |  |  |  | 1.2162 | -6.8375 |  |  | 362.5289 | 24.58 | 69.53
2021-01-06 01:45 |  |  |  |  | -2.6569 | 5.2218 |  |  | 362.5999 | 24.57 | 69.06
2021-01-06 01:50 |  |  |  |  | -5.5376 | -3.8722 |  |  | 363.278 | 24.5 | 68.79
2021-01-06 01:55 |  |  |  |  | 7.4583 | -12.2909 |  |  | 362.7549 | 24.5 | 68.74
2021-01-06 02:00 |  |  |  |  | 6.9656 | 8.8142 |  |  | 364.4854 | 24.48 | 67.78
2021-01-06 02:05 |  |  |  |  | 6.8233 | -0.11236 |  |  | 363.3885 | 24.48 | 68.12
2021-01-06 02:10 | 0.15322 | 0.11087 | 0.056648 | 0.22659 | 10.2554 | 15.4649 | 1.3347 | -0.036466 | 363.9421 | 24.46 | 68.2
2021-01-06 02:15 | 0.16597 | 0.098538 | 0.052445 | 0.20349 | 4.3713 | 4.2487 | 1.3126 | -0.021877 | 363.8616 | 24.43 | 67.98
2021-01-06 02:20 | 0.19153 | 0.072547 | 0.048258 | 0.15946 | 0.18387 | -11.0935 | 1.3055 | -0.0072935 | 363.8347 | 24.4 | 68.66
2021-01-06 02:25 | 0.14047 | 0.057494 | 0.041966 | 0.1301 | 6.9978 | 1.9001 | 1.3056 | 0.014588 | 363.3419 | 24.35 | 69.08
2021-01-06 02:30 | 0.26815 | 0.099926 | 0.060848 | 0.21402 | -1.2871 | 1.6753 | 1.3056 | 0.021881 | 363.0181 | 24.33 | 68.95
2021-01-06 02:35 | 0.26819 | 0.22726 | 0.050365 | 0.39872 | 8.623 | 8.5822 | 1.3058 | 0.01459 | 362.876 | 24.4 | 69.16
2021-01-06 02:40 | 0.25546 | 0.18074 | 0.065065 | 0.34212 | 11.4549 | 11.1177 | 1.306 | 0.007296 | 363.2748 | 24.46 | 69.41
2021-01-06 02:45 | 0.47253 | 0.2259 | 0.075548 | 0.42181 | 9.0726 | -0.1839 | 1.2985 | 0.01459 | 363.1526 | 24.47 | 68.96
2021-01-06 02:50 | 0.43425 | 0.22043 | 0.054566 | 0.39455 | 7.7142 | 12.0158 | 1.2986 | 0.0072953 | 363.6119 | 24.51 | 68.98
2021-01-06 02:55 | 0.43428 | 0.35053 | 0.037779 | 0.57299 | 15.7874 | 8.9513 | 1.2987 | 0.0072959 | 361.9933 | 24.51 | 69.25
2021-01-06 03:00 | 0.40865 | 0.26284 | 0.050362 | 0.45326 | 15.0894 | 1.3383 | 1.2984 | 0.014589 | 363.6701 | 24.5 | 68.62
2021-01-06 03:05 | 0.38309 | 0.2067 | 0.056654 | 0.3735 | 5.3122 | -0.061294 | 1.2983 | 0.014588 | 364.2314 | 24.49 | 68.49
2021-01-06 03:10 | 0.21712 | 0.22317 | 0.071353 | 0.41553 | 8.7562 | 6.8762 | 1.2985 | 0.0072951 | 364.7045 | 24.49 | 68.98
2021-01-06 03:15 | 0.22982 | 0.17383 | 0.058745 | 0.3252 | 3.432 | 9.1929 | 1.2982 | 0.0072931 | 363.2921 | 24.43 | 68.33
2021-01-06 03:20 | 0.35751 | 0.15741 | 0.065041 | 0.30422 | 9.2034 | 1.7161 | 1.3055 | 0.014587 | 363.3177 | 24.4 | 68.55
2021-01-06 03:25 | 0.35751 | 0.13961 | 0.05455 | 0.26855 | 22.8399 | 15.2504 | 1.2982 | 0.0072932 | 362.7903 | 24.4 | 68.53
2021-01-06 03:30 | 0.21706 | 0.15467 | 0.062942 | 0.30002 | 5.6997 | 16.803 | 1.2982 | 0 | 362.7556 | 24.43 | 68.39
2021-01-06 03:35 | 0.21707 | 0.193 | 0.06924 | 0.36508 | 3.9736 | -1.5016 | 1.2982 | -0.0072935 | 363.7865 | 24.44 | 68.49
2021-01-06 03:40 | 0.28096 | 0.27655 | 0.067153 | 0.49316 | 15.2639 | 8.153 | 1.3058 | 0.021884 | 362.5785 | 24.51 | 68.76
2021-01-06 03:45 | 0.30643 | 0.26553 | 0.079724 | 0.48674 | 18.5593 | 3.289 | 1.2981 | 0.029172 | 363.7166 | 24.52 | 67.92
2021-01-06 03:50 | 0.3192 | 0.3942 | 0.083922 | 0.68816 | 11.3177 | 15.9959 | 1.3055 | 0.036466 | 361.0359 | 24.54 | 67.92
2021-01-06 03:55 | 0.45971 | 0.9076 | 0.1217 | 1.5129 | 24.6509 | 21.9233 | 1.3057 | 0.036471 | 363.5362 | 24.62 | 68.02
2021-01-06 04:00 | 0.49794 | 0.51189 | 0.11329 | 0.89794 | 21.9911 | 19.458 | 1.3054 | 0.014586 | 363.8894 | 24.68 | 67.31
2021-01-06 04:05 | 0.34476 | 0.5051 | 0.052455 | 0.82669 | 19.1636 | -4.2699 | 1.3056 | 0.036468 | 363.3361 | 24.67 | 67.66
2021-01-06 04:10 | 0.34477 | 0.43256 | 0.073439 | 0.73648 | 22.6476 | 32.8017 | 1.3056 | 0.036469 | 363.8442 | 24.68 | 67.7
2021-01-06 04:15 | 0.34473 | 0.46673 | 0.1091 | 0.82452 | 19.0088 | 22.5736 | 1.3127 | 0.036465 | 363.3173 | 24.71 | 67.24
2021-01-06 04:20 | 0.37028 | 0.43252 | 0.11539 | 0.77838 | 17.855 | 12.0735 | 1.3055 | 0.014586 | 363.8521 | 24.7 | 67.34
2021-01-06 04:25 | 0.35744 | 0.58708 | 0.13635 | 1.0342 | 22.8763 | 2.4715 | 1.3052 | 0.021875 | 363.414 | 24.68 | 66.84
2021-01-06 04:30 | 0.54901 | 0.64466 | 0.13427 | 1.1224 | 23.9012 | 34.6874 | 1.32 | 0.05105 | 363.2487 | 24.77 | 66.96
2021-01-06 04:35 | 0.72784 | 0.80899 | 0.18045 | 1.4205 |  |  | 1.3202 | 0.051056 | 456.7883 | 24.86 | 66.92
2021-01-06 04:40 | 0.82978 | 0.96068 | 0.1804 | 1.653 |  |  | 1.3125 | 0.072918 | 473.7184 | 24.94 | 65.82
2021-01-06 04:45 | 1.6981 | 0.96354 | 0.19091 | 1.6679 |  | 1.8998 | 1.32 | 0.1021 | 475.2162 | 24.96 | 66.12
2021-01-06 04:50 | 2.0808 | 1.2823 | 0.19928 | 2.1648 | 24.7345 | 43.6173 | 1.3271 | 0.16042 | 474.1781 | 24.99 | 65.56
2021-01-06 04:55 | 2.9999 | 1.3247 | 0.23704 | 2.2655 | 56.7922 | 67.5256 | 1.3344 | 0.14584 | 472.9862 | 25.07 | 65.29
2021-01-06 05:00 | 2.4893 | 1.2453 | 0.21816 | 2.127 | 69.3027 | 54.9846 | 1.3344 | 0.15313 | 472.922 | 25.11 | 65.14
2021-01-06 05:05 | 1.902 | 1.1796 | 0.24961 | 2.0556 | 73.9248 | 74.3333 | 1.327 | 0.13854 | 473.3348 | 25.2 | 64.62
2021-01-06 05:10 | 1.3402 | 1.137 | 0.32089 | 2.0658 | 58.1911 | 61.1522 | 1.3196 | 0.17497 | 473.33 | 25.24 | 64.09
2021-01-06 05:15 | 1.876 | 1.2805 | 0.35231 | 2.3173 | 73.6527 | 43.9425 | 1.3121 | 0.18953 | 473.8449 | 25.28 | 63.62
2021-01-06 05:20 | 3.5357 | 1.5818 | 0.37754 | 2.8022 | 65.4449 | 54.3553 | 1.3342 | 0.21873 | 471.0271 | 25.34 | 63.9
2021-01-06 05:25 | 2.7822 | 1.966 | 0.38378 | 3.3974 | 66.7738 | 72.0014 | 1.3341 | 0.24057 | 470.9784 | 25.41 | 63.24
2021-01-06 05:30 | 3.0765 | 2.6535 | 0.47616 | 4.5435 | 87.1122 | 65.9826 | 1.3344 | 0.31354 | 470.6005 | 25.58 | 63.3
2021-01-06 05:35 | 4.0208 | 2.7394 | 0.50968 | 4.7087 | 98.5408 | 91.0456 | 1.3415 | 0.3208 | 469.8335 | 25.76 | 62.35
2021-01-06 05:40 | 3.9697 | 2.8023 | 0.52645 | 4.822 | 111.8867 | 95.3136 | 1.3634 | 0.36455 | 468.5289 | 25.92 | 61.75
2021-01-06 05:45 | 3.7524 | 2.7884 | 0.59981 | 4.874 | 105.618 | 82.1439 | 1.3633 | 0.34994 | 468.8777 | 26.06 | 60.99
2021-01-06 05:50 | 2.7059 | 2.452 | 0.54741 | 4.308 | 104.4186 | 84.3436 | 1.3488 | 0.28434 | 469.7511 | 26.16 | 60.78
2021-01-06 05:55 | 2.8589 | 2.4477 | 0.57254 | 4.3245 | 106.9949 | 101.0933 | 1.3414 | 0.29161 | 467.5951 | 26.21 | 60.41
2021-01-06 06:00 | 3.6754 | 2.5542 | 0.60394 | 4.5191 | 108.0053 | 94.4064 | 1.3486 | 0.34261 | 470.1107 | 26.28 | 59.94
2021-01-06 06:05 | 2.9994 | 2.1222 | 0.55159 | 3.8045 | 116.7714 | 95.2469 | 1.3998 | 0.34266 | 469.4062 | 26.35 | 60.1
2021-01-06 06:10 | 2.5521 | 1.8987 | 0.49276 | 3.4032 | 117.6946 | 106.1998 | 1.4141 | 0.23325 | 469.543 | 26.33 | 59.53
2021-01-06 06:15 | 2.4757 | 1.7771 | 0.35438 | 3.0783 | 114.5154 | 86.032 | 1.3631 | 0.2041 | 469.4407 | 26.38 | 59.5
2021-01-06 06:20 | 2.8453 | 2.0462 | 0.39206 | 3.5285 | 100.0204 | 65.959 | 1.3993 | 0.32796 | 471.1257 | 26.37 | 59.01
2021-01-06 06:25 | 2.5393 | 2.0628 | 0.36484 | 3.5267 | 90.0974 | 76.3265 | 1.4359 | 0.21866 | 470.5221 | 26.39 | 59.21
2021-01-06 06:30 | 2.0541 | 2.0365 | 0.39623 | 3.52 | 91.4623 | 67.3438 | 1.3045 | 0.13118 | 470.0623 | 26.39 | 58.8
2021-01-06 06:35 | 2.297 | 2.3597 | 0.48228 | 4.0994 | 99.2896 | 89.8364 | 1.2829 | 0.22596 | 468.8227 | 26.45 | 59.14
2021-01-06 06:40 | 2.5647 | 2.0846 | 0.41094 | 3.6063 | 112.2743 | 104.4858 | 1.29 | 0.24051 | 468.7591 | 26.52 | 58.62
2021-01-06 06:45 | 2.6665 | 2.1131 | 0.38575 | 3.6269 | 102.884 | 61.8529 | 1.2972 | 0.30608 | 470.3055 | 26.57 | 58.19
2021-01-06 06:50 | 3.8149 | 2.0133 | 0.37528 | 3.4614 | 86.5261 | 50.5867 | 1.3337 | 0.46643 | 469.2162 | 26.58 | 58.27
2021-01-06 06:55 | 3.1895 | 2.3373 | 0.43395 | 4.0187 | 90.6012 | 64.2179 | 1.3481 | 0.41538 | 469.2253 | 26.6 | 57.96
2021-01-06 07:00 | 2.6284 | 2.8546 | 0.44239 | 4.818 | 96.7673 | 80.1291 | 1.3119 | 0.29881 | 470.1442 | 26.65 | 58.13
2021-01-06 07:05 | 3.9681 | 3.0679 | 0.4277 | 5.1303 | 109.4836 | 93.7337 | 1.3118 | 0.33525 | 470.0757 | 26.7 | 57.9
2021-01-06 07:10 | 4.0702 | 2.9804 | 0.42561 | 4.994 | 102.6854 | 88.0685 | 1.3629 | 0.39355 | 469.4868 | 26.74 | 57.76
2021-01-06 07:15 | 3.5208 | 3.0673 | 0.49469 | 5.1964 | 99.5521 | 73.0899 | 1.4209 | 0.32061 | 469.5811 | 26.74 | 57.2
2021-01-06 07:20 | 3.9677 | 2.3482 | 0.41298 | 4.0103 | 91.6313 | 65.6463 | 1.3846 | 0.18947 | 468.994 | 26.75 | 57.43
2021-01-06 07:25 | 4.6442 | 2.094 | 0.38366 | 3.5934 | 90.9443 | 76.7872 | 1.341 | 0.2405 | 469.9489 | 26.79 | 57.51
2021-01-06 07:30 | 3.5853 | 1.7658 | 0.40044 | 3.1071 | 84.9845 | 77.2271 | 1.3337 | 0.29152 | 469.9276 | 26.8 | 57.51
2021-01-06 07:35 | 2.7938 | 1.8845 | 0.40039 | 3.287 | 85.6066 | 67.0932 | 1.3335 | 0.29148 | 469.5379 | 26.75 | 57.33
2021-01-06 07:40 | 3.036 | 1.8434 | 0.31232 | 3.1358 | 92.58 | 82.9873 | 1.3334 | 0.27688 | 470.1492 | 26.72 | 57.21
2021-01-06 07:45 | 3.661 | 2.069 | 0.33118 | 3.5047 | 95.4065 | 108.8872 | 1.348 | 0.36432 | 470.1981 | 26.69 | 57.3
2021-01-06 07:50 | 4.1076 | 2.5463 | 0.37521 | 4.2782 | 127.1265 | 107.012 | 1.348 | 0.29146 | 469.5557 | 26.72 | 57.32
2021-01-06 07:55 | 3.8525 | 1.9624 | 0.36473 | 3.3727 | 124.2903 | 84.3366 | 1.3407 | 0.26232 | 471.1352 | 26.72 | 57.34
2021-01-06 08:00 | 3.7878 | 1.7377 | 0.36255 | 3.0261 | 90.8563 | 59.4418 | 1.3404 | 0.2404 | 470.8619 | 26.63 | 56.97
2021-01-06 08:05 | 3.1763 | 1.7955 | 0.39407 | 3.1441 | 72.5162 | 46.4528 | 1.3334 | 0.26231 | 470.2222 | 26.64 | 57.51
2021-01-06 08:10 | 3.0356 | 1.6353 | 0.37515 | 2.8838 | 70.3433 | 50.528 | 1.3551 | 0.26956 | 471.2943 | 26.67 | 57.03
2021-01-06 08:15 | 3.1249 | 1.4863 | 0.33743 | 2.6135 | 77.7115 | 60.1713 | 1.3551 | 0.25499 | 468.6325 | 26.68 | 57.04
2021-01-06 08:20 | 2.6911 | 1.5628 | 0.39401 | 2.7916 | 66.4036 | 56.3023 | 1.3405 | 0.22584 | 470.7115 | 26.71 | 56.85
2021-01-06 08:25 | 2.3975 | 1.4354 | 0.34366 | 2.5439 | 55.2133 | 58.682 | 1.3403 | 0.21853 | 470.2152 | 26.73 | 56.41
2021-01-06 08:30 | 2.7164 | 1.6528 | 0.30805 | 2.8416 | 52.3071 | 27.3625 | 1.3331 | 0.2331 | 471.3531 | 26.67 | 56.68
2021-01-06 08:35 | 2.3595 | 1.7022 | 0.33322 | 2.9424 | 56.2199 | 49.9959 | 1.3259 | 0.22584 | 470.7962 | 26.66 | 56.98
2021-01-06 08:40 | 2.768 | 2.0689 | 0.33746 | 3.5108 | 78.0952 | 71.7174 | 1.3406 | 0.25501 | 471.7929 | 26.66 | 57.33
2021-01-06 08:45 | 2.5509 | 1.9648 | 0.36467 | 3.3763 | 87.097 | 55.3846 | 1.3332 | 0.26956 | 468.6425 | 26.68 | 56.98
2021-01-06 08:50 | 2.3854 | 1.7394 | 0.37939 | 3.0456 | 94.7621 | 76.7403 | 1.3261 | 0.22587 | 470.1328 | 26.7 | 57.28
2021-01-06 08:55 | 2.2445 | 1.8552 | 0.35206 | 3.1957 | 83.384 | 80.4049 | 1.3331 | 0.18211 | 469.2061 | 26.69 | 56.64
2021-01-06 09:00 | 2.3465 | 1.672 | 0.39397 | 2.9568 | 76.773 | 36.749 | 1.3258 | 0.17483 | 470.2454 | 26.7 | 56.61
2021-01-06 09:05 | 2.5886 | 2.0013 | 0.38136 | 3.449 | 66.8599 | 41.7135 | 1.3257 | 0.18938 | 469.7322 | 26.72 | 56.27
2021-01-06 09:10 | 2.2189 | 1.6801 | 0.3206 | 2.8959 | 60.3938 | 46.8256 | 1.3184 | 0.1821 | 470.232 | 26.73 | 56.31
2021-01-06 09:15 | 3.1376 | 1.4575 | 0.31227 | 2.5443 | 51.6604 | 39.1305 | 1.3624 | 0.28413 | 468.5632 | 26.73 | 56.82
2021-01-06 09:20 | 3.0611 | 1.4206 | 0.3039 | 2.4815 | 61.8143 | 51.6106 | 1.3915 | 0.25499 | 470.0728 | 26.77 | 56.75
2021-01-06 09:25 | 2.5636 | 1.426 | 0.32065 | 2.5065 | 63.2299 | 33.9566 | 1.3915 | 0.21855 | 470.093 | 26.77 | 56.63
2021-01-06 09:30 | 2.3591 | 1.6582 | 0.25564 | 2.7953 | 73.6148 | 92.4571 | 1.333 | 0.19667 | 458.593 | 26.75 | 56.23
2021-01-06 09:35 | 2.219 | 1.8497 | 0.30804 | 3.1433 | 97.4309 | 281.8661 | 1.3258 | 0.19668 | 419.5592 | 26.72 | 56.49
2021-01-06 09:40 | 2.5379 | 1.9592 | 0.39189 | 3.3949 | 240.3564 | 328.7531 | 1.3258 | 0.21854 | 351.4137 | 26.76 | 56.51
2021-01-06 09:45 | 3.5205 | 1.8966 | 0.39824 | 3.3054 | 199.2305 | 116.7382 | 1.3333 | 0.27687 | 350.1737 | 26.87 | 56.59
2021-01-06 09:50 | 4.0049 | 1.8007 | 0.43384 | 3.1941 | 146.8821 | 96.7106 | 1.3405 | 0.31327 | 351.1355 | 26.97 | 56.07
2021-01-06 09:55 | 3.035 | 2.0478 | 0.4107 | 3.5496 | 116.5642 | 62.6586 | 1.333 | 0.21124 | 351.4745 | 27.04 | 55.35
2021-01-06 10:00 | 2.7159 | 1.6512 | 0.37504 | 2.906 | 93.5288 | 44.7396 | 1.3037 | 0.18208 | 351.8062 | 26.94 | 55.32
2021-01-06 10:05 | 3.7996 | 1.6402 | 0.40646 | 2.9207 | 68.4956 | 70.505 | 1.2891 | 0.25491 | 352.7858 | 26.86 | 55.59
2021-01-06 10:10 | 3.6084 | 1.9013 | 0.41275 | 3.3271 | 66.5582 | 54.2054 | 1.2818 | 0.27676 | 352.2889 | 26.83 | 55.72
2021-01-06 10:15 | 3.7744 | 2.2281 | 0.46097 | 3.8763 | 64.0014 | 51.5051 | 1.3038 | 0.37874 | 351.2486 | 26.8 | 55.97
2021-01-06 10:20 | 5.5465 | 2.6613 | 0.61808 | 4.6974 | 29.3266 |  | 1.3255 | 0.50254 | 413.5409 | 26.84 | 55.7
2021-01-06 10:25 | 4.4118 | 1.6594 | 0.45885 | 3.0024 |  |  | 1.3255 | 0.38601 | 499.4891 | 26.94 | 55.33
2021-01-06 10:30 | 3.569 | 2.118 | 0.42519 | 3.6717 |  | 10.4216 | 1.3178 | 0.28395 | 499.8699 | 26.81 | 54.84
2021-01-06 10:35 | 2.9828 | 1.8434 | 0.41682 | 3.2424 | 7.8317 | 62.3476 | 1.3179 | 0.24755 | 499.5616 | 26.67 | 55.37
2021-01-06 10:40 | 3.1365 | 1.3067 | 0.35197 | 2.3549 | 46.3082 | 34.7923 | 1.3255 | 0.23305 | 497.8206 | 26.69 | 56
2021-01-06 10:45 | 2.7928 | 1.2837 | 0.28918 | 2.2569 | 57.8868 | 35.3809 | 1.3403 | 0.19668 | 498.6751 | 26.75 | 56.37
2021-01-06 10:50 | 2.9714 | 1.255 | 0.30595 | 2.2297 | 58.2243 | 29.0254 | 1.3258 | 0.18211 | 498.6182 | 26.78 | 56.31
2021-01-06 10:55 | 2.6394 | 1.0648 | 0.28075 | 1.9129 | 56.745 | 39.6389 | 1.2891 | 0.28404 | 498.7078 | 26.78 | 55.81
2021-01-06 11:00 | 2.6392 | 1.0046 | 0.32893 | 1.8709 | 136.7302 | 100.347 | 1.289 | 0.38599 | 419.5818 | 26.77 | 55.71
2021-01-06 11:05 | 2.6774 | 1.062 | 0.36453 | 1.9923 |  |  | 1.3181 | 0.26217 | 497.6099 | 26.83 | 55.42
2021-01-06 11:10 | 2.9069 | 1.077 | 0.28911 | 1.94 | -6.6297 | 15.9113 | 1.3254 | 0.22576 | 497.6135 | 26.83 | 55.4
2021-01-06 11:15 | 2.6647 | 1.5048 | 0.30168 | 2.6083 | 29.3445 | 50.9475 | 1.3327 | 0.23304 | 498.6769 | 26.82 | 55.48
2021-01-06 11:20 | 2.2442 | 1.6677 | 0.32896 | 2.8873 | 44.9972 | 14.8732 | 1.3329 | 0.20394 | 495.9195 | 26.85 | 55.77
2021-01-06 11:25 | 2.1036 | 1.446 | 0.33729 | 2.5517 | 45.6836 | 19.9502 | 1.3254 | 0.19663 | 496.5428 | 26.84 | 55.36
2021-01-06 11:30 | 2.2694 | 1.0989 | 0.30796 | 1.9902 | 59.2795 | 40.6144 | 1.3254 | 0.16021 | 496.4766 | 26.88 | 55.23
2021-01-06 11:35 | 1.7597 | 1.2207 | 0.28496 | 2.1561 | 65.1447 | 91.5963 | 1.3183 | 0.13111 | 474.7513 | 26.89 | 55.65
2021-01-06 11:40 | 2.2695 | 1.5951 | 0.34988 | 2.7949 | 169.9329 | 42.4832 | 1.3182 | 0.18207 | 433.6681 | 26.88 | 55.38
2021-01-06 11:45 | 2.5239 | 1.5851 | 0.32466 | 2.7544 | 89.2191 | -0.68324 | 1.3252 | 0.20387 | 454.3209 | 26.9 | 54.66
2021-01-06 11:50 | 2.8291 | 1.4686 | 0.30154 | 2.5526 | 73.4853 | 37.4257 | 1.3321 | 0.23293 | 452.8267 | 26.92 | 53.87
2021-01-06 11:55 | 3.2108 | 1.6568 | 0.36011 | 2.8997 | 65.062 | 34.7786 | 1.3246 | 0.24745 | 452.8676 | 26.95 | 53.25
2021-01-06 12:00 | 3.3503 | 1.7698 | 0.37887 | 3.0917 | 73.0487 | 68.8399 | 1.3243 | 0.32744 | 453.4722 | 26.96 | 52.66
2021-01-06 12:05 | 2.5984 | 1.5115 | 0.31185 | 2.6308 | 78.725 | 41.2476 | 1.3241 | 0.27646 | 454.0442 | 26.97 | 52.27
2021-01-06 12:10 | 3.2861 | 1.3285 | 0.28882 | 2.3252 | 108.11 | 143.2942 | 1.3241 | 0.24008 | 451.3822 | 26.99 | 52.16
2021-01-06 12:15 | 2.7383 | 1.1837 | 0.30346 | 2.118 | 134.2616 | 71.2115 | 1.3168 | 0.2037 | 469.7982 | 27.04 | 51.91
2021-01-06 12:20 | 2.2035 | 1.4227 | 0.3265 | 2.5073 | 93.2651 | 54.2085 | 1.3168 | 0.20371 | 470.3038 | 27.04 | 52.04
2021-01-06 12:25 | 2.1022 | 1.6335 | 0.34124 | 2.843 | 69.8078 | 42.1966 | 1.3172 | 0.21104 | 470.6221 | 27.09 | 52.65
2021-01-06 12:30 | 2.7523 | 1.3974 | 0.335 | 2.4769 | 58.2158 | 49.857 | 1.3246 | 0.24018 | 470.0536 | 27.08 | 53.01
2021-01-06 12:35 | 2.5867 | 1.564 | 0.37689 | 2.7743 | 58.9817 | 26.1677 | 1.332 | 0.21107 | 469.9799 | 27.12 | 52.95
2021-01-06 12:40 | 2.306 | 1.5406 | 0.35798 | 2.7194 | 44.998 | 22.9424 | 1.3172 | 0.21104 | 470.0468 | 27.13 | 52.44
2021-01-06 12:45 | 3.0455 | 1.5955 | 0.35178 | 2.7975 | 45.6602 | 31.4086 | 1.3247 | 0.22564 | 470.9842 | 27.14 | 53
2021-01-06 12:50 | 3.7328 | 1.6279 | 0.33076 | 2.8261 | 55.6072 | 29.9235 | 1.3244 | 0.23287 | 469.0143 | 27.12 | 52.43
2021-01-06 12:55 | 2.9301 | 1.4695 | 0.35169 | 2.6063 | 55.7696 | 35.6408 | 1.3099 | 0.21103 | 470.0746 | 27.12 | 52.4
2021-01-06 13:00 | 3.2618 | 1.5448 | 0.38942 | 2.7574 | 69.925 | 73.9003 | 1.3173 | 0.24017 | 469.3921 | 27.18 | 52.57
2021-01-06 13:05 | 2.6503 | 1.4369 | 0.37268 | 2.5753 | 58.6321 | 42.8325 | 1.3028 | 0.21106 | 469.289 | 27.24 | 52.44
2021-01-06 13:10 | 2.8163 | 1.6393 | 0.33503 | 2.8499 | 69.2008 | 31.5726 | 1.3102 | 0.23293 | 469.2476 | 27.23 | 52.8
2021-01-06 13:15 | 2.4471 | 1.8664 | 0.32043 | 3.1813 | 72.6279 | 45.3835 | 1.3104 | 0.2184 | 470.2877 | 27.19 | 53.37
2021-01-06 13:20 | 2.6639 | 1.8022 | 0.34767 | 3.1081 | 64.3925 | 19.8735 | 1.3178 | 0.23298 | 470.2493 | 27.2 | 53.47
2021-01-06 13:25 | 2.8167 | 1.6204 | 0.33299 | 2.8168 | 61.4114 | 62.6859 | 1.3104 | 0.22568 | 469.7656 | 27.19 | 53.34
2021-01-06 13:30 | 2.8925 | 1.31 | 0.32454 | 2.3304 | 68.8484 | 29.8676 | 1.3028 | 0.19651 | 471.5376 | 27.14 | 52.85
2021-01-06 13:35 |  |  |  |  | 76.4318 | 46.5724 |  |  | 469.6828 | 27.06 | 52.34
2021-01-06 13:40 | 2.4067 | 1.0457 | 0.26574 | 1.8686 | 56.9566 | 32.762 | 1.3093 | 0.20366 | 469.8855 | 27.04 | 51.4
2021-01-06 13:45 | 3.7295 | 1.1516 | 0.27609 | 2.0414 | 45.2019 | 40.2937 | 1.316 | 0.23266 | 470.659 | 27.01 | 50.33
2021-01-06 13:50 | 4.2754 | 1.3654 | 0.31154 | 2.4045 | 56.2323 | 52.079 | 1.3228 | 0.25439 | 471.2913 | 27.04 | 49.36
2021-01-06 13:55 | 3.7924 | 1.6317 | 0.33041 | 2.8336 | 67.6631 | 43.6155 | 1.3157 | 0.23262 | 470.6823 | 27.05 | 49.71
2021-01-06 14:00 | 2.8252 | 1.5825 | 0.30531 | 2.731 | 62.8667 | 62.5613 | 1.3157 | 0.21807 | 470.6598 | 27.07 | 49.6
2021-01-06 14:05 | 2.8644 | 1.6118 | 0.30542 | 2.776 | 69.6728 | 58.1234 | 1.3162 | 0.21815 | 471.4956 | 27.1 | 50.52
2021-01-06 14:10 | 4.0125 | 1.5594 | 0.337 | 2.7295 | 67.9508 | 44.6348 | 1.3388 | 0.23283 | 469.0919 | 27.11 | 52.1
2021-01-06 14:15 | 3.5926 | 1.5501 | 0.33285 | 2.7089 | 77.8451 | 63.7804 | 1.3608 | 0.26197 | 470.0431 | 27.14 | 52.34
2021-01-06 14:20 | 3.4262 | 1.6262 | 0.31812 | 2.8108 | 77.7957 | 58.1608 | 1.3532 | 0.30556 | 470.1882 | 27.12 | 51.74
2021-01-06 14:25 | 3.7046 | 1.4493 | 0.30751 | 2.527 | 60.8629 | 32.3563 | 1.3307 | 0.27633 | 471.5287 | 27.08 | 50.57
2021-01-06 14:30 | 3.6153 | 1.5516 | 0.37234 | 2.7486 | 61.298 | 70.6368 | 1.3379 | 0.3054 | 472.7013 | 27.02 | 50.62
2021-01-06 14:35 | 3.3997 | 1.6148 | 0.37033 | 2.8476 | 72.5168 | 60.8432 | 1.3455 | 0.32002 | 472.5631 | 27.04 | 51.18
2021-01-06 14:40 | 3.8596 | 1.8366 | 0.34536 | 3.1606 | 75.6432 | 60.4697 | 1.3606 | 0.31287 | 470.7939 | 27.04 | 52.26
2021-01-06 14:45 | 3.1708 | 1.7528 | 0.32224 | 3.009 | 78.331 | 52.078 | 1.3675 | 0.29823 | 472.5623 | 27.01 | 51.55
2021-01-06 14:50 | 3.4888 | 1.7581 | 0.3243 | 3.017 | 73.1374 | 50.9517 | 1.3891 | 0.33456 | 471.6067 | 26.98 | 51.33
2021-01-06 14:55 | 3.0676 | 1.8366 | 0.42249 | 3.2377 | 64.885 | 49.8042 | 1.3814 | 0.23993 | 470.7092 | 26.98 | 50.4
2021-01-06 15:00 | 4.6458 | 2.0358 | 0.43503 | 3.5576 | 72.7645 | 53.6824 | 1.3596 | 0.34171 | 473.2686 | 27.04 | 50.15
2021-01-06 15:05 | 5.0417 | 1.7511 | 0.37657 | 3.0607 | 80.016 | 72.377 | 1.3527 | 0.36362 | 472.0519 | 27.06 | 50.84
2021-01-06 15:10 | 3.5656 | 1.8225 | 0.41014 | 3.2037 | 97.9534 | 92.7578 | 1.382 | 0.25459 | 470.8614 | 27.08 | 51.38
2021-01-06 15:15 | 2.3046 | 1.9 | 0.36823 | 3.2806 | 102.8186 | 76.8542 | 1.3964 | 0.24001 | 472.5123 | 27.08 | 50.99
2021-01-06 15:20 | 2.1128 | 1.5977 | 0.32626 | 2.7753 | 77.2731 | 50.0865 | 1.4031 | 0.19629 | 473.795 | 27.05 | 50.04
2021-01-06 15:25 | 2.5589 | 1.6282 | 0.35772 | 2.8534 | 76.2432 | 75.0924 | 1.3744 | 0.20361 | 472.6057 | 27.06 | 50.69
2021-01-06 15:30 | 2.7246 | 1.7347 | 0.35774 | 3.0168 | 72.1424 | 60.0932 | 1.3308 | 0.22544 | 472.0065 | 27.09 | 50.74
2021-01-06 15:35 | 2.7251 | 1.503 | 0.32433 | 2.6281 | 78.9001 | 56.7734 | 1.3456 | 0.20366 | 472.4133 | 27.11 | 51.2
2021-01-06 15:40 | 2.8003 | 1.5037 | 0.31792 | 2.6229 | 59.1836 | 61.4951 | 1.3378 | 0.21812 | 471.6322 | 27.06 | 50.21
2021-01-06 15:45 | 2.9416 | 1.4839 | 0.31178 | 2.5842 | 69.2736 | 52.6887 | 1.3384 | 0.26185 | 472.9455 | 27.07 | 51.39
2021-01-06 15:50 | 2.5982 | 1.2547 | 0.30346 | 2.2246 | 67.8886 | 35.3555 | 1.3459 | 0.2619 | 472.9424 | 27.06 | 51.8
2021-01-06 15:55 | 2.6745 | 1.3025 | 0.32856 | 2.3229 | 74.9779 | 57.0867 | 1.3604 | 0.24734 | 471.4514 | 27.01 | 51.87
2021-01-06 16:00 | 3.7314 | 1.2888 | 0.30553 | 2.281 | 76.1463 | 73.2121 | 1.353 | 0.2255 | 473.0085 | 27.04 | 51.66
2021-01-06 16:05 | 4.1885 | 1.3811 | 0.30124 | 2.4183 | 75.1224 | 78.3 | 1.338 | 0.24724 | 472.1125 | 27.04 | 50.73
2021-01-06 16:10 | 3.6672 | 1.5711 | 0.32222 | 2.7305 | 69.5039 | 40.431 | 1.3456 | 0.24729 | 473.6353 | 27.02 | 51.33
2021-01-06 16:15 | 3.8837 | 1.7186 | 0.37453 | 3.0088 | 58.5326 | 55.6803 | 1.3601 | 0.24729 | 472.5967 | 27.01 | 51.35
2021-01-06 16:20 | 3.7052 | 1.7048 | 0.37032 | 2.9856 | 67.6865 | 63.1741 | 1.3528 | 0.25455 | 472.0803 | 27.02 | 51.16
2021-01-06 16:25 | 3.0941 | 1.6148 | 0.33895 | 2.8162 | 58.4293 | 55.8827 | 1.3383 | 0.24001 | 472.593 | 27.02 | 51.25
2021-01-06 16:30 | 2.8531 | 1.4474 | 0.28464 | 2.5032 | 68.7706 | 66.9059 | 1.3678 | 0.28374 | 471.9262 | 27.01 | 52.18
2021-01-06 16:35 | 3.0945 | 1.4826 | 0.28668 | 2.5613 | 52.9964 | 23.7679 | 1.353 | 0.23277 | 473.6679 | 26.97 | 51.75
2021-01-06 16:40 | 4.0006 | 1.5652 | 0.3266 | 2.7258 | 56.4877 | 70.9511 | 1.3463 | 0.26927 | 473.02 | 26.9 | 53.31
2021-01-06 16:45 | 3.7086 | 1.3689 | 0.31831 | 2.4166 | 56.0234 | 53.3829 | 1.3394 | 0.26934 | 473.9507 | 26.9 | 54.04
2021-01-06 16:50 | 3.4272 | 1.1609 | 0.26378 | 2.0433 | 41.1774 | 44.8977 | 1.3172 | 0.26926 | 473.6847 | 26.82 | 53.5
2021-01-06 16:55 | 3.7078 | 1.1801 | 0.2659 | 2.0727 | 82.3101 | 103.3183 | 1.3028 | 0.26201 | 473.6649 | 26.81 | 53.74
2021-01-06 17:00 | 3.0452 | 1.2129 | 0.26381 | 2.123 | 103.7266 | 68.2745 | 1.2955 | 0.21106 | 473.1656 | 26.79 | 53.82
2021-01-06 17:05 | 2.8672 | 1.127 | 0.22196 | 1.9495 | 78.7213 | 40.0131 | 1.3029 | 0.17469 | 474.2156 | 26.76 | 54.23
2021-01-06 17:10 | 3.1869 | 1.1493 | 0.21366 | 1.9732 | 53.9282 | 43.0977 | 1.318 | 0.18932 | 473.558 | 26.73 | 55.37
2021-01-06 17:15 | 2.9444 | 1.0945 | 0.20736 | 1.883 | 44.6942 | 29.582 | 1.3615 | 0.16746 | 472.0699 | 26.7 | 55.18
2021-01-06 17:20 | 2.5862 | 0.86041 | 0.17585 | 1.4947 | 36.3853 | 11.9654 | 1.3608 | 0.16737 | 475.0413 | 26.61 | 54.09
2021-01-06 17:25 | 2.1906 | 0.92294 | 0.20091 | 1.6177 | 37.2297 | 20.7137 | 1.3458 | 0.13822 | 474.6943 | 26.59 | 53.26
2021-01-06 17:30 | 1.8847 | 0.93786 | 0.21344 | 1.651 | 39.9564 | 43.1044 | 1.3457 | 0.13821 | 474.2265 | 26.58 | 53.02
2021-01-06 17:35 | 1.7567 | 0.86107 | 0.20499 | 1.5249 | 76.8462 | 243.3905 | 1.3452 | 0.12361 | 401.4542 | 26.5 | 52.14
2021-01-06 17:40 | 2.5587 | 0.9798 | 0.23009 | 1.732 | 234.1653 | 240.1636 | 1.3379 | 0.15997 | 318.6516 | 26.47 | 52.3
2021-01-06 17:45 | 3.0299 | 0.99215 | 0.2824 | 1.8032 | 165.3952 | 74.1936 | 1.3598 | 0.19634 | 319.0541 | 26.57 | 52.18
2021-01-06 17:50 | 2.7243 | 0.83382 | 0.24893 | 1.527 | 92.2688 | 29.9212 | 1.3452 | 0.16724 | 319.0084 | 26.62 | 51.96
2021-01-06 17:55 | 2.1764 | 0.82272 | 0.21123 | 1.4723 | 54.2798 | 18.9384 | 1.3231 | 0.1454 | 319.005 | 26.69 | 51.12
2021-01-06 18:00 | 1.8957 | 0.66014 | 0.21534 | 1.2293 | 33.8334 | 23.6752 | 1.3227 | 0.13808 | 319.6418 | 26.69 | 50.18
2021-01-06 18:05 | 1.5774 | 0.85096 | 0.1735 | 1.48 | 37.6956 | 41.0947 | 1.3225 | 0.15259 | 319.17 | 26.68 | 49.79
2021-01-06 18:10 | 2.0989 | 0.95593 | 0.19022 | 1.6534 | 44.5839 | 38.5491 | 1.3224 | 0.27611 | 320.2523 | 26.67 | 49.72
2021-01-06 18:15 | 2.2136 | 0.92327 | 0.19441 | 1.6096 | 61.0133 | 44.5565 | 1.3298 | 0.29793 | 319.71 | 26.66 | 49.95
2021-01-06 18:20 | 2.2392 | 0.93699 | 0.23624 | 1.6725 | 48.6316 | 36.3159 | 1.3372 | 0.27616 | 320.1917 | 26.68 | 50.13
2021-01-06 18:25 | 1.8957 | 0.82106 | 0.2446 | 1.5032 | 37.2119 | 36.3976 | 1.3445 | 0.19622 | 319.6911 | 26.65 | 50.24
2021-01-06 18:30 | 2.3286 | 0.96575 | 0.26554 | 1.7438 | 45.0034 | 22.6188 | 1.3446 | 0.22531 | 319.6654 | 26.64 | 50.59
2021-01-06 18:35 | 2.507 | 1.0545 | 0.2572 | 1.8715 | 41.8015 | 27.5385 | 1.3448 | 0.24714 | 319.673 | 26.6 | 51.02
2021-01-06 18:40 | 3.1052 | 0.97272 | 0.25303 | 1.7441 | 40.2967 | 40.928 | 1.3376 | 0.21081 | 319.6678 | 26.59 | 51.19
2021-01-06 18:45 | 2.5074 | 1.0629 | 0.23843 | 1.8677 | 37.3597 | 20.9149 | 1.3305 | 0.21811 | 318.5731 | 26.58 | 51.62
2021-01-06 18:50 | 1.8456 | 1.0288 | 0.23425 | 1.8113 | 45.1397 | 35.4357 | 1.3305 | 0.15268 | 319.6931 | 26.52 | 51.84
2021-01-06 18:55 | 1.3745 | 0.84452 | 0.21122 | 1.5057 | 59.1038 | 65.3044 | 1.3303 | 0.12358 | 320.8637 | 26.45 | 51.74
2021-01-06 19:00 | 1.2726 | 0.69577 | 0.19239 | 1.2568 | 65.9224 | 45.9471 | 1.3303 | 0.11631 | 320.7109 | 26.41 | 51.78
2021-01-06 19:05 | 1.3489 | 0.61386 | 0.19028 | 1.1291 | 55.9392 | 32.8917 | 1.3301 | 0.12357 | 320.2446 | 26.38 | 51.58
2021-01-06 19:10 | 1.0941 | 0.53054 | 0.16515 | 0.97838 | 40.4269 | 20.3254 | 1.3299 | 0.087205 | 320.3523 | 26.34 | 51.12
2021-01-06 19:15 | 1.0685 | 0.53319 | 0.15886 | 0.97616 | 40.6554 | 28.9015 | 1.3224 | 0.065395 | 319.9499 | 26.26 | 50.97
2021-01-06 19:20 | 1.0939 | 0.4377 | 0.13586 | 0.80678 | 31.3618 | 29.2656 | 1.3223 | 0.079921 | 321.6118 | 26.22 | 50.87
2021-01-06 19:25 | 1.0049 | 0.37091 | 0.14004 | 0.70858 | 20.2102 | 14.9999 | 1.3224 | 0.087191 | 320.6394 | 26.12 | 51.32
2021-01-06 19:30 | 1.0941 | 0.51005 | 0.14633 | 0.93024 | 26.2882 | 9.5057 | 1.3225 | 0.10173 | 321.7119 | 26.08 | 51.75
2021-01-06 19:35 | 3.0786 | 0.50594 | 0.13169 | 0.90722 | 27.3152 | 13.5253 | 1.3298 | 0.18893 | 320.6378 | 26.1 | 51.59
2021-01-06 19:40 | 1.1319 | 0.40084 | 0.1442 | 0.75863 | 22.4658 | 11.5076 | 1.3222 | 0.079912 | 321.3068 | 26.04 | 51.11
2021-01-06 19:45 | 1.0935 | 0.31215 | 0.13999 | 0.61847 | 12.7766 | 5.5135 | 1.3219 | 0.058105 | 321.476 | 25.95 | 50.72
2021-01-06 19:50 | 1.5003 | 0.4239 | 0.13163 | 0.77931 | 11.1687 | 1.0884 | 1.3218 | 0.065364 | 322.6562 | 25.86 | 50.82
2021-01-06 19:55 | 1.1953 | 0.54388 | 0.1379 | 0.97158 | 19.5719 | 23.234 | 1.3219 | 0.072632 | 321.0393 | 25.86 | 51
2021-01-06 20:00 | 1.1065 | 0.50582 | 0.13584 | 0.91118 | 19.3623 | 3.3881 | 1.3222 | 0.065382 | 321.4611 | 25.9 | 51.5
2021-01-06 20:05 | 0.99207 | 0.40904 | 0.12122 | 0.74611 | 12.9732 | 8.2723 | 1.315 | 0.05812 | 320.9687 | 25.85 | 51.78
2021-01-06 20:10 | 0.97933 | 0.39131 | 0.1045 | 0.7043 | 13.034 | 6.6137 | 1.3222 | 0.065384 | 321.6039 | 25.76 | 52
2021-01-06 20:15 | 1.1067 | 0.4541 | 0.11496 | 0.81102 | 25.7567 | 27.9853 | 1.3224 | 0.079926 | 322.1389 | 25.71 | 52.63
2021-01-06 20:20 | 1.2341 | 0.69966 | 0.1338 | 1.2042 | 23.0634 | 25.5366 | 1.3226 | 0.079938 | 321.5262 | 25.74 | 52.98
2021-01-06 20:25 | 0.91608 | 0.63832 | 0.11499 | 1.0913 | 21.9044 | -1.0077 | 1.3154 | 0.072675 | 320.9963 | 25.72 | 53.22
2021-01-06 20:30 | 0.91589 | 0.45546 | 0.1296 | 0.82775 | 36.9613 | 17.0356 | 1.3152 | 0.065395 | 322.7119 | 25.67 | 52.78
2021-01-06 20:35 | 0.82656 | 0.38578 | 0.14418 | 0.73552 | 25.3817 | 29.1559 | 1.3147 | 0.058108 | 320.7365 | 25.63 | 51.86
2021-01-06 20:40 | 1.1063 | 0.38167 | 0.13372 | 0.71876 | 33.8031 | 37.516 | 1.3219 | 0.079894 | 322.3315 | 25.65 | 51.63
2021-01-06 20:45 | 1.6785 | 0.33125 | 0.11701 | 0.62477 | 28.1688 | 4.6287 | 1.3292 | 0.10169 | 321.7945 | 25.64 | 51.8
2021-01-06 20:50 | 1.3732 | 0.23852 | 0.10655 | 0.47426 | 14.2402 | 14.9522 | 1.329 | 0.0581 | 322.2235 | 25.58 | 51.63
2021-01-06 20:55 | 1.3477 | 0.20444 | 0.10028 | 0.41366 | 5.9807 | 7.0589 | 1.3217 | 0.050836 | 320.9078 | 25.52 | 51.7
2021-01-06 21:00 | 1.1825 | 0.22899 | 0.094021 | 0.44712 | 4.7809 | 6.2762 | 1.3291 | 0.043577 | 321.3012 | 25.43 | 52.25
2021-01-06 21:05 | 1.1444 | 0.21401 | 0.087757 | 0.4158 | 7.9448 |  | 1.3292 | 0.058106 | 321.5397 | 25.39 | 52.49
2021-01-06 21:10 | 0.95373 | 0.1963 | 0.075224 | 0.37821 | 5.9207 | 6.287 | 1.3292 | 0.065372 | 322.08 | 25.37 | 52.69
2021-01-06 21:15 | 0.89022 | 0.24403 | 0.089858 | 0.46601 | 14.0502 | 19.5543 | 1.3293 | 0.058113 | 321.3074 | 25.37 | 52.99
2021-01-06 21:20 | 0.78849 | 0.22359 | 0.083591 | 0.42631 | 10.4895 | 14.9661 | 1.3294 | 0.065379 | 322.9133 | 25.36 | 53.08
2021-01-06 21:25 | 1.3609 | 0.30542 | 0.07942 | 0.54758 | 15.1205 | -11.1216 | 1.3223 | 0.087182 | 321.8078 | 25.36 | 53.44
2021-01-06 21:30 | 1.8568 | 0.28495 | 0.075234 | 0.51201 | 13.3184 | 15.1498 | 1.3294 | 0.1017 | 320.7776 | 25.35 | 53.22
2021-01-06 21:35 | 2.0349 | 0.27813 | 0.083595 | 0.50993 | 3.0626 | 4.2428 | 1.3222 | 0.094441 | 322.097 | 25.31 | 53.33
2021-01-06 21:40 | 1.5264 | 0.30681 | 0.091967 | 0.56225 | 16.302 | 1.9233 | 1.3224 | 0.072657 | 321.3706 | 25.25 | 54
2021-01-06 21:45 | 1.6793 | 0.29321 | 0.1087 | 0.55606 | 19.2149 | -5.6179 | 1.3298 | 0.094467 | 322.3841 | 25.26 | 54.38
2021-01-06 21:50 | 1.6663 | 0.23045 | 0.075245 | 0.42639 | 19.1614 | 21.7155 | 1.3369 | 0.2325 | 321.9595 | 25.2 | 54.15
2021-01-06 21:55 | 1.3738 | 0.21272 | 0.083607 | 0.41176 | 24.8602 | 30.8539 | 1.3369 | 0.20344 | 322.0205 | 25.14 | 54.38
2021-01-06 22:00 | 1.2594 | 0.20592 | 0.075251 | 0.39298 | 20.384 | 3.8366 | 1.3297 | 0.15986 | 322.5891 | 25.09 | 54.73
2021-01-06 22:05 | 1.094 | 0.1541 | 0.071071 | 0.30937 | 18.6847 | 15.9267 | 1.3297 | 0.18166 | 322.1162 | 25.03 | 54.96
2021-01-06 22:10 | 2.0102 | 0.27277 | 0.089894 | 0.50801 | 32.9972 | 30.1677 | 1.3371 | 0.21075 | 322.6231 | 25.02 | 55.36
2021-01-06 22:15 | 1.8198 | 0.20873 | 0.077372 | 0.39731 | 22.245 | 18.753 | 1.3302 | 0.17446 | 323.0812 | 25.01 | 56.23
2021-01-06 22:20 | 1.1198 | 0.19644 | 0.066914 | 0.36803 | 13.2752 | 10.1295 | 1.3302 | 0.1163 | 322.1006 | 24.94 | 56.35
2021-01-06 22:25 | 0.89077 | 0.20326 | 0.073186 | 0.38684 | 20.5233 | 3.4816 | 1.3302 | 0.094493 | 322.1607 | 24.89 | 56.46
2021-01-06 22:30 | 0.92895 | 0.26328 | 0.079459 | 0.48303 | 17.6934 | -10.0174 | 1.3374 | 0.1163 | 320.6196 | 24.83 | 56.69
2021-01-06 22:35 | 0.91631 | 0.20055 | 0.081558 | 0.38897 | 6.0273 | 16.3511 | 1.3303 | 0.072694 | 322.76 | 24.8 | 57.08
2021-01-06 22:40 | 0.86543 | 0.18828 | 0.075286 | 0.36388 | 14.0403 | -7.3205 | 1.3303 | 0.058157 | 323.3396 | 24.75 | 57.34
2021-01-06 22:45 | 0.80178 | 0.24285 | 0.081559 | 0.45171 | 8.4404 | -1.517 | 1.3303 | 0.079965 | 322.8204 | 24.74 | 57.33
2021-01-06 22:50 | 0.66159 | 0.24414 | 0.091987 | 0.46621 | 0.71248 | 9.649 | 1.3299 | 0.065406 | 322.9185 | 24.74 | 56.37
2021-01-06 22:55 | 0.81406 | 0.20726 | 0.073154 | 0.39085 | 6.9603 | 5.383 | 1.3369 | 0.058124 | 323.0296 | 24.71 | 55.7
2021-01-06 23:00 | 0.63603 | 0.19637 | 0.062708 | 0.3637 | 1.8419 | -2.4729 | 1.3297 | 0.043596 | 321.96 | 24.69 | 55.98
2021-01-06 23:05 | 0.67423 | 0.21547 | 0.075253 | 0.40553 | -6.3301 | -14.3191 | 1.3297 | 0.036332 | 321.4515 | 24.65 | 56.28
2021-01-06 23:10 | 0.71251 | 0.18959 | 0.068993 | 0.3596 | 6.3922 | 16.3978 | 1.3227 | 0.065408 | 322.5124 | 24.61 | 56.93
2021-01-06 23:15 | 0.71267 | 0.23602 | 0.056462 | 0.41823 | 13.9785 | 10.802 | 1.323 | 0.050884 | 321.3486 | 24.63 | 57.58
2021-01-06 23:20 | 0.48361 | 0.14325 | 0.05019 | 0.26768 | -2.5861 | -8.3894 | 1.3303 | 0.029078 | 323.5195 | 24.59 | 57.83
2021-01-06 23:25 | 0.4581 | 0.12413 | 0.048092 | 0.23628 | -0.81439 | -5.375 | 1.3229 | 0.014537 | 321.7047 | 24.53 | 57.53
2021-01-06 23:30 | 0.45793 | 0.16091 | 0.050165 | 0.29681 | 4.2028 | 8.4158 | 1.3224 | 0.014532 | 322.4295 | 24.46 | 56.63
2021-01-06 23:35 | 0.45787 | 0.12544 | 0.056428 | 0.2487 | -3.724 | -6.5018 | 1.3222 | 0.043589 | 321.9053 | 24.49 | 56.1
2021-01-06 23:40 | 0.39426 | 0.12407 | 0.060605 | 0.25078 | -1.1599 | -4.6599 | 1.3221 | 0.021793 | 323.0571 | 24.43 | 56.13
2021-01-06 23:45 | 0.55972 | 0.24274 | 0.081522 | 0.45568 | 11.2554 | -5.1392 | 1.3224 | 0.029065 | 321.8267 | 24.51 | 56.6
2021-01-06 23:50 |  | 0.15273 | 0.064799 | 0.29891 | -2.015 | 9.9325 | 1.3152 | 0.014532 | 321.7931 | 24.54 | 56.51
2021-01-06 23:55 | 0.52161 | 0.13638 | 0.056444 | 0.26549 | 3.4604 | 6.3713 | 1.3226 | 0.036334 | 321.8272 | 24.48 | 57.02
2021-01-07 | 0.29257 | 0.13227 | 0.050166 | 0.25292 | 15.9261 | 7.6527 | 1.3224 | 0.021798 | 323.3136 | 24.43 | 56.84
2021-01-07 00:05 | 0.22876 | 0.094004 | 0.052208 | 0.1963 | -6.4255 | -15.2708 | 1.3212 | 0 | 323.2515 | 24.27 | 54.37
2021-01-07 00:10 | 0.27964 | 0.16351 | 0.058483 | 0.30703 | 1.5253 | -16.0158 | 1.3069 | 0.014521 | 321.7175 | 24.15 | 55.33
2021-01-07 00:15 | 0.29245 | 0.14857 | 0.048055 | 0.2758 | 13.0814 | 8.0156 | 1.3218 | 0.014526 | 323.454 | 24.13 | 56.43
2021-01-07 00:20 | 0.2671 | 0.10771 | 0.052249 | 0.21736 | -2.7574 | -9.4933 | 1.3222 | 0.007265 | 322.3009 | 24.12 | 57.41
2021-01-07 00:25 | 0.35622 | 0.11183 | 0.052262 | 0.22368 | -12.8137 | -11.745 | 1.3226 | 0.014534 | 323.3105 | 24.1 | 58.32
2021-01-07 00:30 | 0.43265 | 0.12413 | 0.058547 | 0.24882 | -0.091619 | -13.183 | 1.3229 | 0.0072684 | 322.694 | 24.11 | 59
2021-01-07 00:35 | 0.24182 | 0.05321 | 0.043918 | 0.12548 | -1.8429 | 1.9549 | 1.3158 | 0.01454 | 320.9854 | 24.15 | 59.47
2021-01-07 00:40 | 0.20367 | 0.028656 | 0.041833 | 0.085758 | -13.605 | -5.0917 | 1.3233 | 0.0072709 | 321.5566 | 24.07 | 60.27
2021-01-07 00:45 | 0.22917 | 0.027297 | 0.03975 | 0.081592 | -2.9233 | -7.0382 | 1.3163 | 0 | 322.0996 | 24 | 61.22
2021-01-07 00:50 | 0.17828 | 0.025938 | 0.039758 | 0.079516 | 5.3179 | -16.2798 | 1.3166 | 0 | 322.088 | 23.95 | 62.08
2021-01-07 00:55 | 0.17832 | 0.025944 | 0.037674 | 0.077442 | 3.0366 | 4.8606 | 1.3169 | 0.014551 | 322.0256 | 23.94 | 62.87
2021-01-07 01:00 | 0.19111 | 0.028682 | 0.050246 | 0.094211 | 8.0318 | 22.2608 | 1.3245 | 0 | 322.4631 | 23.95 | 63.72
2021-01-07 01:05 |  |  |  |  | 11.9086 | 17.9648 |  |  | 322.3139 | 24 | 64.5
2021-01-07 01:10 |  |  |  |  | 7.3824 | -7.3212 |  |  | 322.3149 | 23.97 | 64.94
2021-01-07 01:15 |  |  |  |  | 0.91762 | -7.29 |  |  | 321.8408 | 23.94 | 64.77
2021-01-07 01:20 |  |  |  |  | 8.4597 | 9.3668 |  |  | 323.0719 | 23.89 | 63.86
2021-01-07 01:25 |  |  |  |  | 13.4589 | 13.2245 |  |  | 322.1398 | 23.88 | 62.59
2021-01-07 01:30 |  |  |  |  | 6.2547 | 4.1053 |  |  | 322.7274 | 23.88 | 62.05
2021-01-07 01:35 |  |  |  |  | 9.5238 | -10.0127 |  |  | 321.1805 | 23.85 | 61.89
2021-01-07 01:40 |  |  |  |  | 10.3086 | -2.8725 |  |  | 323.3187 | 23.84 | 62.07
2021-01-07 01:45 |  |  |  |  | -1.8745 | 20.9352 |  |  | 322.7041 | 23.88 | 62.29
2021-01-07 01:50 |  |  |  |  | 5.6604 | 20.6053 |  |  | 322.4005 | 23.87 | 60.05
2021-01-07 01:55 |  |  |  |  | 20.3007 | -8.4315 |  |  | 324.2981 | 23.89 | 56.77
2021-01-07 02:00 |  |  |  |  | 1.9421 | 5.0028 |  |  | 322.2724 | 23.85 | 56.13
2021-01-07 02:05 |  |  |  |  | 1.708 | 9.8413 |  |  | 322.8945 | 23.82 | 55.68
2021-01-07 02:10 | 0.26685 | 0.055851 | 0.041761 | 0.12737 | 17.6172 | -9.6574 |  |  | 322.3647 | 23.84 | 55.32
2021-01-07 02:15 | 0.24144 | 0.05449 | 0.050115 | 0.13364 | 7.4517 | -5.6523 |  |  | 322.9119 | 23.82 | 55.5
2021-01-07 02:20 | 0.22871 | 0.079 | 0.043845 | 0.16494 | 10.3579 | 3.4459 |  |  | 322.9432 | 23.83 | 55.03
2021-01-07 02:25 | 0.22866 | 0.058558 | 0.050099 | 0.13777 | 10.0206 | 14.6955 |  |  | 322.992 | 23.84 | 54.38
2021-01-07 02:30 | 0.22866 | 0.07626 | 0.04801 | 0.1649 | 8.2317 | -9.1056 |  |  | 322.9804 | 23.86 | 54.21
2021-01-07 02:35 | 0.20323 | 0.084421 | 0.064702 | 0.19411 | 0.40646 | -3.3025 |  |  | 322.9285 | 23.94 | 53.59
2021-01-07 02:40 | 0.17776 | 0.093918 | 0.05216 | 0.19612 | 3.8599 | -6.1657 |  |  | 324.1214 | 23.94 | 52.36
2021-01-07 02:45 | 0.2412 | 0.073486 | 0.047977 | 0.16062 | 3.9911 | 0.2742 |  |  | 323.695 | 23.9 | 51.8
2021-01-07 02:50 | 0.31733 | 0.13063 | 0.060486 | 0.26072 | -1.7567 | 6.8746 |  |  | 323.7081 | 23.92 | 51.38
2021-01-07 02:55 | 0.30462 | 0.13606 | 0.047969 | 0.25653 | 6.2954 | 20.0132 |  |  | 324.2334 | 23.95 | 51.07
2021-01-07 03:00 | 0.29196 | 0.16874 | 0.068833 | 0.32748 | 14.0546 | -1.5436 |  |  | 324.612 | 24.06 | 51.12
2021-01-07 03:05 | 0.39349 | 0.14287 | 0.0584 | 0.2774 | 7.5245 | -1.513 |  |  | 324.115 | 24.04 | 51
2021-01-07 03:10 | 0.44429 | 0.17146 | 0.056318 | 0.32122 | 11.3433 | 7.1695 |  |  | 323.0213 | 24.04 | 51.21
2021-01-07 03:15 | 0.52051 | 0.21639 | 0.062583 | 0.39427 | 15.9149 | 7.7899 |  |  | 322.4038 | 24.08 | 51.47
2021-01-07 03:20 | 0.57129 | 0.31846 | 0.064669 | 0.5549 | 8.6125 | -6.4391 |  |  | 322.8209 | 24.19 | 51.13
2021-01-07 03:25 | 0.43166 | 0.21504 | 0.07093 | 0.40055 | 9.3847 | 16.2201 |  |  | 324.3968 | 24.21 | 51.18
2021-01-07 03:30 | 0.40641 | 0.17018 | 0.077216 | 0.33599 | 20.9301 | 16.0836 |  |  | 323.2647 | 24.16 | 52.49
2021-01-07 03:35 | 0.36841 | 0.17704 | 0.073061 | 0.34443 | 14.4415 | 5.9351 |  |  | 323.5235 | 24.14 | 53.47
2021-01-07 03:40 | 0.36845 | 0.22064 | 0.077246 | 0.41546 | 12.8476 | -0.71149 |  |  | 324.0075 | 24.15 | 53.86
2021-01-07 03:45 | 0.62249 | 0.28327 | 0.093937 | 0.53022 | 24.0865 | 9.5939 |  |  | 324.0107 | 24.18 | 53.4
2021-01-07 03:50 | 0.57162 | 0.52699 | 0.12106 | 0.92885 | 13.9831 | 4.4408 |  |  | 322.849 | 24.29 | 52.74
2021-01-07 03:55 | 0.53344 | 0.4425 | 0.10852 | 0.7868 | 14.2046 | 11.4613 |  |  | 323.3871 | 24.33 | 52.16
2021-01-07 04:00 | 0.57156 | 0.51468 | 0.085571 | 0.87449 | 19.2349 | 9.775 |  |  | 323.4071 | 24.3 | 52.38
2021-01-07 04:05 | 0.73648 | 0.48187 | 0.11267 | 0.8513 | 11.0522 | 14.1098 |  |  | 324.0221 | 24.31 | 51.45
2021-01-07 04:10 | 0.49514 | 0.31711 | 0.098051 | 0.58413 | 9.72 | 16.8195 |  |  | 323.6011 | 24.25 | 51.13
2021-01-07 04:15 | 0.45706 | 0.43009 | 0.11892 | 0.78025 | 22.5179 | 20.4256 |  |  | 323.6589 | 24.19 | 51.39
2021-01-07 04:20 | 0.67297 | 0.4206 | 0.12936 | 0.77408 | 16.0091 | 8.1468 |  |  | 324.095 | 24.25 | 51.56
2021-01-07 04:25 | 0.68561 | 0.48045 | 0.1523 | 0.88876 | 24.1131 | 10.9494 |  |  | 323.9814 | 24.38 | 50.88
2021-01-07 04:30 | 0.58403 | 0.57028 | 0.16899 | 1.0431 |  |  |  |  | 411.2648 | 24.49 | 50.52
2021-01-07 04:35 | 0.64751 | 0.62744 | 0.15647 | 1.1182 |  |  |  |  | 471.7183 | 24.58 | 50.21
2021-01-07 04:40 | 0.81253 | 0.74991 | 0.20862 | 1.3581 |  | 11.2332 |  |  | 472.2692 | 24.58 | 50.11
2021-01-07 04:45 | 0.90147 | 1.0426 | 0.1836 | 1.7817 | 16.5261 | 20.2031 |  |  | 471.6343 | 24.62 | 50.23
2021-01-07 04:50 | 1.2315 | 1.6482 | 0.28789 | 2.8143 | 43.2572 | 59.0712 |  |  | 469.9186 | 24.71 | 49.73
2021-01-07 04:55 | 1.333 | 1.7611 | 0.30874 | 3.0082 | 58.8763 | 52.559 |  |  | 470.2963 | 24.82 | 49.3
2021-01-07 05:00 | 1.6115 | 1.6446 | 0.32736 | 2.8483 | 64.2994 | 39.4892 |  |  | 472.034 | 24.88 | 47.62
2021-01-07 05:05 | 1.8136 | 1.2413 | 0.3001 | 2.2028 | 66.0417 | 55.2563 |  |  | 471.2066 | 24.88 | 45.99
2021-01-07 05:10 | 1.5344 | 1.6531 | 0.33965 | 2.8735 | 61.5795 | 38.6318 |  |  | 471.8196 | 24.87 | 45.61
2021-01-07 05:15 | 1.8767 | 2.2524 | 0.46256 | 3.913 | 65.2269 | 68.5339 |  |  | 470.6237 | 24.97 | 45.11
2021-01-07 05:20 | 2.5233 | 2.4427 | 0.48131 | 4.2234 | 84.4291 | 78.4238 |  |  | 469.3824 | 25.08 | 44.79
2021-01-07 05:25 | 3.4992 | 2.5266 | 0.42916 | 4.302 | 88.8502 | 70.8469 |  |  | 469.6977 | 25.26 | 43.9
2021-01-07 05:30 | 3.6641 | 2.8786 | 0.46875 | 4.8833 | 107.5132 | 76.3141 |  |  | 467.2558 | 25.45 | 43.42
2021-01-07 05:35 | 3.5369 | 3.1284 | 0.61035 | 5.4057 | 101.7626 | 96.8945 |  |  | 467.6483 | 25.57 | 42.82
2021-01-07 05:40 | 3.917 | 2.9773 | 0.71029 | 5.274 | 104.2695 | 85.4378 |  |  | 468.5986 | 25.67 | 42.33
2021-01-07 05:45 | 3.9165 | 3.0912 | 0.66231 | 5.4005 | 130.1054 | 118.3532 |  |  | 467.4208 | 25.77 | 41.77
2021-01-07 05:50 | 5.1707 | 3.3 | 0.67889 | 5.7372 | 140.2069 | 117.7398 |  |  | 468.929 | 25.87 | 41.14
2021-01-07 05:55 | 4.3346 | 2.6032 | 0.61021 | 4.5984 | 119.5432 | 74.6359 |  |  | 468.2497 | 25.94 | 41.19
2021-01-07 06:00 | 3.5737 | 2.8189 | 0.56224 | 4.8831 | 94.2336 | 77.3131 |  |  | 467.1772 | 25.98 | 40.72
2021-01-07 06:05 | 5.5255 | 2.9834 | 0.59766 | 5.1728 | 115.5996 | 118.2153 |  |  | 467.5819 | 26.05 | 40.68
2021-01-07 06:10 | 4.3978 | 3.1561 | 0.65392 | 5.4917 | 154.671 | 148.841 |  |  | 467.9994 | 26.11 | 40.68
2021-01-07 06:15 | 1.8756 | 2.8231 | 0.57059 | 4.8958 | 142.1512 | 98.2619 |  |  | 467.376 | 26.14 | 40.48
2021-01-07 06:20 | 1.7998 | 2.3561 | 0.50194 | 4.1113 | 116.5684 | 74.5588 |  |  | 469.4787 | 26.12 | 40.95
2021-01-07 06:25 | 1.7364 | 1.8057 | 0.40404 | 3.174 | 93.7408 | 55.8288 |  |  | 468.4695 | 26.09 | 40.94
2021-01-07 06:30 | 2.3829 | 1.9227 | 0.51862 | 3.4658 | 81.9834 | 63.5891 |  |  | 469.0098 | 26.07 | 41.15
2021-01-07 06:35 | 3.0547 | 2.2692 | 0.51029 | 3.9865 | 80.5338 | 50.9851 |  |  | 468.4096 | 26.11 | 41.07
2021-01-07 06:40 | 3.7268 | 2.3604 | 0.50199 | 4.1201 | 87.2524 | 67.3052 |  |  | 468.7568 | 26.21 | 41.02
2021-01-07 06:45 | 3.9556 | 2.5401 | 0.46874 | 4.3624 | 120.6348 | 126.3145 |  |  | 468.0714 | 26.26 | 41.35
2021-01-07 06:50 | 3.6263 | 3.0691 | 0.4667 | 5.1712 | 120.3626 | 94.2431 |  |  | 468.4343 | 26.34 | 41.44
2021-01-07 06:55 | 3.3855 | 2.7036 | 0.41254 | 4.5567 | 119.5134 | 70.3468 |  |  | 467.3237 | 26.36 | 41.46
2021-01-07 07:00 | 4.2224 | 2.4957 | 0.47506 | 4.3005 | 100.6285 | 74.0411 |  |  | 466.1497 | 26.42 | 41.39
2021-01-07 07:05 | 5.5546 | 3.0099 | 0.49595 | 5.1096 | 92.0483 | 73.3911 |  |  | 469.1995 | 26.48 | 41.61
2021-01-07 07:10 | 5.2506 | 3.21 | 0.54184 | 5.4643 | 91.3356 | 69.7345 |  |  | 468.0928 | 26.48 | 41.85
2021-01-07 07:15 | 4.1984 | 2.9805 | 0.53357 | 5.1022 | 97.2718 | 74.6637 |  |  | 466.4083 | 26.5 | 42.12
2021-01-07 07:20 | 3.2604 | 2.6587 | 0.5274 | 4.6028 | 94.02 | 69.8249 |  |  | 466.2218 | 26.57 | 42.42
2021-01-07 07:25 | 4.5668 | 2.9183 | 0.49403 | 4.9674 | 85.9474 | 61.4185 |  |  | 467.8452 | 26.57 | 42.28
2021-01-07 07:30 | 4.5662 | 2.7534 | 0.41476 | 4.6353 | 92.6843 | 83.7345 |  |  | 468.3079 | 26.61 | 41.86
2021-01-07 07:35 | 3.4118 | 2.291 | 0.38764 | 3.8972 | 90.6791 | 70.7615 |  |  | 467.2563 | 26.62 | 41.64
2021-01-07 07:40 | 3.0817 | 1.8911 | 0.4022 | 3.3009 | 97.9564 | 71.5371 |  |  | 468.9275 | 26.6 | 41.46
2021-01-07 07:45 | 3.6399 | 2.3045 | 0.4564 | 3.9909 | 105.6512 | 92.4613 |  |  | 466.7714 | 26.6 | 41.58
2021-01-07 07:50 | 3.1319 | 2.1246 | 0.41255 | 3.6712 | 102.5959 | 72.4988 |  |  | 469.5407 | 26.6 | 40.98
2021-01-07 07:55 | 2.8528 | 1.8037 | 0.40002 | 3.1626 | 83.9759 | 44.9751 |  |  | 470.6732 | 26.58 | 40.83
2021-01-07 08:00 | 2.916 | 1.6567 | 0.38332 | 2.9249 | 63.5427 | 38.5414 |  |  | 471.8716 | 26.52 | 40.76
2021-01-07 08:05 | 2.4976 | 1.809 | 0.35833 | 3.1312 | 66.2419 | 44.0396 |  |  | 470.8716 | 26.47 | 40.94
2021-01-07 08:10 | 3.2459 | 1.8839 | 0.37294 | 3.2607 | 63.0321 | 43.2015 |  |  | 470.8781 | 26.44 | 41.26
2021-01-07 08:15 | 4.793 | 1.7467 | 0.34587 | 3.0211 | 64.3425 | 52.5452 |  |  | 471.462 | 26.4 | 41.44
2021-01-07 08:20 | 3.9436 | 1.8704 | 0.42298 | 3.29 | 60.8046 | 48.5504 |  |  | 470.9095 | 26.4 | 41.55
2021-01-07 08:25 | 2.7651 | 1.9226 | 0.43351 | 3.3806 | 69.0197 | 48.0764 |  |  | 469.667 | 26.43 | 42.25
2021-01-07 08:30 | 2.4102 | 1.708 | 0.41272 | 3.0308 | 74.0015 | 72.9055 |  |  | 470.1078 | 26.45 | 42.58
2021-01-07 08:35 | 2.6012 | 1.956 | 0.42534 | 3.4235 | 93.5908 | 63.8387 |  |  | 469.4094 | 26.48 | 43.22
2021-01-07 08:40 | 2.8577 | 2.4481 | 0.47167 | 4.2242 | 87.2819 | 59.3598 |  |  | 469.464 | 26.49 | 46.02
2021-01-07 08:45 | 2.8467 | 2.4536 | 0.4448 | 4.2057 | 84.3943 | 83.6115 |  |  | 467.5615 | 26.51 | 47.62
2021-01-07 08:50 | 2.1731 | 1.8378 | 0.38424 | 3.2013 | 74.7763 | 43.2798 |  |  | 468.1898 | 26.45 | 47.78
2021-01-07 08:55 | 2.4154 | 2.1178 | 0.39272 | 3.6389 | 73.5296 | 46.05 |  |  | 467.6127 | 26.38 | 48.92
2021-01-07 09:00 | 2.8879 | 2.4685 | 0.462 | 4.2437 | 62.0433 | 32.7315 |  |  | 467.2928 | 26.36 | 51.14
2021-01-07 09:05 | 3.1922 | 1.6974 | 0.43468 | 3.0344 | 60.4557 | 73.6925 |  |  | 468.4836 | 26.38 | 50.12
2021-01-07 09:10 | 2.696 | 1.4328 | 0.38241 | 2.5808 | 56.0165 | 34.0514 |  |  | 469.0754 | 26.36 | 50.01
2021-01-07 09:15 | 1.9461 | 1.6008 | 0.39084 | 2.8446 | 55.253 | 44.5789 |  |  | 470.0269 | 26.38 | 50.46
2021-01-07 09:20 | 2.2514 | 1.8612 | 0.38875 | 3.2438 | 51.6209 | 34.4445 |  |  | 469.0187 | 26.34 | 50.61
2021-01-07 09:25 | 2.62 | 1.9115 | 0.37618 | 3.3062 | 49.8768 | 43.2632 |  |  | 467.521 | 26.3 | 50.49
2021-01-07 09:30 | 2.4669 | 1.5812 | 0.34267 | 2.7664 | 44.1491 | 36.1941 |  |  | 470.8675 | 26.27 | 49.96
2021-01-07 09:35 | 2.5555 | 1.6192 | 0.35307 | 2.835 | 46.8382 | 47.9163 |  |  | 468.7852 | 26.28 | 49.52
2021-01-07 09:40 | 3.2935 | 1.948 | 0.40536 | 3.3913 | 43.3771 | -17.1616 |  |  | 496.3512 | 26.33 | 49.86
2021-01-07 09:45 | 3.6357 | 2.1027 | 0.36138 | 3.5845 | 130.2149 | 106.9463 |  |  | 469.2685 | 26.35 | 48.95
2021-01-07 09:50 | 3.6103 | 1.6435 | 0.33631 | 2.8555 | 109.9067 | 97.7536 |  |  | 467.6021 | 26.39 | 48.86
2021-01-07 09:55 | 3.5723 | 1.754 | 0.41153 | 3.1022 | 96.7508 | 57.4626 |  |  | 467.5826 | 26.39 | 48.98
2021-01-07 10:00 | 4.0682 | 1.8848 | 0.38855 | 3.2776 | 71.1317 | 37.9966 |  |  | 493.0913 | 26.44 | 48.84
2021-01-07 10:05 | 3.2298 | 1.5798 | 0.31968 | 2.7413 | 126.4638 | 103.7081 |  |  | 468.4442 | 26.46 | 49.36
2021-01-07 10:10 | 2.4927 | 1.5106 | 0.33436 | 2.6498 |  |  |  |  | 566.9766 | 26.44 | 49.91
2021-01-07 10:15 | 1.8695 | 1.1984 | 0.29675 | 2.1337 |  |  |  |  | 607.0067 | 26.41 | 49.98
2021-01-07 10:20 | 2.213 | 1.2748 | 0.3302 | 2.2842 | 102.4782 | 31.4496 |  |  | 607.0822 | 26.36 | 50.25
2021-01-07 10:25 | 2.4166 | 1.3444 | 0.31976 | 2.3804 | 191.8792 | 49.9997 |  |  | 607.1601 | 26.31 | 50.51
2021-01-07 10:30 | 1.9337 | 1.0365 | 0.30938 | 1.8981 | 206.7928 | 61.7661 |  |  | 607.5928 | 26.29 | 51.24
2021-01-07 10:35 | 1.9218 | 0.92778 | 0.28861 | 1.7128 | 210.2674 | 59.8189 |  |  | 608.4629 | 26.25 | 52.68
2021-01-07 10:40 | 2.1146 | 1.2222 | 0.31188 | 2.1853 | 208.2556 | 71.9152 |  |  | 606.9208 | 26.23 | 55.21
2021-01-07 10:45 | 2.3953 | 1.3358 | 0.29939 | 2.3469 | 188.9142 | 54.1546 |  |  | 605.2524 | 26.2 | 55.94
2021-01-07 10:50 | 2.9934 | 1.3382 | 0.32861 | 2.3777 | 175.027 | 43.6039 |  |  | 604.8764 | 26.2 | 55.19
2021-01-07 10:55 | 2.3168 | 1.2213 | 0.29702 | 2.1691 | 161.3498 | 57.782 |  |  | 607.9097 | 26.21 | 53.29
2021-01-07 11:00 | 2.4691 | 1.3957 | 0.35971 | 2.4991 | 192.924 | 259.5127 |  |  | 560.0441 | 26.22 | 52.72
2021-01-07 11:05 | 2.6726 | 1.4694 | 0.34715 | 2.5973 | 497.1858 | 474.6443 |  |  | 468.7971 | 26.27 | 52.5
2021-01-07 11:10 | 3.156 | 1.5593 | 0.41823 | 2.8105 | 332.6373 | 112.4164 |  |  | 469.2773 | 26.32 | 52.19
2021-01-07 11:15 | 2.5587 | 1.179 | 0.36606 | 2.1733 | 173.2882 | 53.7707 |  |  | 468.9964 | 26.41 | 52.77
2021-01-07 11:20 | 2.4064 | 1.3881 | 0.295 | 2.4228 | 106.9532 | 34.989 |  |  | 468.4257 | 26.37 | 53.51
2021-01-07 11:25 | 2.9019 | 1.6687 | 0.38691 | 2.9447 | 83.9407 | 49.7189 |  |  | 467.6208 | 26.32 | 52.54
2021-01-07 11:30 | 3.0787 | 1.406 | 0.35955 | 2.5148 | 44.4344 | 32.2725 |  |  | 470.0471 | 26.27 | 51.37
2021-01-07 11:35 | 3.6674 | 1.6272 | 0.39129 | 2.8855 | 29.3087 | 2.5672 |  |  | 491.9628 | 26.28 | 54.14
2021-01-07 11:40 | 4.5446 | 1.8163 | 0.3807 | 3.1628 | 76.3794 | 79.6994 |  |  | 468.663 | 26.28 | 53.2
2021-01-07 11:45 | 3.8549 | 1.4839 | 0.32613 | 2.6006 | 57.4036 | 45.4343 |  |  | 470.5862 | 26.25 | 51.59
2021-01-07 11:50 | 3.666 | 1.3932 | 0.34094 | 2.4765 | 42.3219 | 38.1874 |  |  | 471.4987 | 26.19 | 53.31
2021-01-07 11:55 | 3.2599 | 1.2614 | 0.35781 | 2.2892 | 42.3488 | 27.842 |  |  | 469.2777 | 26.17 | 54.47
2021-01-07 12:00 | 2.4462 | 1.1459 | 0.31403 | 2.0705 | 37.2126 | 30.2614 |  |  | 470.1393 | 26.15 | 55.99
2021-01-07 12:05 | 2.4593 | 1.2991 | 0.31617 | 2.3074 | 28.2172 | 35.1594 |  |  | 468.4663 | 26.15 | 56.46
2021-01-07 12:10 | 2.4215 | 1.3307 | 0.31622 | 2.3539 | 20.6768 | 27.406 |  |  | 469.5365 | 26.1 | 57.08
2021-01-07 12:15 | 2.6132 | 1.51 | 0.32886 | 2.6435 | 25.3013 | 33.1232 |  |  | 470.4916 | 26.1 | 57.76
2021-01-07 12:20 | 2.9446 | 1.3242 | 0.34562 | 2.3753 | 38.5072 | 45.2684 |  |  | 468.9177 | 26.09 | 57.75
2021-01-07 12:25 | 2.8049 | 1.3312 | 0.36662 | 2.405 | 40.8387 | 28.4157 |  |  | 468.2657 | 26.12 | 58.1
2021-01-07 12:30 | 2.257 | 1.4381 | 0.39392 | 2.5982 | 41.0703 | 42.6821 |  |  | 469.7798 | 26.12 | 58.61
2021-01-07 12:35 | 1.8117 | 1.3417 | 0.29979 | 2.3564 | 30.1608 | 21.5259 |  |  | 469.013 | 26.11 | 60.2
2021-01-07 12:40 | 2.1834 | 1.1374 | 0.28534 | 2.0288 | 30.4188 | 47.5485 |  |  | 468.5764 | 26.16 | 62.24
2021-01-07 12:45 | 2.2994 | 1.1681 | 0.31486 | 2.1054 | 43.8616 | 46.2529 |  |  | 468.8372 | 26.19 | 63.51
2021-01-07 12:50 | 2.6038 | 1.4025 | 0.35865 | 2.5084 | 47.4715 | 76.7059 |  |  | 467.1222 | 26.17 | 61.24
2021-01-07 12:55 | 3.0092 | 1.453 | 0.35828 | 2.5834 | 52.4819 | 40.8227 |  |  | 469.7644 | 26.15 | 58.31
2021-01-07 13:00 | 3.1469 | 1.2907 | 0.3245 | 2.305 | 40.7087 | 49.2601 |  |  | 471.2822 | 26.1 | 56.16
2021-01-07 13:05 | 3.3867 | 1.0237 | 0.29499 | 1.8641 | 44.6947 | 6.5392 |  |  | 471.6277 | 26.08 | 54.28
2021-01-07 13:10 | 3.3108 | 1.4852 | 0.31596 | 2.5926 | 41.3398 | 13.4268 |  |  | 470.0355 | 26.03 | 54.89
2021-01-07 13:15 | 3.2355 | 1.4652 | 0.29932 | 2.5453 | 37.4197 | 31.7945 |  |  | 469.412 | 25.99 | 55.98
2021-01-07 13:20 | 2.7137 | 1.0639 | 0.25331 | 1.8841 | 45.9258 | 36.2637 |  |  | 472.0495 | 25.96 | 56.54
2021-01-07 13:25 | 2.8045 | 0.93199 | 0.21366 | 1.6422 | 40.5987 | 15.0116 |  |  | 470.2387 | 25.92 | 58.4
2021-01-07 13:30 | 2.845 | 0.9081 | 0.24947 | 1.6414 | 38.4364 | 44.3662 |  |  | 470.4158 | 25.91 | 60.76
2021-01-07 13:35 | 2.7068 | 0.99232 | 0.23498 | 1.756 | 50.1929 | 53.6045 |  |  | 469.9796 | 25.95 | 62.95
2021-01-07 13:40 | 3.2816 | 1.1019 | 0.20562 | 1.8926 | 46.2537 | 45.3957 |  |  | 468.8964 | 25.94 | 63.21
2021-01-07 13:45 | 3.9175 | 1.2229 | 0.27049 | 2.145 | 53.7373 | 52.7369 |  |  | 469.1677 | 25.96 | 61.24
2021-01-07 13:50 | 4.8845 | 1.2304 | 0.28291 | 2.169 | 49.4724 | 42.8917 |  |  | 470.9083 | 26.04 | 59.27
2021-01-07 13:55 | 4.6111 | 1.1798 | 0.22605 | 2.0345 | 41.5047 | 34.8913 |  |  | 470.3996 | 26.05 | 55.68
2021-01-07 14:00 | 3.6508 | 1.4537 | 0.24247 | 2.4707 | 38.5489 | 34.4375 |  |  | 471.5946 | 26.03 | 51.82
2021-01-07 14:05 | 3.421 | 1.7982 | 0.31764 | 3.074 | 56.4349 | 56.5875 |  |  | 470.555 | 26.09 | 50.88
2021-01-07 14:10 | 3.1786 | 1.8918 | 0.39278 | 3.2926 | 61.3447 | 58.3441 |  |  | 470.5705 | 26.15 | 50.02
2021-01-07 14:15 | 2.9884 | 1.5922 | 0.46598 | 2.9045 | 55.0879 | 37.4577 |  |  | 470.4005 | 26.21 | 50.31
2021-01-07 14:20 | 2.6323 | 1.2814 | 0.42627 | 2.3905 | 49.1159 | 58.9228 |  |  | 470.9527 | 26.2 | 50.32
2021-01-07 14:25 | 3.4972 | 1.291 | 0.37196 | 2.353 | 59.7698 | 33.7153 |  |  | 470.3983 | 26.2 | 50.45
2021-01-07 14:30 | 3.305 | 1.3395 | 0.4282 | 2.4815 | 55.4429 | 40.311 |  |  | 469.5148 | 26.21 | 49.19
2021-01-07 14:35 | 2.7327 | 1.4511 | 0.4574 | 2.6838 | 64.1623 | 55.0718 |  |  | 469.9973 | 26.27 | 48.75
2021-01-07 14:40 | 2.3772 | 1.4541 | 0.38226 | 2.6111 | 68.8493 | 40.8418 |  |  | 469.8221 | 26.34 | 48.95
2021-01-07 14:45 | 2.8354 | 1.6411 | 0.41995 | 2.9355 | 65.6093 | 43.9226 |  |  | 469.6884 | 26.36 | 49.52
2021-01-07 14:50 | 2.6702 | 1.6125 | 0.41161 | 2.8854 | 72.4468 | 61.125 |  |  | 468.5315 | 26.41 | 49.45
2021-01-07 14:55 | 2.5939 | 1.5416 | 0.40951 | 2.7726 | 89.7785 | 68.1324 |  |  | 470.061 | 26.46 | 49.25
2021-01-07 15:00 | 3.0892 | 1.4528 | 0.38228 | 2.6091 | 69.5241 | 33.7043 |  |  | 470.1896 | 26.43 | 48.84
2021-01-07 15:05 | 3.5214 | 1.4745 | 0.3781 | 2.6383 | 63.2479 | 69.0856 |  |  | 469.6647 | 26.43 | 48.79
2021-01-07 15:10 | 3.5724 | 1.7608 | 0.39065 | 3.0897 | 76.6346 | 49.4184 |  |  | 468.5188 | 26.47 | 48.78
2021-01-07 15:15 | 3.2278 | 1.6715 | 0.35707 | 2.9213 | 77.4769 | 58.1814 |  |  | 469.138 | 26.54 | 47.39
2021-01-07 15:20 | 3.3545 | 1.764 | 0.38835 | 3.0922 | 81.7075 | 65.9921 |  |  | 468.6083 | 26.57 | 47
2021-01-07 15:25 | 3.3163 | 1.7476 | 0.37373 | 3.0525 | 64.863 | 33.3921 |  |  | 469.6338 | 26.6 | 46.88
2021-01-07 15:30 | 2.3756 | 1.5525 | 0.29642 | 2.6761 | 65.3264 | 38.7914 |  |  | 470.2542 | 26.61 | 46.23
2021-01-07 15:35 | 3.0613 | 1.6068 | 0.31935 | 2.7823 | 74.8941 | 52.8222 |  |  | 469.2073 | 26.62 | 45.99
2021-01-07 15:40 | 3.1883 | 1.4624 | 0.34231 | 2.5819 | 90.6025 | 36.6231 |  |  | 469.7673 | 26.61 | 45.95
2021-01-07 15:45 | 3.9111 | 1.6022 | 0.30047 | 2.7585 | 73.9048 | 46.4051 |  |  | 471.54 | 26.59 | 45.15
2021-01-07 15:50 | 3.7968 | 1.8323 | 0.3422 | 3.1508 | 60.9828 | 45.44 |  |  | 468.3245 | 26.6 | 45.12
2021-01-07 15:55 | 3.977 | 1.7408 | 0.35076 | 3.0191 | 58.692 | 36.685 |  |  | 468.5116 | 26.64 | 46.73
2021-01-07 16:00 | 3.3778 | 1.7996 | 0.38185 | 3.1403 | 64.5076 | 74.4935 |  |  | 469.8174 | 26.67 | 44.92
2021-01-07 16:05 | 2.8818 | 1.6726 | 0.30248 | 2.8663 | 78.0306 | 45.429 |  |  | 470.9168 | 26.72 | 44.12
2021-01-07 16:10 | 3.5306 | 1.714 | 0.33181 | 2.9592 | 74.0762 | 59.1817 |  |  | 469.2093 | 26.68 | 45.25
2021-01-07 16:15 | 4.7159 | 1.7537 | 0.38641 | 3.0746 | 66.3427 | 52.1467 |  |  | 469.3394 | 26.67 | 47.8
2021-01-07 16:20 | 4.6544 | 1.5964 | 0.34479 | 2.7917 | 66.626 | 51.4065 |  |  | 469.0872 | 26.7 | 48.95
2021-01-07 16:25 | 3.7784 | 1.7934 | 0.38255 | 3.1315 | 83.6178 | 70.2853 |  |  | 467.8554 | 26.69 | 50.08
2021-01-07 16:30 | 3.1526 | 1.8615 | 0.35929 | 3.2106 | 78.1037 | 53.7166 |  |  | 469.885 | 26.64 | 48.09
2021-01-07 16:35 | 3.7617 | 1.6934 | 0.32785 | 2.9256 | 76.6464 | 48.9423 |  |  | 468.4137 | 26.65 | 47.2
2021-01-07 16:40 | 3.9902 | 1.8077 | 0.37586 | 3.1468 | 66.8222 | 56.1579 |  |  | 469.5027 | 26.65 | 47.06
2021-01-07 16:45 | 3.5192 | 1.5962 | 0.286 | 2.7327 | 59.3561 | 57.5063 |  |  | 469.6154 | 26.65 | 46.38
2021-01-07 16:50 | 3.3285 | 1.6778 | 0.30061 | 2.8725 | 63.358 | 64.6183 |  |  | 469.7131 | 26.6 | 46.4
2021-01-07 16:55 | 4.6371 | 1.6792 | 0.3528 | 2.9268 | 68.3599 | 52.6877 |  |  | 470.7847 | 26.59 | 46.49
2021-01-07 17:00 | 4.4469 | 1.5908 | 0.35283 | 2.7913 | 61.9211 | 54.8874 |  |  | 471.2644 | 26.6 | 46.69
2021-01-07 17:05 | 3.8489 | 1.374 | 0.32353 | 2.4275 | 61.4914 | 56.5323 |  |  | 469.8268 | 26.56 | 46.2
2021-01-07 17:10 | 2.9342 | 1.2064 | 0.25464 | 2.1039 | 61.6211 | 43.6551 |  |  | 470.4255 | 26.53 | 46.17
2021-01-07 17:15 | 2.7826 | 1.2259 | 0.23175 | 2.1129 | 64.3845 | 39.4907 |  |  | 470.2346 | 26.56 | 46.96
2021-01-07 17:20 | 2.44 | 1.1389 | 0.21717 | 1.9608 | 66.9063 | 54.9199 |  |  | 469.1061 | 26.55 | 47.46
2021-01-07 17:25 | 2.8338 | 1.1961 | 0.23387 | 2.0652 | 68.2966 | 54.7247 |  |  | 470.2843 | 26.49 | 47.52
2021-01-07 17:30 | 3.127 | 1.1719 | 0.23603 | 2.0302 | 58.2686 | 23.4193 |  |  | 471.2169 | 26.45 | 48.48
2021-01-07 17:35 | 3 | 0.96344 | 0.21724 | 1.694 | 46.5968 | 24.478 |  |  | 469.641 | 26.42 | 48.7
2021-01-07 17:40 | 2.5173 | 0.90088 | 0.24652 | 1.6253 | 35.8628 | 7.9435 |  |  | 470.2336 | 26.34 | 49.34
2021-01-07 17:45 | 2.2253 | 0.90242 | 0.2591 | 1.6424 | 36.246 | 29.0842 |  |  | 470.7417 | 26.3 | 50
2021-01-07 17:50 | 2.4921 | 0.86417 | 0.23609 | 1.5607 | 31.3603 | 38.4604 |  |  | 471.3944 | 26.25 | 49.9
2021-01-07 17:55 | 2.327 | 0.86831 | 0.22984 | 1.5608 | 36.1432 | 1.2207 |  |  | 472.0122 | 26.18 | 50.27
2021-01-07 18:00 | 1.9574 | 0.91971 | 0.21303 | 1.6228 | 19.3093 | 31.1145 |  |  | 472.8476 | 26.12 | 49.17
2021-01-07 18:05 | 1.5504 | 0.73565 | 0.17959 | 1.3072 | 23.4949 | 22.7324 |  |  | 471.9312 | 26.07 | 48.86
2021-01-07 18:10 | 1.8682 | 0.67576 | 0.18587 | 1.2217 | 22.5003 | -2.5723 |  |  | 472.5554 | 25.99 | 49.32
2021-01-07 18:15 | 1.6012 | 0.56671 | 0.18167 | 1.0524 | 125.1776 | 399.4845 |  |  | 375.4034 | 25.91 | 49.25
2021-01-07 18:20 | 1.9188 | 0.59256 | 0.16913 | 1.0774 | 164.4408 | 135.8649 |  |  | 358.3829 | 25.85 | 49.26
2021-01-07 18:25 | 2.6812 | 0.6961 | 0.18793 | 1.2549 | 92.3974 | 45.1974 |  |  | 358.8416 | 25.91 | 49.12
2021-01-07 18:30 | 2.6052 | 0.63622 | 0.142 | 1.1172 | 55.9378 | 9.2518 |  |  | 358.6994 | 26 | 49.14
2021-01-07 18:35 | 2.0334 | 0.59262 | 0.13783 | 1.0483 | 33.3776 | 15.6365 |  |  | 358.6638 | 26.03 | 49.05
2021-01-07 18:40 | 1.6774 | 0.68793 | 0.15243 | 1.209 | 19.8642 | 13.1039 |  |  | 358.7073 | 26.02 | 48.82
2021-01-07 18:45 | 1.6901 | 0.79553 | 0.18375 | 1.4032 | 21.897 | 32.6421 |  |  | 357.0507 | 26.07 | 48.62
2021-01-07 18:50 | 1.8425 | 0.79006 | 0.18166 | 1.3927 | 31.3911 | 3.2326 |  |  | 358.1507 | 26.05 | 48.62
2021-01-07 18:55 | 2.1218 | 0.91802 | 0.1712 | 1.5805 | 29.0501 | 31.1237 |  |  | 358.5782 | 26.02 | 48.46
2021-01-07 19:00 | 1.9186 | 1.057 | 0.2067 | 1.8269 | 26.5099 | 40.7102 |  |  | 359.6364 | 26.02 | 48.56
2021-01-07 19:05 | 1.9197 | 0.9513 | 0.19011 | 1.6483 | 26.2611 | 23.8099 |  |  | 358.9142 | 26 | 50.35
2021-01-07 19:10 | 1.9329 | 0.89425 | 0.17761 | 1.5483 | 24.8628 | 4.4253 |  |  | 359.4687 | 25.92 | 51.22
2021-01-07 19:15 | 1.8437 | 0.69654 | 0.15462 | 1.2223 | 26.8551 | 10.8133 |  |  | 359.5978 | 25.83 | 51.32
2021-01-07 19:20 | 1.5512 | 0.50568 | 0.12327 | 0.90048 | 33.3227 | 24.3716 |  |  | 359.7404 | 25.73 | 51.44
2021-01-07 19:25 | 1.602 | 0.47567 | 0.13162 | 0.86282 | 20.3017 | 22.7834 |  |  | 358.2511 | 25.65 | 51.51
2021-01-07 19:30 | 1.7414 | 0.45375 | 0.13367 | 0.8292 | 15.8124 | 17.2971 |  |  | 358.9676 | 25.57 | 51.04
2021-01-07 19:35 | 1.6523 | 0.50822 | 0.11904 | 0.89806 | 21.068 | -9.1918 |  |  | 360.0797 | 25.56 | 50.83
2021-01-07 19:40 | 1.3723 | 0.44816 | 0.11484 | 0.80179 | 24.8141 | 13.5202 |  |  | 359.6535 | 25.54 | 50.17
2021-01-07 19:45 | 1.5367 | 0.46834 | 0.15026 | 0.86606 | 13.4114 | 20.747 |  |  | 360.4166 | 25.51 | 48.65
2021-01-07 19:50 | 1.3965 | 0.53623 | 0.17315 | 0.99718 | 19.1858 | 29.8197 |  |  | 359.4469 | 25.53 | 47.52
2021-01-07 19:55 | 1.3836 | 0.4817 | 0.13141 | 0.86978 | 17.3851 | 5.4531 |  |  | 358.9601 | 25.54 | 46.97
2021-01-07 20:00 | 0.88834 | 0.43942 | 0.13346 | 0.80701 | 5.8478 | 10.6397 |  |  | 360.7638 | 25.45 | 46.5
2021-01-07 20:05 | 0.93905 | 0.47748 | 0.1272 | 0.8591 | 12.0401 | 15.1465 |  |  | 359.7831 | 25.39 | 46.49
2021-01-07 20:10 | 0.9645 | 0.37685 | 0.12512 | 0.70068 | 15.8585 | 10.3659 |  |  | 358.2146 | 25.33 | 46.91
2021-01-07 20:15 | 1.1296 | 0.4966 | 0.098019 | 0.85923 | 9.5747 | 3.8888 |  |  | 359.8354 | 25.3 | 47.22
2021-01-07 20:20 | 0.90109 | 0.65305 | 0.13764 | 1.1387 | 23.7176 | 1.0559 |  |  | 359.8235 | 25.32 | 47.06
2021-01-07 20:25 | 1.0287 | 0.60312 | 0.11687 | 1.0414 | 27.5846 | 7.234 |  |  | 360.124 | 25.31 | 49.21
2021-01-07 20:30 | 1.3726 | 0.62263 | 0.1086 | 1.0651 | 12.8923 | 12.0382 |  |  | 360.461 | 25.26 | 51.58
2021-01-07 20:35 | 1.3861 | 0.48392 | 0.11492 | 0.8567 | 19.5014 | 16.3783 |  |  | 359.7674 | 25.23 | 53.33
2021-01-07 20:40 | 1.5647 | 0.54413 | 0.13378 | 0.96784 | 25.4528 | 6.1368 |  |  | 358.6089 | 25.18 | 54.75
2021-01-07 20:45 | 1.3997 | 0.40376 | 0.09618 | 0.71508 | 22.1201 | -3.3185 |  |  | 359.1299 | 25.12 | 55.7
2021-01-07 20:50 | 1.3971 | 0.35536 | 0.093915 | 0.64071 | 7.9761 | 11.8067 |  |  | 360.0005 | 24.95 | 50.46
2021-01-07 20:55 | 1.3577 | 0.37677 | 0.11259 | 0.69012 | 16.4035 | 30.9392 |  |  | 359.8299 | 24.94 | 47.39
2021-01-07 21:00 | 1.1415 | 0.33177 | 0.087536 | 0.59816 | 11.1211 | 19.1676 |  |  | 359.9969 | 24.91 | 46.33
2021-01-07 21:05 | 1.3314 | 0.32079 | 0.1146 | 0.6084 | 10.7729 | 2.8403 |  |  | 360.6543 | 24.9 | 45.42
2021-01-07 21:10 | 1.6102 | 0.26368 | 0.10834 | 0.51251 | 23.2175 | 9.3316 |  |  | 359.6096 | 24.9 | 45.14
2021-01-07 21:15 | 1.6862 | 0.23649 | 0.099999 | 0.46458 | 13.4493 | -2.5763 |  |  | 361.871 | 24.82 | 45.26
2021-01-07 21:20 | 1.4196 | 0.22963 | 0.093725 | 0.44571 | 4.4414 | 23.8394 |  |  | 360.9365 | 24.78 | 44.54
2021-01-07 21:25 | 1.4447 | 0.19971 | 0.079133 | 0.38317 | 17.1037 | 8.7191 |  |  | 359.9997 | 24.71 | 44.23
2021-01-07 21:30 | 1.6094 | 0.24996 | 0.07288 | 0.45602 | 15.3485 | -6.255 |  |  | 360.6532 | 24.64 | 44.15
2021-01-07 21:35 | 1.609 | 0.22409 | 0.072863 | 0.41636 | 11.9597 | 0.79056 |  |  | 362.3786 | 24.62 | 43.46
2021-01-07 21:40 | 1.3807 | 0.3164 | 0.064527 | 0.54952 | 10.7419 | 14.0152 |  |  | 361.9274 | 24.59 | 43.08
2021-01-07 21:45 | 1.1273 | 0.30281 | 0.083256 | 0.54741 | 15.342 | 5.8875 |  |  | 361.9326 | 24.6 | 42.9
2021-01-07 21:50 | 0.96265 | 0.27021 | 0.097824 | 0.50993 | 6.5562 | -12.4638 |  |  | 361.4138 | 24.59 | 42.85
2021-01-07 21:55 | 0.88665 | 0.36662 | 0.085335 | 0.64522 | 7.5188 | -9.8899 |  |  | 360.9127 | 24.56 | 42.91
2021-01-07 22:00 | 0.75993 | 0.4562 | 0.1103 | 0.80958 | 18.6639 | 3.6983 |  |  | 361.9697 | 24.6 | 42.57
2021-01-07 22:05 | 0.58254 | 0.28373 | 0.076994 | 0.51191 | 5.2276 | 17.0911 |  |  | 361.5262 | 24.56 | 42.25
2021-01-07 22:10 | 0.43053 | 0.27013 | 0.076987 | 0.49105 | 0.04052 | -0.12156 |  |  | 362.2585 | 24.43 | 42.27
2021-01-07 22:15 | 0.4558 | 0.27824 | 0.08322 | 0.50972 | 10.0479 |  |  |  | 360.2359 | 24.35 | 42.11
2021-01-07 22:20 | 0.53175 | 0.27823 | 0.087377 | 0.51386 | 4.8212 | -15.0408 |  |  | 363.0135 | 24.3 | 42.09
2021-01-07 22:25 | 0.36716 | 0.20494 | 0.068654 | 0.3828 | -0.6381 | 10.9389 |  |  | 361.4372 | 24.26 | 42.23
2021-01-07 22:30 | 0.51908 | 0.20494 | 0.083215 | 0.39943 | 7.3532 | 6.2796 |  |  | 362.0096 | 24.24 | 42.21
2021-01-07 22:35 | 0.45573 | 0.18592 | 0.066565 | 0.35155 | 6.5119 | -2.8559 |  |  | 362.0736 | 24.22 | 41.9
2021-01-07 22:40 | 0.36709 | 0.17505 | 0.091522 | 0.35985 | 6.9064 | -13.0635 |  |  | 361.553 | 24.22 | 41.72
2021-01-07 22:45 | 0.37979 | 0.18185 | 0.079049 | 0.3578 | 8.6289 | 2.694 |  |  | 362.0084 | 24.26 | 41.95
2021-01-07 22:50 | 0.35448 | 0.13029 | 0.058249 | 0.25796 | 15.7492 | 6.877 |  |  | 361.456 | 24.26 | 42.06
2021-01-07 22:55 | 0.5824 | 0.14251 | 0.064493 | 0.28294 | -1.5598 | 4.801 |  |  | 361.4372 | 24.26 | 42.23
2021-01-07 23:00 | 0.51913 | 0.13302 | 0.066578 | 0.27047 | 6.7867 | -3.0388 |  |  | 361.362 | 24.3 | 42.37
2021-01-07 23:05 | 0.73429 | 0.18865 | 0.060329 | 0.34949 | 21.6539 | -3.9905 |  |  | 361.4432 | 24.27 | 42.04
2021-01-07 23:10 | 0.53164 | 0.12755 | 0.064479 | 0.26 | 0.51645 | 1.3569 |  |  | 362.6693 | 24.2 | 41.67
2021-01-07 23:15 | 0.46826 | 0.1411 | 0.060308 | 0.27451 | 5.1636 | 5.5989 |  |  | 361.2336 | 24.1 | 41.33
2021-01-07 23:20 | 0.50624 | 0.13432 | 0.047831 | 0.25579 | 10.2665 | -4.4144 |  |  | 362.3955 | 24.03 | 41.55
2021-01-07 23:25 | 0.53154 | 0.13702 | 0.058228 | 0.26826 | -4.4143 | -5.8013 |  |  | 360.2428 | 24.03 | 41.45
2021-01-07 23:30 | 0.48086 | 0.18177 | 0.068618 | 0.34517 | -6.1651 | 10.3663 |  |  | 362.9771 | 24.04 | 41.04
2021-01-07 23:35 | 0.40494 | 0.12344 | 0.054063 | 0.24328 | 10.6296 | 2.0247 |  |  | 361.4111 | 23.99 | 41.2
2021-01-07 23:40 | 0.34166 | 0.11124 | 0.054063 | 0.22457 | 8.5846 | 1.6501 |  |  | 362.0029 | 23.95 | 41.28
2021-01-07 23:45 | 0.53153 | 0.42735 | 0.049909 | 0.70497 | 4.0498 | -9.0107 |  |  | 361.3764 | 23.99 | 41.52
2021-01-07 23:50 |  | 0.47214 | 0.049911 | 0.77154 | 11.0461 | 3.1691 |  |  | 362.9003 | 24.06 | 41.47
2021-01-07 23:55 | 0.43033 | 0.24965 | 0.062392 | 0.44506 | 4.2526 | -14.297 |  |  | 360.8019 | 23.99 | 41.83
2021-01-08 | 0.18985 | 0.31749 | 0.066553 | 0.55322 | 1.0429 | 6.3082 |  |  | 361.9527 | 23.93 | 42.02
2021-01-08 00:05 | 0.11393 | 0.25241 | 0.049923 | 0.43475 | 0.98234 | -8.4764 |  |  | 362.432 | 23.93 | 42.59
2021-01-08 00:10 | 0.037986 | 0.11537 | 0.052015 | 0.22887 | 4.457 | -14.3332 |  |  | 362.0627 | 23.87 | 43.47
2021-01-08 00:15 | 0.15197 | 0.12354 | 0.054104 | 0.24347 | -5.025 | 4.2145 |  |  | 362.0926 | 23.8 | 44.17
2021-01-08 00:20 | 0.11401 | 0.084192 | 0.058282 | 0.18733 | 9.5562 | 3.3948 |  |  | 360.9477 | 23.77 | 45.19
2021-01-08 00:25 | 0.07603 | 0.070637 | 0.043726 | 0.152 | 9.3365 | -12.0432 |  |  | 360.8724 | 23.73 | 46.46
2021-01-08 00:30 | 0.11406 | 0.054343 | 0.045814 | 0.12703 | 2.1697 | -16.1001 |  |  | 361.957 | 23.69 | 46.99
2021-01-08 00:35 | 0.1014 | 0.0625 | 0.039571 | 0.13537 | 3.1027 | 0.34475 |  |  | 361.3576 | 23.71 | 47.26
2021-01-08 00:40 | 0.10139 | 0.044836 | 0.041652 | 0.11038 | 8.9429 | 5.6577 |  |  | 361.4032 | 23.68 | 47.26
2021-01-08 00:45 | 0.063361 | 0.042112 | 0.041646 | 0.1062 | 3.3049 | -0.77046 |  |  | 360.9204 | 23.68 | 46.72
2021-01-08 00:50 | 0.038003 | 0.028518 | 0.035387 | 0.077018 | -0.48644 | -1.2161 |  |  | 362.102 | 23.7 | 45.49
2021-01-08 00:55 | 0.10132 | 0.013576 | 0.031216 | 0.049945 | 0.59777 | -12.4923 |  |  | 360.5958 | 23.68 | 44.69
2021-01-08 01:00 | 0.050656 | 0.013576 | 0.047861 | 0.068671 | -5.5721 | 1.2765 |  |  | 361.1674 | 23.67 | 44.54
2021-01-08 01:05 |  |  |  |  | -7.619 | 2.9382 |  |  | 362.2295 | 23.67 | 44.72
2021-01-08 01:10 |  |  |  |  | 6.3631 | -0.96258 |  |  | 361.1335 | 23.66 | 45
2021-01-08 01:15 |  |  |  |  | -4.9645 | -12.1884 |  |  | 361.7374 | 23.63 | 44.83
2021-01-08 01:20 |  |  |  |  | -3.596 | -12.5708 |  |  | 361.7516 | 23.68 | 43.99
2021-01-08 01:25 |  |  |  |  | 0.94185 | -4.213 |  |  | 362.3938 | 23.66 | 43.32
2021-01-08 01:30 |  |  |  |  | -3.4628 | 10.7933 |  |  | 361.9743 | 23.63 | 42.6
2021-01-08 01:35 |  |  |  |  | -2.8751 | -14.8411 |  |  | 362.5206 | 23.67 | 41.99
2021-01-08 01:40 |  |  |  |  | 3.1282 | -17.595 |  |  | 362.575 | 23.62 | 42.18
2021-01-08 01:45 |  |  |  |  | -1.7616 | 2.369 |  |  | 360.4262 | 23.6 | 42.31
2021-01-08 01:50 | 7.8346 | 1.2157 | -0.49914 | 1.9092 | -1.6606 | -6.4195 |  |  | 360.9018 | 23.61 | 42.79
2021-01-08 01:55 | 0.17723 | 0.090924 | 0.041603 | 0.18097 | 5.6106 | 4.3446 |  |  | 361.4943 | 23.66 | 43.27
2021-01-08 02:00 | 0.30387 | 0.11401 | 0.052013 | 0.22678 | 6.7156 | -12.9349 |  |  | 361.4326 | 23.66 | 43.85
2021-01-08 02:05 | 0.17734 | 0.093696 | 0.047873 | 0.19149 | 2.7361 | -6.4146 |  |  | 360.7308 | 23.66 | 45.37
2021-01-08 02:10 | 0.19021 | 0.095157 | 0.050009 | 0.19587 | 12.1736 | 2.0797 |  |  | 360.854 | 23.68 | 49
2021-01-08 02:15 | 0.15222 | 0.058471 | 0.041687 | 0.13131 | 11.3756 | -1.096 |  |  | 360.3388 | 23.57 | 50.36
2021-01-08 02:20 | 0.15224 | 0.078882 | 0.054202 | 0.17512 | 1.157 | -1.0353 |  |  | 360.8637 | 23.53 | 51.08
2021-01-08 02:25 | 0.16496 | 0.085696 | 0.062552 | 0.19599 | 5.6238 | -14.3538 |  |  | 360.2775 | 23.52 | 51.67
2021-01-08 02:30 | 0.19033 | 0.076174 | 0.062551 | 0.17931 | 9.4609 | 17.6325 |  |  | 360.8794 | 23.47 | 51.81
2021-01-08 02:35 | 0.20299 | 0.11288 | 0.072965 | 0.246 | 1.2991 | 9.8756 |  |  | 360.885 | 23.51 | 51.17
2021-01-08 02:40 | 0.12684 | 0.073427 | 0.05836 | 0.17091 | 4.4649 | -2.6282 |  |  | 359.8444 | 23.54 | 50.37
2021-01-08 02:45 | 0.038054 | 0.082948 | 0.0667 | 0.19593 | 2.9936 | -2.8515 |  |  | 360.3722 | 23.54 | 50.48
2021-01-08 02:50 | 0.088789 | 0.1183 | 0.089623 | 0.27095 | -4.0995 | -2.2527 |  |  | 360.8555 | 23.6 | 50.14
2021-01-08 02:55 | 0.076089 | 0.13731 | 0.085437 | 0.29799 | 5.3262 | 8.3799 |  |  | 361.3984 | 23.66 | 49.24
2021-01-08 03:00 | 0.10143 | 0.10329 | 0.0625 | 0.22083 | 5.8118 | -1.278 |  |  | 362.0738 | 23.62 | 48.54
2021-01-08 03:05 | 0.21547 | 0.12636 | 0.060399 | 0.25409 | -0.42587 | -5.1105 |  |  | 360.62 | 23.57 | 47.7
2021-01-08 03:10 | 0.1267 | 0.17249 | 0.085359 | 0.34976 | 0.7602 | -1.0947 |  |  | 361.8386 | 23.57 | 46.39
2021-01-08 03:15 | 0.063341 | 0.17383 | 0.060368 | 0.32682 | 8.1888 | 11.3609 |  |  | 360.2897 | 23.55 | 46
2021-01-08 03:20 | 0.17733 | 0.38562 | 0.079089 | 0.67018 | 8.2989 | 13.0411 |  |  | 360.7563 | 23.66 | 45.13
2021-01-08 03:25 | 0.1393 | 0.34753 | 0.074912 | 0.6097 | 8.3478 | 19.816 |  |  | 360.7202 | 23.75 | 44.2
2021-01-08 03:30 | 0.088633 | 0.31898 | 0.089465 | 0.5784 | 14.9612 | -8.8025 |  |  | 361.092 | 23.78 | 43.7
2021-01-08 03:35 | 0.17726 | 0.31082 | 0.07906 | 0.55342 | 10.9395 | 5.257 |  |  | 362.6879 | 23.81 | 43.52
2021-01-08 03:40 | 0.11397 | 0.29185 | 0.076988 | 0.52435 | 13.5645 | 16.9278 |  |  | 359.9319 | 23.82 | 43.88
2021-01-08 03:45 | 0.22798 | 0.35844 | 0.097816 | 0.64517 | 23.9428 | 13.4558 |  |  | 360.8669 | 23.88 | 44.4
2021-01-08 03:50 | 0.32937 | 0.36259 | 0.091591 | 0.6453 | 18.6373 | 15.3841 |  |  | 362.3277 | 23.95 | 44.9
2021-01-08 03:55 | 0.58282 | 0.31239 | 0.099933 | 0.5767 | 7.5108 | -5.3417 |  |  | 361.2292 | 23.92 | 45.49
2021-01-08 04:00 | 0.5829 | 0.28527 | 0.097865 | 0.53513 | 15.7434 | 16.1388 |  |  | 360.6991 | 23.87 | 46.1
2021-01-08 04:05 | 0.70967 | 0.46733 | 0.14577 | 0.86211 | 15.8156 | 16.0995 |  |  | 360.6712 | 23.87 | 46.36
2021-01-08 04:10 | 0.73506 | 0.52034 | 0.13745 | 0.93296 | 10.2909 | 6.8538 |  |  | 359.5342 | 23.9 | 46.47
2021-01-08 04:15 | 0.64637 | 0.7391 | 0.24574 | 1.3766 |  |  |  |  | 456.6591 | 23.92 | 46.53
2021-01-08 04:20 | 0.27882 | 0.55295 | 0.14369 | 0.99127 |  |  |  |  | 511.5821 | 24.01 | 46.15
2021-01-08 04:25 | 0.3168 | 0.38443 | 0.12702 | 0.71421 |  | -8.9717 |  |  | 511.7661 | 23.94 | 45.93
2021-01-08 04:30 | 0.4055 | 0.4836 | 0.14576 | 0.88911 | -7.7855 | 19.8389 |  |  | 511.8904 | 23.87 | 46.1
2021-01-08 04:35 | 0.43123 | 1.2332 | 0.24384 | 2.1362 | 26.0257 | 14.4486 |  |  | 510.7221 | 23.97 | 48.8
2021-01-08 04:40 | 0.4186 | 1.489 | 0.3731 | 2.6555 | 39.3027 | 29.8753 |  |  | 510.4976 | 24.06 | 48.99
2021-01-08 04:45 | 0.67244 | 0.97112 | 0.30647 | 1.795 | 41.392 | 40.6308 |  |  | 510.3524 | 24.08 | 49.65
2021-01-08 04:50 | 0.57101 | 0.91682 | 0.28774 | 1.6952 | 43.6708 | 39.8641 |  |  | 509.7019 | 24.11 | 49.95
2021-01-08 04:55 | 0.79955 | 1.2068 | 0.25859 | 2.1084 | 58.4407 | 42.7644 |  |  | 508.9909 | 24.16 | 50.36
2021-01-08 05:00 | 1.9425 | 1.3011 | 0.25869 | 2.2531 | 65.8361 | 56.7661 |  |  | 507.0168 | 24.26 | 51.27
2021-01-08 05:05 | 2.2355 | 1.156 | 0.27758 | 2.0495 | 75.8529 | 70.3354 |  |  | 507.7545 | 24.33 | 52.46
2021-01-08 05:10 | 2.0711 | 1.3008 | 0.4134 | 2.4094 | 72.7198 | 56.7508 |  |  | 508.1035 | 24.33 | 53.67
2021-01-08 05:15 | 1.9433 | 1.3766 | 0.41951 | 2.5296 | 75.9647 | 58.1726 |  |  | 508.813 | 24.34 | 52.43
2021-01-08 05:20 | 3.3364 | 1.8549 | 0.38981 | 3.2331 | 79.16 | 68.1486 |  |  | 507.1801 | 24.4 | 48.27
2021-01-08 05:25 | 3.9548 | 2.0573 | 0.39157 | 3.545 | 72.8793 | 77.1991 |  |  | 509.6295 | 24.47 | 45.43
2021-01-08 05:30 | 3.5117 | 2.4653 | 0.36456 | 4.1435 | 82.2123 | 58.9158 |  |  | 507.184 | 24.59 | 45.65
2021-01-08 05:35 | 3.2457 | 2.1352 | 0.38125 | 3.6541 | 83.5961 | 84.0728 |  |  | 506.0125 | 24.63 | 45.71
2021-01-08 05:40 | 2.2449 | 2.0721 | 0.47101 | 3.6472 | 88.3467 | 93.3591 |  |  | 506.2863 | 24.67 | 46.84
2021-01-08 05:45 | 2.55 | 2.1665 | 0.4628 | 3.7837 | 93.4656 | 72.2636 |  |  | 507.1739 | 24.7 | 47.62
2021-01-08 05:50 | 2.8293 | 2.508 | 0.46283 | 4.3072 | 98.2316 | 100.0586 |  |  | 505.9995 | 24.74 | 47.7
2021-01-08 05:55 | 3.046 | 2.5034 | 0.45881 | 4.2961 | 109.8177 | 78.3426 |  |  | 505.7346 | 24.8 | 48.55
2021-01-08 06:00 | 2.8177 | 2.4015 | 0.50264 | 4.1838 | 89.2638 | 74.5507 |  |  | 507.2932 | 24.81 | 48.75
2021-01-08 06:05 | 2.5519 | 2.2484 | 0.5007 | 3.9451 | 95.5766 | 87.9995 |  |  | 503.8566 | 24.85 | 49.54
2021-01-08 06:10 | 1.968 | 1.8661 | 0.42352 | 3.2839 | 97.6938 | 85.2002 |  |  | 505.9121 | 24.87 | 49.68
2021-01-08 06:15 | 1.8405 | 2.3254 | 0.41923 | 3.9837 | 96.0308 | 85.4397 |  |  | 506.6125 | 24.86 | 48.8
2021-01-08 06:20 | 3.1603 | 2.5306 | 0.43587 | 4.3149 | 107.7181 | 85.0759 |  |  | 508.2252 | 24.89 | 48.4
2021-01-08 06:25 | 4.3903 | 2.1818 | 0.41492 | 3.7593 | 119.7519 | 139.2825 |  |  | 507.1514 | 24.96 | 47.45
2021-01-08 06:30 | 2.9931 | 1.7389 | 0.31469 | 2.9802 | 119.4613 | 77.73 |  |  | 508.453 | 24.97 | 45.92
2021-01-08 06:35 | 3.2082 | 2.0894 | 0.36465 | 3.5673 | 92.7019 | 67.0055 |  |  | 508.0257 | 24.95 | 45.5
2021-01-08 06:40 | 3.8422 | 2.1383 | 0.41257 | 3.6902 | 101.2012 | 67.4911 |  |  | 507.3782 | 25.02 | 45.25
2021-01-08 06:45 | 3.5371 | 2.3036 | 0.40206 | 3.9331 | 91.8482 | 75.509 |  |  | 507.37 | 25.09 | 44.38
2021-01-08 06:50 | 2.7 | 2.2747 | 0.36867 | 3.8555 | 91.7432 | 84.2593 |  |  | 507.3269 | 25.16 | 43.73
2021-01-08 06:55 | 2.8395 | 2.2462 | 0.34369 | 3.7889 | 82.8211 | 76.0368 |  |  | 508.3242 | 25.2 | 43.69
2021-01-08 07:00 | 2.6745 | 1.9743 | 0.40406 | 3.4303 | 89.2734 | 68.0401 |  |  | 506.1467 | 25.24 | 43.33
2021-01-08 07:05 | 2.941 | 2.0221 | 0.35619 | 3.4536 | 81.9716 | 63.9304 |  |  | 508.7277 | 25.27 | 43.6
2021-01-08 07:10 | 3.4976 | 2.035 | 0.29986 | 3.4192 | 79.452 | 58.8616 |  |  | 507.7434 | 25.31 | 42.53
2021-01-08 07:15 | 3.179 | 2.1222 | 0.37045 | 3.6254 | 83.5417 | 64.7461 |  |  | 507.9753 | 25.34 | 40.74
2021-01-08 07:20 | 2.7101 | 2.1776 | 0.38082 | 3.7187 | 85.8431 | 78.9841 |  |  | 507.4388 | 25.37 | 40.35
2021-01-08 07:25 | 4.7226 | 2.4295 | 0.37657 | 4.1006 | 99.5063 | 68.755 |  |  | 507.0068 | 25.38 | 39.58
2021-01-08 07:30 | 3.9741 | 2.0677 | 0.34315 | 3.5126 | 80.0585 | 68.84 |  |  | 506.5271 | 25.46 | 38.22
2021-01-08 07:35 | 2.9231 | 2.0714 | 0.35764 | 3.5327 | 73.9196 | 59.9901 |  |  | 507.2245 | 25.42 | 37.76
2021-01-08 07:40 | 2.5683 | 1.8309 | 0.35133 | 3.1578 | 74.31 | 56.2537 |  |  | 508.4009 | 25.42 | 37.16
2021-01-08 07:45 | 2.3922 | 1.8006 | 0.37645 | 3.1343 | 77.7565 | 41.8603 |  |  | 507.578 | 25.45 | 38.5
2021-01-08 07:50 | 2.1412 | 1.786 | 0.3331 | 3.0729 | 82.8496 | 61.0983 |  |  | 508.1251 | 25.47 | 41.43
2021-01-08 07:55 | 3.0792 | 1.7591 | 0.3269 | 3.0233 | 69.7845 | 49.3783 |  |  | 506.9766 | 25.47 | 41.87
2021-01-08 08:00 | 3.3825 | 1.8673 | 0.36845 | 3.2307 | 70.8617 | 46.3358 |  |  | 507.7082 | 25.43 | 41.21
2021-01-08 08:05 | 3.7868 | 2.3162 | 0.47241 | 4.0228 | 84.8048 | 58.3806 |  |  | 507.271 | 25.45 | 40.35
2021-01-08 08:10 | 2.8352 | 2.1886 | 0.42636 | 3.7811 | 80.5588 | 59.9027 |  |  | 508.0646 | 25.49 | 38.31
2021-01-08 08:15 | 2.0757 | 1.7096 | 0.38683 | 3.0073 | 68.0926 | 41.9491 |  |  | 508.0938 | 25.48 | 38.26
2021-01-08 08:20 | 2.3799 | 1.6637 | 0.3765 | 2.9267 | 63.0611 | 29.8241 |  |  | 505.8879 | 25.46 | 38.83
2021-01-08 08:25 | 2.4694 | 1.7512 | 0.3704 | 3.0548 | 57.2199 | 49.8851 |  |  | 506.7828 | 25.45 | 40.05
2021-01-08 08:30 | 3.1926 | 1.9163 | 0.42261 | 3.36 | 72.0726 | 56.0891 |  |  | 507.6234 | 25.46 | 41.34
2021-01-08 08:35 | 3.7136 | 1.7935 | 0.40612 | 3.1552 | 77.334 | 56.913 |  |  | 506.7939 | 25.51 | 42.46
2021-01-08 08:40 | 3.6508 | 1.6117 | 0.41243 | 2.8808 | 77.1332 | 41.8321 |  |  | 506.6799 | 25.53 | 42.89
2021-01-08 08:45 | 2.9913 | 1.8533 | 0.38739 | 3.2283 | 76.2219 | 30.9775 |  |  | 508.8877 | 25.53 | 42.54
2021-01-08 08:50 | 2.8772 | 1.9702 | 0.44571 | 3.4657 | 64.7646 | 58.2851 |  |  | 506.6975 | 25.55 | 42.53
2021-01-08 08:55 | 2.4082 | 1.7854 | 0.40821 | 3.1428 | 60.8486 | 44.2498 |  |  | 506.1429 | 25.57 | 42.38
2021-01-08 09:00 | 2.8403 | 1.6434 | 0.41255 | 2.9316 | 53.9866 | 55.5387 |  |  | 507.0018 | 25.57 | 43.67
2021-01-08 09:05 | 2.7127 | 1.4934 | 0.42076 | 2.7078 | 59.1625 | 25.9204 |  |  | 507.1718 | 25.56 | 42.78
2021-01-08 09:10 | 2.2065 | 1.4437 | 0.3584 | 2.5734 | 57.3477 | 35.6686 |  |  | 505.8813 | 25.58 | 43.82
2021-01-08 09:15 | 2.2323 | 1.5962 | 0.37097 | 2.8177 | 67.0593 | 49.3128 |  |  | 506.2494 | 25.62 | 44.32
2021-01-08 09:20 | 1.9653 | 1.4299 | 0.33753 | 2.5273 | 55.3638 | 36.1417 |  |  | 505.8648 | 25.62 | 43.41
2021-01-08 09:25 | 1.851 | 1.5059 | 0.36457 | 2.6728 | 59.0394 | 36.1275 |  |  | 507.5659 | 25.58 | 43.22
2021-01-08 09:30 | 2.1421 | 1.6468 | 0.44779 | 2.9721 | 61.7326 | 36.7273 |  |  | 508.8306 | 25.56 | 42.5
2021-01-08 09:35 | 2.0033 | 1.612 | 0.4146 | 2.8856 | 72.5855 | 45.513 |  |  | 505.3914 | 25.57 | 43.49
2021-01-08 09:40 | 1.6486 | 1.4737 | 0.39802 | 2.6549 | 79.2867 | 58.7117 |  |  | 508.5102 | 25.57 | 44.13
2021-01-08 09:45 | 1.8896 | 1.5757 | 0.38135 | 2.7966 | 184.3848 | 386.7577 |  |  | 401.0531 | 25.53 | 44.26
2021-01-08 09:50 | 2.2822 | 1.7982 | 0.43335 | 3.1876 | 337.8967 | 221.0382 |  |  | 345.3061 | 25.46 | 43.71
2021-01-08 09:55 | 2.7139 | 1.887 | 0.45846 | 3.3509 | 201.3699 | 80.9112 |  |  | 347.7507 | 25.43 | 44.59
2021-01-08 10:00 | 2.9053 | 1.8823 | 0.42946 | 3.3147 | 109.4133 | 48.8097 |  |  | 348.6998 | 25.42 | 45.84
2021-01-08 10:05 | 3.5038 | 2.157 | 0.44224 | 3.7507 | 77.3891 | 44.2093 |  |  | 347.0026 | 25.47 | 47.58
2021-01-08 10:10 | 4.3822 | 2.7478 | 0.54058 | 4.7505 | 77.4721 | 46.8958 |  |  | 346.1136 | 25.61 | 48.84
2021-01-08 10:15 | 3.0977 | 2.5123 | 0.47564 | 4.3267 | 86.2488 | 71.136 |  |  | 345.4972 | 25.83 | 46.7
2021-01-08 10:20 | 3.0338 | 2.4807 | 0.47765 | 4.2822 | 100.9301 | 76.6293 |  |  | 349.1064 | 26 | 45.79
2021-01-08 10:25 | 3.3383 | 2.2384 | 0.42549 | 3.8565 | 88.3137 | 66.3394 |  |  | 347.3969 | 26.1 | 45.39
2021-01-08 10:30 | 2.6022 | 1.7268 | 0.36293 | 3.0098 | 20.1778 |  |  |  | 405.8173 | 26.1 | 45.5
2021-01-08 10:35 | 3.3249 | 1.6543 | 0.33782 | 2.8714 | 116.7008 | 284.7824 |  |  | 354.1316 | 25.91 | 45.26
2021-01-08 10:40 | 3.1227 | 1.8207 | 0.40257 | 3.1934 | 108.619 | 73.9596 |  |  | 353.0438 | 25.84 | 46.27
2021-01-08 10:45 | 2.9706 | 2.0046 | 0.47979 | 3.5525 | 73.1023 | 55.3092 |  |  | 352.4789 | 25.84 | 46.51
2021-01-08 10:50 | 2.9188 | 1.9916 | 0.47127 | 3.5241 | 80.5887 | 59.4923 |  |  | 353.6203 | 25.89 | 45.3
2021-01-08 10:55 | 4.5803 | 1.643 | 0.38153 | 2.9 | 75.2846 | 50.3453 |  |  | 353.7132 | 25.87 | 44.77
2021-01-08 11:00 | 7.1187 | 1.8731 | 0.40451 | 3.2757 | 54.899 | 55.2848 |  |  | 351.0361 | 25.83 | 45.22
2021-01-08 11:05 | 6.1032 | 1.7397 | 0.40449 | 3.0712 | 61.9912 | 60.5802 |  |  | 354.755 | 25.88 | 44.91
2021-01-08 11:10 | 6.4957 | 2.7867 | 0.61708 | 4.8887 | 81.2271 | 60.6945 |  |  | 351.4256 | 26.01 | 44.2
2021-01-08 11:15 | 5.6587 | 2.6863 | 0.5504 | 4.668 | 82.0138 | 70.6049 |  |  | 352.2528 | 26.2 | 43.89
2021-01-08 11:20 | 4.1738 | 2.2208 | 0.4607 | 3.8648 | 82.2369 | 69.1448 |  |  | 352.1441 | 26.33 | 43.19
2021-01-08 11:25 | 4.4628 | 2.214 | 0.48333 | 3.8771 | 89.5613 | 67.6527 |  |  | 351.1663 | 26.43 | 41.2
2021-01-08 11:30 | 3.538 | 2.0078 | 0.42717 | 3.5049 | 73.986 | 62.1978 |  |  | 350.4922 | 26.49 | 41.61
2021-01-08 11:35 | 3.6394 | 2.2158 | 0.51051 | 3.9049 | 80.4881 | 60.9393 |  |  | 350.9374 | 26.57 | 41.39
2021-01-08 11:40 | 4.0341 | 2.6396 | 0.62119 | 4.6673 | 94.5546 | 80.9961 |  |  | 350.1734 | 26.65 | 42.29
2021-01-08 11:45 | 3.6693 | 2.8827 | 0.61962 | 5.0363 | 96.1268 | 80.5052 |  |  | 349.276 | 26.71 | 44.51
2021-01-08 11:50 | 4.855 | 2.624 | 0.58115 | 4.6034 | 86.1384 | 64.5176 |  |  | 350.9458 | 26.67 | 40.13
2021-01-08 11:55 | 4.0921 | 2.321 | 0.42052 | 3.9762 | 86.6758 | 50.4629 |  |  | 352.247 | 26.65 | 38.51
2021-01-08 12:00 | 5.2167 | 2.4941 | 0.51307 | 4.3361 | 90.3617 | 89.2448 |  |  | 351.1351 | 26.58 | 44.02
2021-01-08 12:05 | 5.2687 | 2.1857 | 0.46521 | 3.8156 | 176.2965 | 240.9324 |  |  | 351.6593 | 26.52 | 44.84
2021-01-08 12:10 | 3.9064 | 2.0898 | 0.47517 | 3.6784 | 251.3292 | 229.7171 |  |  | 351.6102 | 26.4 | 42.32
2021-01-08 12:15 | 2.8509 | 2.0035 | 0.4643 | 3.5333 | 222.9245 | 124.6804 |  |  | 352.596 | 26.31 | 39.71
2021-01-08 12:20 | 2.5978 | 2.2578 | 0.50392 | 3.9668 | 142.8419 | 24.2801 |  |  | 381.5821 | 26.27 | 40.15
2021-01-08 12:25 | 3.9163 | 2.2255 | 0.5498 | 3.9611 | 7.8376 | 7.0569 |  |  | 401.9348 | 26.26 | 40.57
2021-01-08 12:30 | 3.6125 | 2.0287 | 0.50612 | 3.6158 | 132.3208 | 133.061 |  |  | 352.5386 | 26.25 | 40.91
2021-01-08 12:35 | 3.917 | 1.8101 | 0.44576 | 3.2203 | 94.83 | 48.9615 |  |  | 352.0074 | 26.22 | 41.23
2021-01-08 12:40 | 4.0419 | 2.0374 | 0.50385 | 3.6269 | 78.4259 | 46.4048 |  |  | 351.7858 | 26.25 | 39.77
2021-01-08 12:45 | 3.8394 | 2.2128 | 0.47889 | 3.8686 | 74.8717 | 51.4147 |  |  | 351.7215 | 26.29 | 39.82
2021-01-08 12:50 | 3.4221 | 2.106 | 0.46443 | 3.6925 | 67.5488 | 45.384 |  |  | 351.1008 | 26.29 | 40.52
2021-01-08 12:55 | 3.2948 | 2.2415 | 0.52891 | 3.9648 | 85.9192 | 76.6836 |  |  | 351.1393 | 26.3 | 40.08
2021-01-08 13:00 | 2.8511 | 1.7727 | 0.40811 | 3.1233 | 108.5901 | 90.2417 |  |  | 352.2601 | 26.28 | 39.92
2021-01-08 13:05 | 2.8511 | 1.8542 | 0.40394 | 3.2461 | 96.5661 | 81.9079 |  |  | 352.8598 | 26.23 | 40
2021-01-08 13:10 | 3.6246 | 1.9618 | 0.49563 | 3.5027 | 86.655 | 52.4371 |  |  | 352.2349 | 26.26 | 40.37
2021-01-08 13:15 | 3.8407 | 1.9689 | 0.46447 | 3.4825 | 88.0286 | 56.7557 |  |  | 352.1278 | 26.3 | 40.77
2021-01-08 13:20 | 4.5121 | 2.0285 | 0.43111 | 3.5405 | 69.1115 | 49.3697 |  |  | 351.6307 | 26.29 | 40.57
2021-01-08 13:25 | 3.6245 | 1.9047 | 0.40191 | 3.3215 | 67.1476 | 55.4883 |  |  | 351.131 | 26.29 | 40.27
2021-01-08 13:30 | 3.2074 | 1.7654 | 0.40413 | 3.1101 | 73.4884 | 36.3386 |  |  | 352.1089 | 26.27 | 41.29
2021-01-08 13:35 | 3.8541 | 1.828 | 0.40831 | 3.2103 | 67.2334 | 63.2374 |  |  | 352.6549 | 26.25 | 41.45
2021-01-08 13:40 | 3.5495 | 1.6158 | 0.39162 | 2.8684 | 30.5768 |  |  |  | 421.2737 | 26.26 | 41.21
2021-01-08 13:45 | 2.561 | 1.4746 | 0.38958 | 2.65 |  |  |  |  | 488.2488 | 26.24 | 41.58
2021-01-08 13:50 | 4.1853 | 1.8694 | 0.4689 | 3.3344 |  | 12.9566 |  |  | 486.9618 | 26.27 | 42.5
2021-01-08 13:55 | 4.4649 | 1.3924 | 0.38976 | 2.5241 | 44.2431 | 62.539 |  |  | 487.9195 | 26.3 | 42.81
2021-01-08 14:00 | 4.4265 | 1.5772 | 0.446 | 2.8636 | 68.8858 | 66.065 |  |  | 487.4724 | 26.27 | 42.65
2021-01-08 14:05 | 3.9566 | 1.6422 | 0.42301 | 2.9382 | 68.5504 | 31.7643 |  |  | 486.4933 | 26.26 | 42.22
2021-01-08 14:10 | 3.7904 | 1.6185 | 0.36245 | 2.8455 | 69.3371 | 48.4761 |  |  | 486.1482 | 26.25 | 41.2
2021-01-08 14:15 | 3.4226 | 1.9432 | 0.40618 | 3.3849 | 62.5403 | 39.0535 |  |  | 487.7883 | 26.24 | 41.13
2021-01-08 14:20 | 3.4985 | 1.5763 | 0.33743 | 2.7536 | 60.0932 | 43.8682 |  |  | 487.245 | 26.26 | 40.93
2021-01-08 14:25 | 3.6632 | 1.3969 | 0.30826 | 2.4515 | 51.8279 | 28.2817 |  |  | 486.7479 | 26.24 | 40.94
2021-01-08 14:30 | 3.295 | 1.383 | 0.38941 | 2.5093 | 51.087 | 55.4971 |  |  | 487.4198 | 26.22 | 40.37
2021-01-08 14:35 | 3.1563 | 1.7964 | 0.37284 | 3.1264 | 53.2997 | 31.3044 |  |  | 487.742 | 26.28 | 40.92
2021-01-08 14:40 | 4.1072 | 2.0506 | 0.35828 | 3.5015 | 62.9772 | 46.5585 |  |  | 486.5957 | 26.31 | 41
2021-01-08 14:45 | 3.1438 | 1.8916 | 0.39369 | 3.2933 | 62.0448 | 37.9287 |  |  | 487.0621 | 26.35 | 40.93
2021-01-08 14:50 | 2.587 | 1.6857 | 0.40843 | 2.9924 | 55.7578 | 37.1921 |  |  | 486.3278 | 26.36 | 41.99
2021-01-08 14:55 | 3.6019 | 1.849 | 0.46057 | 3.2948 | 52.2529 | 41.0515 |  |  | 488.4367 | 26.35 | 42.31
2021-01-08 15:00 | 3.6539 | 1.7708 | 0.43154 | 3.1459 | 57.1423 | 58.1268 |  |  | 488.1747 | 26.41 | 43.13
2021-01-08 15:05 | 3.9699 | 1.8002 | 0.44184 | 3.2012 | 78.7589 | 43.8846 |  |  | 487.8261 | 26.38 | 42.39
2021-01-08 15:10 | 3.4617 | 1.6883 | 0.40005 | 2.9879 | 77.5012 | 69.1729 |  |  | 486.8798 | 26.38 | 41.65
2021-01-08 15:15 | 2.6628 | 1.4408 | 0.37087 | 2.5774 | 77.9252 | 56.3289 |  |  | 487.3472 | 26.43 | 41.45
2021-01-08 15:20 | 2.4091 | 1.3552 | 0.32502 | 2.4043 | 60.1306 | 28.767 |  |  | 488.4522 | 26.42 | 41.37
2021-01-08 15:25 | 5.1375 | 1.7936 | 0.3877 | 3.1391 | 63.5882 | 69.7481 |  |  | 488.2132 | 26.43 | 42.66
2021-01-08 15:30 | 4.8204 | 1.9079 | 0.3481 | 3.2726 | 67.6073 | 47.7371 |  |  | 486.0035 | 26.47 | 42.58
2021-01-08 15:35 | 3.5003 | 1.5594 | 0.31259 | 2.7029 | 75.2718 | 45.8185 |  |  | 488.8108 | 26.46 | 41.93
2021-01-08 15:40 | 2.9184 | 1.5833 | 0.30442 | 2.7314 | 65.1497 | 49.0602 |  |  | 488.0052 | 26.47 | 43.4
2021-01-08 15:45 | 3.1463 | 1.579 | 0.32312 | 2.7434 | 67.8887 | 45.0934 |  |  | 488.6098 | 26.48 | 42.87
2021-01-08 15:50 | 3.4257 | 1.5614 | 0.35234 | 2.7479 | 75.8025 | 59.0951 |  |  | 486.9242 | 26.5 | 43.1
2021-01-08 15:55 | 3.3369 | 1.6431 | 0.33984 | 2.8584 | 63.1048 | 62.8815 |  |  | 486.3702 | 26.51 | 43.09
2021-01-08 16:00 | 2.8157 | 1.686 | 0.36889 | 2.9511 | 69.8298 | 39.4708 |  |  | 487.566 | 26.54 | 41.99
2021-01-08 16:05 | 3.6019 | 1.4398 | 0.35012 | 2.5571 | 66.8237 | 53.4508 |  |  | 485.9838 | 26.57 | 41.76
2021-01-08 16:10 | 5.861 | 1.3695 | 0.35647 | 2.4577 | 69.571 | 76.655 |  |  | 485.2381 | 26.59 | 42.49
2021-01-08 16:15 | 3.945 | 1.2986 | 0.33141 | 2.322 | 66.1129 | 41.0783 |  |  | 486.9797 | 26.54 | 42.29
2021-01-08 16:20 | 2.8923 | 1.4687 | 0.33769 | 2.5889 | 71.6479 | 48.6617 |  |  | 486.4465 | 26.52 | 42.52
2021-01-08 16:25 | 2.5497 | 1.6087 | 0.32934 | 2.7973 | 57.5911 | 39.6186 |  |  | 485.4512 | 26.48 | 42.56
2021-01-08 16:30 | 2.5881 | 1.7313 | 0.3544 | 3.0082 | 54.6039 | 26.967 |  |  | 487.5343 | 26.48 | 42.9
2021-01-08 16:35 | 3.4643 | 1.6787 | 0.34823 | 2.9213 | 53.4799 | 41.6632 |  |  | 485.7966 | 26.49 | 43.56
2021-01-08 16:40 | 4.2132 | 1.5196 | 0.39204 | 2.7213 | 59.3406 | 51.838 |  |  | 486.8412 | 26.49 | 43.71
2021-01-08 16:45 | 4.1751 | 1.4203 | 0.37952 | 2.5566 | 67.2793 | 42.5382 |  |  | 485.207 | 26.51 | 43.64
2021-01-08 16:50 | 4.9989 | 1.3819 | 0.28562 | 2.4038 | 58.5865 | 48.7206 |  |  | 485.9276 | 26.46 | 43.15
2021-01-08 16:55 | 4.7329 | 1.3017 | 0.31275 | 2.3081 | 57.5358 | 50.4098 |  |  | 487.4752 | 26.47 | 43.37
2021-01-08 17:00 | 3.8832 | 1.4053 | 0.37117 | 2.5252 | 58.3542 | 37.6135 |  |  | 486.8875 | 26.47 | 43.68
2021-01-08 17:05 | 2.9573 | 1.3674 | 0.41295 | 2.509 | 61.1472 | 43.9261 |  |  | 487.8832 | 26.46 | 44.24
2021-01-08 17:10 | 2.6783 | 1.2437 | 0.30869 | 2.2151 | 50.6212 | 35.0845 |  |  | 488.4485 | 26.42 | 44.55
2021-01-08 17:15 | 2.7669 | 1.2204 | 0.23358 | 2.1043 | 44.3102 | 21.6474 |  |  | 487.4482 | 26.41 | 44.26
2021-01-08 17:20 | 3.6042 | 1.1578 | 0.24816 | 2.0228 | 44.053 | 37.1288 |  |  | 487.5512 | 26.37 | 44.14
2021-01-08 17:25 | 3.7433 | 1.0148 | 0.24187 | 1.7974 | 40.0982 | 41.8544 |  |  | 488.1835 | 26.35 | 43.81
2021-01-08 17:30 | 3.9709 | 1.0975 | 0.28143 | 1.9637 | 52.8063 | 31.2392 |  |  | 486.7507 | 26.31 | 43.27
2021-01-08 17:35 | 3.3105 | 1.0239 | 0.27095 | 1.8404 | 50.5125 | 53.4044 |  |  | 489.0403 | 26.28 | 42.76
2021-01-08 17:40 | 3.2722 | 0.94766 | 0.30011 | 1.7527 | 51.889 | 33.3514 |  |  | 488.5865 | 26.25 | 42.64
2021-01-08 17:45 | 2.9423 | 0.8606 | 0.23757 | 1.5567 | 39.336 | 30.925 |  |  | 489.2595 | 26.18 | 42.68
2021-01-08 17:50 | 2.4349 | 0.72734 | 0.20214 | 1.3191 | 26.6525 | 6.2801 |  |  | 488.3524 | 26.09 | 42.8
2021-01-08 17:55 | 2.1943 | 0.88244 | 0.23134 | 1.584 | 35.4533 | 28.7969 |  |  | 488.8754 | 26.06 | 43.25
2021-01-08 18:00 | 3.2976 | 0.91912 | 0.2626 | 1.6715 | 40.3632 | 33.5041 |  |  | 488.3542 | 26.06 | 43.16
2021-01-08 18:05 | 3.069 | 0.86737 | 0.25424 | 1.5838 | 40.9274 | 20.3014 |  |  | 488.9541 | 26.05 | 42.9
2021-01-08 18:10 | 2.676 | 0.72329 | 0.19381 | 1.3004 | 31.8992 | 29.7584 |  |  | 487.9586 | 25.99 | 43.18
2021-01-08 18:15 | 2.1558 | 0.61719 | 0.1667 | 1.1128 | 24.6121 | 10.6422 |  |  | 489.1898 | 25.92 | 43.09
2021-01-08 18:20 | 2.3333 | 0.57776 | 0.15212 | 1.0377 | 28.3044 | 6.5232 |  |  | 488.8088 | 25.83 | 43.27
2021-01-08 18:25 | 1.5725 | 0.61446 | 0.1792 | 1.1232 | 12.7826 | 13.2391 |  |  | 489.9983 | 25.76 | 43.44
2021-01-08 18:30 | 1.6868 | 0.65258 | 0.18964 | 1.1899 | 27.3534 | 21.5601 |  |  | 490.0328 | 25.71 | 43.86
2021-01-08 18:35 | 1.5979 | 0.69606 | 0.16879 | 1.2337 | 24.8665 | 1.9987 |  |  | 489.6165 | 25.65 | 43.88
2021-01-08 18:40 | 1.1161 | 0.54246 | 0.17297 | 1.0045 | 26.1257 | 35.1861 |  |  | 489.6758 | 25.6 | 44.15
2021-01-08 18:45 | 0.96369 | 0.40236 | 0.14794 | 0.76468 | 47.4543 | 36.9145 |  |  | 490.3807 | 25.55 | 43.75
2021-01-08 18:50 | 1.0143 | 0.39553 | 0.14584 | 0.75212 | 36.7693 | 15.4583 |  |  | 491.0593 | 25.49 | 43.64
2021-01-08 18:55 | 1.3187 | 0.40642 | 0.12293 | 0.7459 | 27.4186 | -6.2993 |  |  | 489.9764 | 25.48 | 43.82
2021-01-08 19:00 | 1.4962 | 0.43225 | 0.1271 | 0.78966 | 20.6122 | 20.9267 |  |  | 490.6433 | 25.4 | 44.04
2021-01-08 19:05 | 1.3314 | 0.43091 | 0.1146 | 0.77512 | 16.515 | 4.8997 |  |  | 490.1468 | 25.36 | 44.3
2021-01-08 19:10 | 1.1667 | 0.38745 | 0.1292 | 0.72309 | 19.2557 | 5.4581 |  |  | 491.2262 | 25.33 | 44.66
2021-01-08 19:15 | 1.154 | 0.47445 | 0.12086 | 0.84811 | 17.2771 | 12.9756 |  |  | 490.7619 | 25.29 | 44.72
2021-01-08 19:20 | 1.1668 | 0.4636 | 0.1292 | 0.83983 | 16.0303 | 19.9364 |  |  | 489.6884 | 25.27 | 44.97
2021-01-08 19:25 | 1.1285 | 0.5043 | 0.12502 | 0.89803 | 19.5172 | -3.5504 |  |  | 489.8518 | 25.22 | 44.59
2021-01-08 19:30 | 1.1032 | 0.55869 | 0.12919 | 0.98557 | 15.7137 | 15.3789 |  |  | 489.917 | 25.17 | 44.83
2021-01-08 19:35 | 1.0906 | 0.69742 | 0.15004 | 1.2191 | 15.9283 | 19.9358 |  |  | 490.4217 | 25.16 | 45.17
2021-01-08 19:40 | 1.0906 | 0.46492 | 0.093768 | 0.80641 | 22.4707 | -2.6681 |  |  | 491.0565 | 25.12 | 45.08
2021-01-08 19:45 | 1.357 | 0.39018 | 0.09586 | 0.69394 | 21.5493 | 25.5974 |  |  | 491.6702 | 25.05 | 45.52
2021-01-08 19:50 | 1.4585 | 0.38069 | 0.09795 | 0.68148 | 27.0702 | 19.3996 |  |  | 490.0746 | 25.02 | 45.8
2021-01-08 19:55 | 1.6361 | 0.47722 | 0.11671 | 0.84821 | 27.608 | 10.9681 |  |  | 490.1227 | 24.99 | 45.89
2021-01-08 20:00 | 1.6233 | 0.4704 | 0.10628 | 0.82733 | 34.1001 | 18.4045 |  |  | 491.2704 | 24.96 | 45.83
2021-01-08 20:05 | 1.1668 | 0.46634 | 0.11671 | 0.83152 | 19.4197 | 27.5772 |  |  | 489.0529 | 24.99 | 45.85
2021-01-08 20:10 | 0.93857 | 0.3739 | 0.10004 | 0.67317 | 21.5616 | 11.4657 |  |  | 490.5413 | 25.02 | 45.97
2021-01-08 20:15 | 0.91317 | 0.39021 | 0.10629 | 0.70441 | 23.1336 | 15.3717 |  |  | 490.0346 | 25.01 | 45.9
2021-01-08 20:20 | 0.76098 | 0.45819 | 0.14172 | 0.84405 | 14.1339 | 4.5354 |  |  | 491.663 | 25 | 45.95
2021-01-08 20:25 | 0.76097 | 0.45954 | 0.10003 | 0.80444 | 18.1212 | 5.3674 |  |  | 490.6434 | 24.97 | 45.98
2021-01-08 20:30 | 0.76098 | 0.46635 | 0.10629 | 0.81904 | 12.3481 | 6.1081 |  |  | 492.3367 | 24.92 | 46.15
2021-01-08 20:35 | 0.63416 | 0.33311 | 0.091701 | 0.60231 | 12.734 | 6.7373 |  |  | 491.3467 | 24.86 | 46.39
2021-01-08 20:40 | 0.6722 | 0.37525 | 0.11046 | 0.68566 | 16.3762 | 29.4447 |  |  | 491.4397 | 24.81 | 46.46
2021-01-08 20:45 | 0.41855 | 0.24745 | 0.10837 | 0.48768 | 17.4318 | 4.2007 |  |  | 492.5583 | 24.78 | 46.6
2021-01-08 20:50 | 0.54532 | 0.30589 | 0.11045 | 0.57932 | 24.8667 | 8.502 |  |  | 491.5783 | 24.75 | 46.37
2021-01-08 20:55 | 0.74822 | 0.31948 | 0.12295 | 0.61265 | 18.8094 | 16.6992 |  |  | 492.6672 | 24.75 | 46.3
2021-01-08 21:00 | 0.72283 | 0.32354 | 0.097938 | 0.59596 | 13.4015 | 10.5 |  |  | 491.1331 | 24.71 | 46.3
2021-01-08 21:05 | 0.69746 | 0.43501 | 0.091685 | 0.7564 | 10.9564 | -3.0029 |  |  | 492.2498 | 24.69 | 46.32
2021-01-08 21:10 | 0.6214 | 0.31812 | 0.097941 | 0.58556 | 10.1251 | -0.37538 |  |  | 492.8145 | 24.66 | 46.56
2021-01-08 21:15 | 0.8243 | 0.36298 | 0.095857 | 0.65224 | 12.2555 | 9.3134 |  |  | 491.2662 | 24.62 | 46.65
2021-01-08 21:20 | 0.6468 | 0.32357 | 0.091694 | 0.58559 | 4.6569 | -10.643 |  |  | 491.8296 | 24.59 | 46.9
2021-01-08 21:25 | 0.59612 | 0.2189 | 0.079197 | 0.41474 | 8.5739 | 3.7746 |  |  | 491.8533 | 24.55 | 47.29
2021-01-08 21:30 | 0.55812 | 0.21213 | 0.075036 | 0.40019 | 10.7769 | 18.6921 |  |  | 491.8371 | 24.53 | 47.67
2021-01-08 21:35 | 0.41857 | 0.15093 | 0.070863 | 0.30013 | 1.3394 | -14.9162 |  |  | 491.8676 | 24.53 | 47.47
2021-01-08 21:40 | 0.5073 | 0.1278 | 0.060435 | 0.25633 | 7.7819 | -10.0648 |  |  | 492.5447 | 24.48 | 47.25
2021-01-08 21:45 | 0.45657 | 0.18626 | 0.075023 | 0.36053 | 0.2638 | 1.3393 |  |  | 492.02 | 24.47 | 47.29
2021-01-08 21:50 | 0.59606 | 0.21616 | 0.075021 | 0.40636 | 4.9714 | 1.6943 |  |  | 491.5444 | 24.44 | 47.28
2021-01-08 21:55 | 0.72289 | 0.25559 | 0.077106 | 0.46889 | 9.1313 | 15.9594 |  |  | 490.9471 | 24.47 | 47.25
2021-01-08 22:00 | 0.6341 | 0.24879 | 0.081273 | 0.46263 | 3.3379 | -6.3816 |  |  | 491.4632 | 24.49 | 47.13
2021-01-08 22:05 | 0.4946 | 0.20121 | 0.064601 | 0.3751 | 105.1082 | 252.5133 |  |  | 397.111 | 24.45 | 47.22
2021-01-08 22:10 | 0.46923 | 0.21616 | 0.077104 | 0.40636 | 287.4521 | 167.4208 |  |  | 328.0512 | 24.45 | 47.19
2021-01-08 22:15 | 0.76085 | 0.34392 | 0.085432 | 0.61261 | 154.8371 | 16.5154 |  |  | 326.3951 | 24.51 | 46.74
2021-01-08 22:20 | 0.72282 | 0.32354 | 0.081266 | 0.5772 | 73.4486 | 6.7362 |  |  | 328.9967 | 24.59 | 46.59
2021-01-08 22:25 | 0.55798 | 0.26101 | 0.089603 | 0.48761 | 29.6641 | 6.5943 |  |  | 328.4621 | 24.58 | 46.68
2021-01-08 22:30 | 0.65939 | 0.36295 | 0.089598 | 0.64594 | 7.1012 | -1.4912 |  |  | 327.939 | 24.58 | 46.52
2021-01-08 22:35 | 0.78619 | 0.40916 | 0.12502 | 0.7522 | 11.5646 | 2.5868 |  |  | 327.3724 | 24.61 | 46.38
2021-01-08 22:40 | 0.57062 | 0.28682 | 0.10001 | 0.53966 | 18.7264 | 9.84 |  |  | 328.4531 | 24.61 | 46.36
2021-01-08 22:45 | 0.87497 | 0.43092 | 0.1146 | 0.77305 | 10.6721 | 3.6318 |  |  | 327.937 | 24.58 | 46.54
2021-01-08 22:50 | 1.2427 | 0.41462 | 0.087518 | 0.72515 | 1.7145 | -9.1203 |  |  | 328.973 | 24.61 | 46.55
2021-01-08 22:55 | 1.3697 | 0.41057 | 0.10628 | 0.73353 | 2.8611 | 5.3061 |  |  | 327.8719 | 24.61 | 46.77
2021-01-08 23:00 | 1.2556 | 0.42691 | 0.085446 | 0.73984 | 12.5408 | 4.7485 |  |  | 328.3996 | 24.6 | 47.02
2021-01-08 23:05 | 1.1288 | 0.39566 | 0.081281 | 0.68777 | 9.1625 | 7.7217 |  |  | 328.4178 | 24.57 | 47.25
2021-01-08 23:10 | 1.1035 | 0.2937 | 0.070864 | 0.52106 | -1.9888 | -9.1629 |  |  | 328.6388 | 24.55 | 47.4
2021-01-08 23:15 | 0.87523 | 0.29235 | 0.072951 | 0.52316 | 2.5369 | -13.679 |  |  | 328.1411 | 24.5 | 47.68
2021-01-08 23:20 | 0.68501 | 0.21486 | 0.066703 | 0.39605 | 14.5425 | 8.5043 |  |  | 328.1406 | 24.48 | 47.96
2021-01-08 23:25 | 0.58356 | 0.19039 | 0.060453 | 0.3523 | 10.1794 | 17.4967 |  |  | 328.7038 | 24.44 | 48.27
2021-01-08 23:30 | 0.57091 | 0.20536 | 0.081304 | 0.39609 | -3.5117 | -5.8461 |  |  | 329.2354 | 24.43 | 48.48
2021-01-08 23:35 | 0.59632 | 0.2489 | 0.081309 | 0.46284 | 2.9233 | -8.4145 |  |  | 327.5846 | 24.44 | 48.68
2021-01-08 23:40 | 0.72325 | 0.21491 | 0.066719 | 0.39615 | 16.9214 | 3.8269 |  |  | 328.6529 | 24.43 | 48.91
2021-01-08 23:45 | 0.72331 | 0.22173 | 0.085492 | 0.42746 | 13.0348 | 9.4614 |  |  | 327.0302 | 24.41 | 49.25
2021-01-08 23:50 |  | 0.19182 | 0.06673 | 0.36076 | -0.8528 | 2.5584 |  |  | 327.5348 | 24.42 | 49.45
2021-01-08 23:55 | 0.53306 | 0.21769 | 0.056309 | 0.38999 | 0.1523 | -15.7988 |  |  | 328.0612 | 24.4 | 49.85
2021-01-09 | 0.22847 | 0.26533 | 0.064657 | 0.47137 | 11.3831 | 6.5394 |  |  | 327.4942 | 24.4 | 50.13
2021-01-09 00:05 | 0.17772 | 0.26128 | 0.054234 | 0.45473 | 8.4494 | 12.5115 |  |  | 328.0085 | 24.39 | 50.51
2021-01-09 00:10 | 0.19041 | 0.22317 | 0.058406 | 0.4005 | -5.3417 | 0.060932 |  |  | 328.0447 | 24.36 | 50.57
2021-01-09 00:15 | 0.12695 | 0.16875 | 0.06258 | 0.32125 | 1.4015 | -12.7456 |  |  | 328.6005 | 24.33 | 50.82
2021-01-09 00:20 | 0.13965 | 0.25042 | 0.06467 | 0.44852 | 12.2791 | 2.7829 |  |  | 326.9885 | 24.31 | 51.06
2021-01-09 00:25 | 0.11427 | 0.34707 | 0.060502 | 0.5925 | 7.8007 | 5.3935 |  |  | 328.5804 | 24.31 | 51.3
2021-01-09 00:30 | 0.11427 | 0.23138 | 0.070934 | 0.42352 | -0.97509 | 4.0426 |  |  | 328.5562 | 24.33 | 51.26
2021-01-09 00:35 | 0.025394 | 0.17694 | 0.047986 | 0.31712 | 4.4286 | -8.9487 |  |  | 328.5946 | 24.29 | 51.44
2021-01-09 00:40 | 0.063486 | 0.20145 | 0.054247 | 0.36304 | 11.976 | -0.16252 |  |  | 327.5163 | 24.28 | 51.59
2021-01-09 00:45 | 0.088882 | 0.12931 | 0.050075 | 0.25037 | 1.3815 | 8.5327 |  |  | 327.2176 | 24.25 | 51.7
2021-01-09 00:50 | 0.19045 | 0.11161 | 0.060504 | 0.23159 | -4.2459 | 3.2504 |  |  | 326.7487 | 24.2 | 51.71
2021-01-09 00:55 | 0.27934 | 0.16606 | 0.060505 | 0.31296 | 3.6567 | -13.3573 |  |  | 327.8335 | 24.19 | 51.77
2021-01-09 01:00 | 0.19046 | 0.13203 | 0.054247 | 0.25663 | 9.782 | -7.3746 |  |  | 327.8154 | 24.2 | 51.81
2021-01-09 01:05 |  |  |  |  | -3.5452 | 6.2472 |  |  | 327.8398 | 24.17 | 51.99
2021-01-09 01:10 |  |  |  |  | -10.168 | 8.4716 |  |  | 328.4094 | 24.15 | 51.96
2021-01-09 01:15 |  |  |  |  | 0.66027 | -12.9108 |  |  | 326.8348 | 24.11 | 52.12
2021-01-09 01:20 |  |  |  |  | 11.6928 | 0.19302 |  |  | 326.302 | 24.08 | 52.49
2021-01-09 01:25 |  |  |  |  | 2.9359 | 8.8586 |  |  | 328.4397 | 24.09 | 52.51
2021-01-09 01:30 |  |  |  |  | -4.622 | -1.0361 |  |  | 328.4849 | 24.07 | 52.34
2021-01-09 01:35 |  |  |  |  | 3.4233 | 1.2291 |  |  | 329.0713 | 24.03 | 52.43
2021-01-09 01:40 |  |  |  |  | 9.5287 | -11.1033 |  |  | 328.5851 | 23.97 | 52.76
2021-01-09 01:45 |  |  |  |  | 3.3525 | 9.1634 |  |  | 328.0674 | 23.94 | 52.98
2021-01-09 01:50 |  |  |  |  | -3.3623 | 5.2009 |  |  | 328.6468 | 23.93 | 52.71
2021-01-09 01:55 |  |  |  |  | -0.56887 | 1.412 |  |  | 328.0972 | 23.93 | 52.82
2021-01-09 02:00 |  |  |  |  | 6.7555 | -19.5453 |  |  | 327.5925 | 23.89 | 53.05
2021-01-09 02:05 |  |  |  |  | 2.9464 | -7.7927 |  |  | 328.0901 | 23.89 | 53.47
2021-01-09 02:10 | 0.08889 | 0.12252 | 0.050079 | 0.23996 | -4.3683 | 2.3162 | 1.4434 | -0.079788 | 327.5754 | 23.9 | 53.08
2021-01-09 02:15 | 0.012698 | 0.18104 | 0.079288 | 0.3568 | 0 | -4.49 | 1.4289 | -0.021759 | 328.6912 | 23.88 | 52.98
2021-01-09 02:20 | 0.012698 | 0.1511 | 0.04799 | 0.2796 | 8.8886 | -0.14222 | 1.4144 | 0 | 327.633 | 23.86 | 53.07
2021-01-09 02:25 | 0.038098 | 0.13342 | 0.054256 | 0.25876 | 5.9637 | -4.4093 | 1.4073 | 0.021762 | 327.6296 | 23.83 | 53.54
2021-01-09 02:30 | 0.050795 | 0.13341 | 0.047993 | 0.25249 | 1.3004 | 3.7995 | 1.4072 | 0.014507 | 327.7024 | 23.78 | 53.52
2021-01-09 02:35 | -0.025397 | 0.078955 | 0.052166 | 0.17319 | 4.1143 | -2.9054 | 1.4144 | 0.014507 | 328.8408 | 23.73 | 53.63
2021-01-09 02:40 | 0.038098 | 0.068069 | 0.039649 | 0.14399 | 7.386 | 5.6284 | 1.4218 | 0.029016 | 328.3471 | 23.67 | 54.04
2021-01-09 02:45 | 0.088905 | 0.063991 | 0.043826 | 0.13983 | 8.7177 | -8.1894 | 1.4364 | 0.029018 | 328.3698 | 23.62 | 54.54
2021-01-09 02:50 | 0.063513 | 0.073533 | 0.050095 | 0.16281 | 0.20324 | 11.2392 | 1.4511 | 0.079813 | 327.7484 | 23.65 | 54.95
2021-01-09 02:55 | 0.063508 | 0.095313 | 0.050091 | 0.19619 | 1.1177 | 7.9665 | 1.4583 | 0.079807 | 328.7949 | 23.7 | 54.54
2021-01-09 03:00 | 0.10161 | 0.12663 | 0.054265 | 0.24837 | 13.3824 | 4.5116 | 1.4728 | 0.065296 | 327.7178 | 23.7 | 54.53
2021-01-09 03:05 | 0.06351 | 0.17838 | 0.056355 | 0.32978 | 16.6346 | 3.6582 | 1.4801 | 0.072554 | 327.6836 | 23.72 | 54.59
2021-01-09 03:10 | 0.050807 | 0.13889 | 0.04383 | 0.25463 | 4.9181 | -7.0114 | 1.4946 | 0.087063 | 328.8251 | 23.67 | 54.67
2021-01-09 03:15 | 0.076203 | 0.21375 | 0.033391 | 0.36104 | 2.2962 | 6.909 | 1.5017 | 0.094308 | 328.9697 | 23.57 | 54.65
2021-01-09 03:20 | 0.17779 | 0.20693 | 0.054255 | 0.37352 | 8.3815 | 3.5558 | 1.5088 | 0.10155 | 328.519 | 23.52 | 54.47
2021-01-09 03:25 | 0.025395 | 0.20962 | 0.060506 | 0.38182 | 14.4343 | 11.6308 | 1.5231 | 0.094285 | 329.1499 | 23.48 | 54.11
2021-01-09 03:30 | 0.12697 | 0.18783 | 0.050073 | 0.33799 | 4.2967 | -5.5257 | 1.5303 | 0.094283 | 327.617 | 23.41 | 54.25
2021-01-09 03:35 | 0.33012 | 0.21233 | 0.056331 | 0.3818 | -0.38598 | 3.6465 | 1.5448 | 0.10879 | 328.7229 | 23.39 | 54.27
2021-01-09 03:40 | 0.31741 | 0.23138 | 0.060501 | 0.41308 | 12.3306 | 10.6242 | 1.552 | 0.10878 | 328.1428 | 23.44 | 53.95
2021-01-09 03:45 | 0.30473 | 0.20962 | 0.064679 | 0.38599 | 22.6417 | 17.4409 | 1.5521 | 0.11604 | 328.6133 | 23.48 | 54.08
2021-01-09 03:50 | 0.29206 | 0.18649 | 0.087635 | 0.37349 | 12.0276 | -2.9358 | 1.5522 | 0.1088 | 328.5922 | 23.48 | 54.3
2021-01-09 03:55 | 0.35549 | 0.19463 | 0.085535 | 0.38386 | 6.4902 | 0.76176 | 1.5519 | 0.10153 | 329.1618 | 23.5 | 53.69
2021-01-09 04:00 | 0.87598 | 0.26538 | 0.077186 | 0.48397 | 10.8266 | 22.6688 | 1.5518 | 0.11603 | 328.6292 | 23.51 | 53.47
2021-01-09 04:05 | 0.62209 | 0.55391 | 0.10431 | 0.95545 | 19.1958 | 13.8331 | 1.5446 | 0.11603 | 328.5444 | 23.58 | 53.32
2021-01-09 04:10 | 0.59674 | 0.51993 | 0.093883 | 0.89085 | 18.0392 | 4.6622 | 1.5592 | 0.11604 | 329.0381 | 23.6 | 53.5
2021-01-09 04:15 | 1.3077 | 0.46545 | 0.08136 | 0.79482 | 4.672 | -5.0072 | 1.5591 | 0.13778 | 329.1385 | 23.53 | 53.49
2021-01-09 04:20 | 0.86329 | 0.46136 | 0.098048 | 0.80524 | 3.9407 | 5.0985 | 1.5519 | 0.13053 | 328.1083 | 23.49 | 53.57
2021-01-09 04:25 | 0.63479 | 0.38652 | 0.093878 | 0.68635 | 13.5389 | 18.7492 | 1.5592 | 0.13053 | 329.7063 | 23.5 | 53.64
2021-01-09 04:30 | 0.64745 | 0.31846 | 0.095959 | 0.5841 | 20.2411 | 16.4021 | 1.5663 | 0.13778 | 328.0944 | 23.51 | 53.42
2021-01-09 04:35 | 0.48246 | 0.3389 | 0.10014 | 0.61962 | 12.8385 | 0.76178 | 1.5665 | 0.12329 | 327.5373 | 23.5 | 53.75
2021-01-09 04:40 | 0.39362 | 0.39337 | 0.13562 | 0.73859 | 12.9512 | 9.6804 | 1.5593 | 0.13055 | 328.5237 | 23.56 | 53.83
2021-01-09 04:45 | 0.35554 | 0.37297 | 0.11059 | 0.68229 | 23.6588 | 22.2163 | 1.5812 | 0.13781 | 328.9684 | 23.63 | 53.78
2021-01-09 04:50 | 0.38094 | 0.31172 | 0.098067 | 0.57588 | 24.6036 | 11.1742 | 1.5812 | 0.10154 | 328.4611 | 23.6 | 53.89
2021-01-09 04:55 | 0.39367 | 0.50641 | 0.12729 | 0.90562 | 21.6085 | 17.8395 | 1.574 | 0.10155 | 328.4143 | 23.62 | 54.08
2021-01-09 05:00 | 0.52066 | 0.61532 | 0.15024 | 1.0934 | 15.1574 | 15.6755 | 1.574 | 0.094297 | 327.7764 | 23.71 | 53.78
2021-01-09 05:05 | 0.50794 | 0.77866 | 0.1878 | 1.3813 | 22.7457 | 18.9971 | 1.5667 | 0.12331 | 327.6858 | 23.8 | 53.4
2021-01-09 05:10 | 0.55875 | 0.88486 | 0.2045 | 1.5608 | 42.3433 | 36.5526 | 1.574 | 0.12331 | 328.6329 | 23.91 | 53.14
2021-01-09 05:15 | 0.80004 | 1.0156 | 0.19198 | 1.7487 | 52.7059 | 32.2757 | 1.574 | 0.13782 | 329.1368 | 23.94 | 53.06
2021-01-09 05:20 | 1.1938 | 1.4459 | 0.21078 | 2.4292 | 42.9377 | 31.5479 | 1.5815 | 0.1596 | 327.9331 | 24.02 | 53.19
2021-01-09 05:25 | 1.5113 | 1.3342 | 0.2066 | 2.2496 | 37.4395 | 41.158 | 1.5814 | 0.22488 | 327.8797 | 24.08 | 52.87
2021-01-09 05:30 | 1.6764 | 1.1586 | 0.19616 | 1.9721 | 39.3697 | 32.593 | 1.5887 | 0.23939 | 327.8481 | 24.11 | 52.76
2021-01-09 05:35 | 2.4512 | 1.2798 | 0.2233 | 2.185 | 45.4977 | 35.7235 | 1.596 | 0.26841 | 327.8148 | 24.13 | 52.81
2021-01-09 05:40 | 3.3405 | 1.25 | 0.2275 | 2.1456 | 55.4705 | 47.5651 | 1.5961 | 0.34099 | 328.2314 | 24.21 | 52.89
2021-01-09 05:45 | 3.4675 | 1.2581 | 0.31724 | 2.2478 | 62.2679 | 85.2526 | 1.5816 | 0.30471 | 327.0699 | 24.29 | 52.61
2021-01-09 05:50 | 2.8705 | 1.3385 | 0.30472 | 2.3563 | 73.7092 | 59.2194 | 1.5816 | 0.25393 | 326.5441 | 24.28 | 52.63
2021-01-09 05:55 | 2.2355 | 1.4365 | 0.29638 | 2.4983 | 81.4543 | 58.5707 | 1.5817 | 0.24668 | 329.2137 | 24.29 | 52.69
2021-01-09 06:00 | 2.6544 | 1.7618 | 0.41739 | 3.1158 | 85.8155 | 57.9148 | 1.5815 | 0.30469 | 327.5763 | 24.34 | 52.22
2021-01-09 06:05 | 2.1211 | 1.3943 | 0.27758 | 2.4147 | 80.4347 | 66.9002 | 1.6106 | 0.38451 | 327.471 | 24.42 | 52.14
2021-01-09 06:10 | 1.8288 | 1.1232 | 0.24207 | 1.9658 | 57.474 | 29.8088 | 1.6322 | 0.46426 | 327.5216 | 24.41 | 51.78
2021-01-09 06:15 | 1.435 | 1.0142 | 0.24206 | 1.7946 | 47.2198 | 29.2177 | 1.6176 | 0.46423 | 327.3621 | 24.38 | 51.72
2021-01-09 06:20 | 0.87628 | 1.0197 | 0.22955 | 1.7926 | 48.0355 | 30.3067 | 1.6104 | 0.27566 | 328.4735 | 24.33 | 52.08
2021-01-09 06:25 | 1.1431 | 1.0838 | 0.22749 | 1.8888 | 50.7024 | 32.7076 | 1.6251 | 0.23215 | 328.485 | 24.29 | 52.53
2021-01-09 06:30 | 2.4513 | 1.0348 | 0.20035 | 1.7886 | 39.5252 | 49.3506 | 1.6178 | 0.27568 | 327.9607 | 24.28 | 52.53
2021-01-09 06:35 | 2.4005 | 0.99257 | 0.17114 | 1.6926 | 35.5731 | 15.7493 | 1.6178 | 0.28294 | 327.9781 | 24.26 | 52.64
2021-01-09 06:40 | 2.5912 | 1.0321 | 0.21706 | 1.7991 | 48.9984 | 12.59 | 1.6179 | 0.32649 | 328.4649 | 24.29 | 52.73
2021-01-09 06:45 | 2.3753 | 1.1438 | 0.22959 | 1.9828 | 47.851 | 36.8866 | 1.6107 | 0.38454 | 328.415 | 24.33 | 52.66
2021-01-09 06:50 | 2.1593 | 1.393 | 0.25046 | 2.3856 | 40.3512 | 39.3249 | 1.6107 | 0.33374 | 328.3306 | 24.41 | 52.37
2021-01-09 06:55 | 1.6895 | 1.2909 | 0.27135 | 2.2501 | 43.413 | 43.1081 | 1.618 | 0.26121 | 328.2078 | 24.5 | 52.32
2021-01-09 07:00 | 1.8169 | 1.0923 | 0.26097 | 1.9374 | 54.8471 | 28.9686 | 1.5966 | 0.20321 | 328.5645 | 24.6 | 52.7
2021-01-09 07:05 | 1.7916 | 0.89628 | 0.2067 | 1.5826 | 57.2196 | 29.3671 | 1.604 | 0.20322 | 326.3567 | 24.63 | 52.84
2021-01-09 07:10 | 1.8934 | 0.81051 | 0.20463 | 1.447 | 43.3463 | 34.7665 | 1.6113 | 0.20323 | 327.9096 | 24.67 | 52.87
2021-01-09 07:15 | 1.6264 | 0.72465 | 0.17956 | 1.2903 | 32.5485 | 26.0225 | 1.604 | 0.18145 | 327.3692 | 24.69 | 52.62
2021-01-09 07:20 | 1.906 | 0.71241 | 0.15451 | 1.2486 | 38.4964 | 29.8456 | 1.575 | 0.18871 | 328.367 | 24.75 | 52.54
2021-01-09 07:25 | 2.8849 | 0.79699 | 0.16289 | 1.3845 | 56.8032 | 46.6565 | 1.568 | 0.23956 | 327.1849 | 24.8 | 52.89
2021-01-09 07:30 | 2.6689 | 0.86648 | 0.17751 | 1.5057 | 56.6512 | 49.6054 | 1.568 | 0.20326 | 327.1271 | 24.85 | 52.76
2021-01-09 07:35 | 2.7193 | 0.88133 | 0.20045 | 1.5535 | 58.6854 | 55.0563 | 1.5823 | 0.28307 | 325.524 | 24.89 | 52.13
2021-01-09 07:40 | 2.1223 | 0.90187 | 0.20465 | 1.5871 | 65.7991 | 43.473 | 1.5752 | 0.18874 | 327.0295 | 24.95 | 52.33
2021-01-09 07:45 | 2.8594 | 1.0272 | 0.21091 | 1.7854 | 59.7999 | 16.1852 | 1.5752 | 0.33391 | 326.9793 | 25 | 52.13
2021-01-09 07:50 | 3.1523 | 1.0983 | 0.2214 | 1.9048 | 47.7521 | 52.5416 | 1.5828 | 0.39932 | 325.7513 | 25.08 | 52.52
2021-01-09 07:55 | 3.1379 | 1.1344 | 0.2338 | 1.9748 | 63.408 | 62.7575 | 1.5601 | 0.38459 | 326.3992 | 25.14 | 50.65
2021-01-09 08:00 | 2.4382 | 1.0155 | 0.26918 | 1.8237 | 83.2527 | 48.8646 | 1.545 | 0.33366 | 325.9207 | 25.21 | 49.16
2021-01-09 08:05 | 2.5396 | 1.1693 | 0.29837 | 2.0907 | 76.0144 | 44.5542 | 1.5594 | 0.29737 | 326.4029 | 25.28 | 48.75
2021-01-09 08:10 | 3.2137 | 1.3453 | 0.29221 | 2.3544 | 62.4949 | 50.7072 | 1.5527 | 0.58044 | 326.2035 | 25.36 | 49.57
2021-01-09 08:15 | 3.8473 | 1.6456 | 0.36513 | 2.8855 | 70.4652 | 53.8977 | 1.5086 | 0.84132 | 327.9274 | 25.37 | 48.37
2021-01-09 08:20 | 3.6442 | 1.7927 | 0.42773 | 3.1756 | 74.6219 | 49.8563 | 1.4578 | 0.75431 | 327.3485 | 25.4 | 48.37
2021-01-09 08:25 | 3.2649 | 1.6383 | 0.34862 | 2.862 | 68.5613 | 54.6376 | 1.4005 | 0.35557 | 326.5939 | 25.45 | 49.75
2021-01-09 08:30 | 3.0372 | 1.7056 | 0.3529 | 2.9673 | 68.5815 | 47.5679 | 1.3864 | 0.22502 | 325.3816 | 25.49 | 50.53
2021-01-09 08:35 | 3.3682 | 1.2699 | 0.30075 | 2.2472 | 72.5387 | 28.4705 | 1.3794 | 0.1815 | 325.817 | 25.53 | 50.94
2021-01-09 08:40 | 3.5214 | 0.9962 | 0.28201 | 1.8111 | 48.7962 | 32.3308 | 1.3869 | 0.22511 | 325.1928 | 25.55 | 51.5
2021-01-09 08:45 | 3.4577 | 1.668 | 0.29661 | 2.8533 | 42.3359 | 43.0987 | 1.3941 | 0.23962 | 325.7348 | 25.56 | 51.31
2021-01-09 08:50 | 3.941 | 1.7962 | 0.33842 | 3.0917 | 57.1981 | 38.8914 | 1.4015 | 0.2832 | 324.6277 | 25.57 | 51.51
2021-01-09 08:55 | 3.6241 | 1.6249 | 0.29462 | 2.7832 | 64.8721 | 46.7136 | 1.4091 | 0.26148 | 326.0789 | 25.64 | 52.03
2021-01-09 09:00 | 4.5013 | 1.3658 | 0.29461 | 2.3861 | 51.8284 | 25.3191 | 1.3945 | 0.276 | 325.5355 | 25.66 | 51.84
2021-01-09 09:05 | 4.9338 | 1.3713 | 0.35104 | 2.451 | 54.4042 | 35.4929 | 1.3873 | 0.30506 | 325.4896 | 25.69 | 51.87
2021-01-09 09:10 | 4.1203 | 1.1029 | 0.3218 | 2.0123 | 64.5507 | 38.7507 | 1.3801 | 0.23244 | 324.8789 | 25.74 | 51.91
2021-01-09 09:15 | 2.7715 | 1.0071 | 0.33424 | 1.878 | 47.1913 | 32.5356 | 1.3797 | 0.20333 | 326.043 | 25.74 | 51.05
2021-01-09 09:20 | 2.3373 | 1.0758 | 0.3298 | 1.9767 | 36.0354 | 19.9587 | 1.3859 | 0.1814 | 325.2372 | 25.74 | 48.61
2021-01-09 09:25 | 3.2016 | 1.1713 | 0.30271 | 2.0981 | 39.446 | 26.9038 | 1.3861 | 0.26125 | 325.6776 | 25.78 | 48.97
2021-01-09 09:30 | 3.9 | 1.1535 | 0.3152 | 2.0812 | 37.2162 | 16.789 | 1.3932 | 0.28299 | 325.7006 | 25.79 | 48.63
2021-01-09 09:35 | 5.1577 | 1.2992 | 0.32982 | 2.3233 | 29.4723 | 10.356 | 1.3932 | 0.38458 | 325.1305 | 25.82 | 48.56
2021-01-09 09:40 | 3.9367 | 1.2892 | 0.35056 | 2.3246 | 40.1083 | 28.2323 | 1.3782 | 0.31191 | 324.6485 | 25.88 | 47.3
2021-01-09 09:45 | 3.2148 | 1.2587 | 0.36122 | 2.2905 | 52.8403 | 41.0889 | 1.3718 | 0.28307 | 324.9162 | 25.94 | 48.98
2021-01-09 09:50 | 3.2289 | 1.4254 | 0.38852 | 2.5755 | 51.3566 | 51.0718 | 1.3723 | 0.25414 | 324.752 | 25.97 | 50.09
2021-01-09 09:55 | 3.4578 | 1.8902 | 0.35094 | 3.2483 | 52.9755 | 37.7205 | 1.3797 | 0.27593 | 325.2315 | 26.01 | 50.08
2021-01-09 10:00 | 4.0429 | 1.8276 | 0.3238 | 3.1252 | 66.3741 | 50.0908 | 1.387 | 0.33405 | 325.1541 | 26.06 | 50.14
2021-01-09 10:05 | 5.7087 | 2.1808 | 0.31965 | 3.6624 | 68.5657 | 52.688 | 1.3944 | 0.49384 | 324.5745 | 26.08 | 50.29
2021-01-09 10:10 | 6.1667 | 1.8196 | 0.38234 | 3.1715 | 63.0042 | 44.8679 | 1.4017 | 0.50112 | 323.439 | 26.13 | 50.25
2021-01-09 10:15 | 4.9461 | 1.5688 | 0.35309 | 2.7558 | 65.0388 | 32.5906 | 1.3944 | 0.42124 | 324.9877 | 26.18 | 50.11
2021-01-09 10:20 | 3.8144 | 1.2621 | 0.39905 | 2.3316 | 63.1355 | 38.1946 | 1.4017 | 0.3486 | 323.8918 | 26.21 | 49.97
2021-01-09 10:25 | 4.8056 | 1.2211 | 0.35931 | 2.2332 | 48.117 | 30.8779 | 1.4015 | 0.27595 | 324.9846 | 26.22 | 49.63
2021-01-09 10:30 | 6.9673 | 1.2416 | 0.35307 | 2.2584 | 38.7726 | 27.1368 | 1.3943 | 0.2687 | 325.445 | 26.27 | 49.66
2021-01-09 10:35 | 6.9042 | 1.4953 | 0.38861 | 2.6827 | 56.3016 | 49.8933 | 1.4017 | 0.26872 | 324.2882 | 26.33 | 49.69
2021-01-09 10:40 | 6.4593 | 1.5498 | 0.36773 | 2.7433 | 64.5731 | 50.8915 | 1.4017 | 0.28325 | 323.6806 | 26.39 | 49.59
2021-01-09 10:45 | 4.9078 | 1.3889 | 0.31966 | 2.4507 | 59.1685 | 34.0547 | 1.3944 | 0.29777 | 323.6867 | 26.4 | 49.41
2021-01-09 10:50 | 4.2973 | 1.6123 | 0.3844 | 2.8558 | 63.5587 | 26.5871 | 1.3798 | 0.28322 | 323.1942 | 26.38 | 49.29
2021-01-09 10:55 | 4.348 | 1.7281 | 0.48885 | 3.1378 | 65.7136 | 69.5684 | 1.3798 | 0.33405 | 323.2009 | 26.38 | 49.23
2021-01-09 11:00 | 4.2845 | 1.6968 | 0.46169 | 3.0626 | 64.1787 | 48.5765 | 1.3798 | 0.29048 | 323.1857 | 26.39 | 49.24
2021-01-09 11:05 | 5.1362 | 1.6941 | 0.39275 | 2.9895 | 63.5366 | 36.5536 | 1.387 | 0.35583 | 324.2502 | 26.4 | 49.15
2021-01-09 11:10 | 5.7849 | 1.4597 | 0.32382 | 2.5613 | 59.359 | 36.6976 | 1.3943 | 0.3268 | 323.6693 | 26.43 | 49.19
2021-01-09 11:15 | 4.9711 | 1.5251 | 0.3468 | 2.6845 | 43.2677 | 39.8299 | 1.4016 | 0.37763 | 324.1639 | 26.47 | 49.04
2021-01-09 11:20 | 5.5946 | 1.8074 | 0.42204 | 3.1925 | 51.6329 | 39.6299 | 1.4017 | 0.35588 | 324.049 | 26.55 | 49.06
2021-01-09 11:25 | 5.3912 | 1.7147 | 0.41369 | 3.0442 | 78.0298 | 58.3672 | 1.3945 | 0.38493 | 324.5259 | 26.6 | 48.94
2021-01-09 11:30 | 4.3472 | 1.567 | 0.41356 | 2.8155 | 70.5412 | 64.3484 | 1.394 | 0.35577 | 324.1052 | 26.59 | 48.07
2021-01-09 11:35 | 5.7589 | 1.5986 | 0.4366 | 2.887 | 64.8865 | 41.1287 | 1.4015 | 0.37034 | 324.0479 | 26.6 | 48.45
2021-01-09 11:40 | 4.5004 | 1.5577 | 0.40108 | 2.7888 | 75.1789 | 56.0079 | 1.3942 | 0.33403 | 324.0149 | 26.63 | 48.37
2021-01-09 11:45 | 4.7927 | 1.435 | 0.35094 | 2.5485 | 71.3329 | 69.1972 | 1.3797 | 0.36307 | 323.9898 | 26.66 | 48.22
2021-01-09 11:50 | 5.2499 | 1.3491 | 0.35927 | 2.4293 | 69.0396 | 44.0637 | 1.3723 | 0.38483 | 324.5476 | 26.66 | 48.01
2021-01-09 11:55 | 6.1903 | 1.5371 | 0.39268 | 2.7487 | 76.2366 | 49.1973 | 1.3868 | 0.45742 | 324.5166 | 26.7 | 47.79
2021-01-09 12:00 | 5.5804 | 1.3055 | 0.353 | 2.3541 | 67.5245 | 30.4674 | 1.3796 | 0.42113 | 323.4037 | 26.73 | 47.82
2021-01-09 12:05 | 5.0078 | 1.1677 | 0.37802 | 2.1679 | 44.3229 | 27.3726 | 1.3794 | 0.37026 | 324.5536 | 26.69 | 47.59
2021-01-09 12:10 | 4.8666 | 1.2532 | 0.40297 | 2.3239 | 53.9065 | 42.6027 | 1.3863 | 0.34113 | 324.6442 | 26.69 | 46.8
2021-01-09 12:15 | 3.6318 | 1.1244 | 0.35264 | 2.0762 | 55.7514 | 26.87 | 1.3781 | 0.3264 | 324.53 | 26.69 | 44.94
2021-01-09 12:20 | 5.1933 | 1.3503 | 0.42356 | 2.4933 | 43.9542 | 49.8459 | 1.3926 | 0.3844 | 322.9171 | 26.72 | 44.68
2021-01-09 12:25 | 4.9885 | 1.2587 | 0.4401 | 2.3673 | 52.4791 | 37.1253 | 1.3848 | 0.36252 | 324.6194 | 26.73 | 43.68
2021-01-09 12:30 | 4.7739 | 1.1624 | 0.41517 | 2.1969 | 63.2188 | 33.3463 | 1.3779 | 0.35536 | 324.5136 | 26.75 | 44.36
2021-01-09 12:35 | 4.1278 | 1.3234 | 0.3694 | 2.398 | 49.2697 | 35.3494 | 1.3712 | 0.29019 | 323.8777 | 26.74 | 45.37
2021-01-09 12:40 | 4.6089 | 1.4441 | 0.40892 | 2.6225 | 48.6745 | 45.9828 | 1.378 | 0.35537 | 324.4963 | 26.76 | 44.39
2021-01-09 12:45 | 3.9988 | 1.3187 | 0.36922 | 2.3905 | 56.557 | 35.2707 | 1.3705 | 0.3408 | 324.5424 | 26.77 | 43.87
2021-01-09 12:50 | 4.3422 | 1.2549 | 0.34007 | 2.2636 | 44.3671 | 24.926 | 1.3707 | 0.38437 | 324.4905 | 26.77 | 44.32
2021-01-09 12:55 | 4.1784 | 1.273 | 0.33599 | 2.2873 | 40.2954 | 43.0793 | 1.3711 | 0.32645 | 323.8314 | 26.8 | 45.05
2021-01-09 13:00 | 3.9522 | 1.2996 | 0.34037 | 2.3325 | 43.3701 | 25.5178 | 1.3574 | 0.29761 | 324.6774 | 26.82 | 46.72
2021-01-09 13:05 | 3.9266 | 1.3677 | 0.40091 | 2.4974 | 40.9283 | 25.4353 | 1.3646 | 0.25405 | 323.6366 | 26.81 | 46.62
2021-01-09 13:10 | 3.7332 | 1.2401 | 0.386 | 2.2868 | 43.1624 | 33.7051 | 1.3636 | 0.29737 | 323.9051 | 26.79 | 44.53
2021-01-09 13:15 | 4.3409 | 1.392 | 0.40254 | 2.5362 | 47.5219 | 21.923 | 1.3703 | 0.33351 | 324.5552 | 26.8 | 43.4
2021-01-09 13:20 | 4.4821 | 1.3312 | 0.37764 | 2.4202 | 57.401 | 47.1926 | 1.3635 | 0.36988 | 324.4353 | 26.81 | 44.32
2021-01-09 13:25 | 3.4052 | 1.2218 | 0.35494 | 2.2277 | 56.12 | 53.0807 | 1.3499 | 0.31934 | 324.1636 | 26.85 | 46.19
2021-01-09 13:30 | 3.9502 | 1.2731 | 0.36316 | 2.3167 | 52.7174 | 19.0628 | 1.364 | 0.30472 | 324.8278 | 26.83 | 45.3
2021-01-09 13:35 | 3.9982 | 1.143 | 0.31077 | 2.0627 | 57.1379 | 41.48 | 1.3558 | 0.29 | 323.4454 | 26.84 | 43.29
2021-01-09 13:40 | 3.9118 | 1.0484 | 0.3193 | 1.9242 | 54.4802 | 31.1925 | 1.3566 | 0.32645 | 323.2161 | 26.87 | 44.92
2021-01-09 13:45 | 4.7724 | 1.113 | 0.33787 | 2.0439 | 54.1614 | 26.3395 | 1.363 | 0.348 | 323.9541 | 26.87 | 43.15
2021-01-09 13:50 | 4.3264 | 1.2023 | 0.37526 | 2.2182 | 50.9725 | 46.8517 | 1.3624 | 0.29713 | 324.6096 | 26.88 | 41.98
2021-01-09 13:55 | 4.2881 | 1.2512 | 0.42527 | 2.3432 | 52.7056 | 15.5894 | 1.3696 | 0.28987 | 324.6145 | 26.89 | 41.82
2021-01-09 14:00 | 3.3515 |  | 0.34628 | 2.2508 | 52.8214 | 28.5384 |  |  | 323.8573 | 26.9 | 43.63
2021-01-09 14:05 | 8.0472 | 1.4586 | 0.36708 | 2.605 | 56.386 | 26.6445 | 1.3848 | 0.98601 | 324.4397 | 26.91 | 43.09
2021-01-09 14:10 | 10.8195 | 1.5424 | 0.34222 | 2.7085 | 65.7093 | 40.5756 | 1.4072 | 1.0953 | 323.7037 | 26.95 | 44.36
2021-01-09 14:15 | 10.1065 | 1.6646 | 0.44856 | 3.0022 | 65.6771 | 49.0496 | 1.4069 | 1.3417 | 324.3067 | 26.94 | 43.88
2021-01-09 14:20 | 7.1448 | 1.5427 | 0.41707 | 2.7839 | 71.8392 | 42.5289 | 1.3845 | 0.94961 | 324.4487 | 26.95 | 42.54
2021-01-09 14:25 | 5.5583 | 1.3903 | 0.43582 | 2.5669 | 66.923 | 51.7963 | 1.37 | 0.66687 | 325.1609 | 26.99 | 42.3
2021-01-09 14:30 | 5.0792 | 1.2196 | 0.39435 | 2.2639 | 66.2932 | 42.2891 | 1.3636 | 0.44244 | 323.8875 | 27 | 43.96
2021-01-09 14:35 | 4.9391 | 1.0834 | 0.36094 | 2.0217 | 52.8905 | 22.5397 | 1.3562 | 0.38438 | 324.4435 | 27 | 43.76
2021-01-09 14:40 | 4.8007 | 1.1545 | 0.36104 | 2.1307 | 52.427 | 35.3171 | 1.3566 | 0.39174 | 324.3686 | 26.99 | 44.52
2021-01-09 14:45 | 4.2386 | 1.1849 | 0.33156 | 2.1478 | 50.6396 | 16.6904 | 1.3555 | 0.30445 | 324.123 | 26.96 | 42.41
2021-01-09 14:50 | 3.9326 | 1.1056 | 0.36063 | 2.0554 | 46.8059 | 22.4286 | 1.3478 | 0.27535 | 324.2156 | 26.98 | 41.38
2021-01-09 14:55 | 3.8987 | 1.0837 | 0.38814 | 2.0492 | 45.6974 | 27.5119 | 1.3637 | 0.25389 | 323.8501 | 27 | 44.28
2021-01-09 15:00 | 3.4934 | 1.0922 | 0.36947 | 2.0436 | 35.2137 | 12.3782 | 1.3714 | 0.25397 | 323.7371 | 27.01 | 45.13
2021-01-09 15:05 | 3.9745 | 1.1353 | 0.36723 | 2.1074 | 39.4553 | 36.55 | 1.3708 | 0.31188 | 324.939 | 27.01 | 43.96
2021-01-09 15:10 | 4.3687 | 0.96114 | 0.32345 | 1.7967 | 48.5022 | 32.2772 | 1.371 | 0.38446 | 324.8992 | 27.01 | 44.3
2021-01-09 15:15 | 4.5476 | 0.86061 | 0.29848 | 1.6197 | 52.9955 | 31.4213 | 1.3568 | 0.47888 | 323.7442 | 27.02 | 44.95
2021-01-09 15:20 | 5.5476 | 0.87776 | 0.2983 | 1.6417 | 56.6285 | 41.3441 | 1.3777 | 0.71062 | 325.0565 | 26.98 | 43.31
2021-01-09 15:25 | 4.4563 | 0.803 | 0.27121 | 1.5021 | 49.3419 | 12.4117 | 1.3561 | 0.56565 | 324.4566 | 27.01 | 43.53
2021-01-09 15:30 | 4.3683 | 1.0781 | 0.30882 | 1.9614 | 52.7139 | 28.597 | 1.3636 | 0.52224 | 323.8619 | 27.01 | 44.06
2021-01-09 15:35 | 4.4311 | 1.2536 | 0.32964 | 2.2511 | 49.8114 | 28.3693 | 1.3489 | 0.36262 | 323.8767 | 27.04 | 43.58
2021-01-09 15:40 | 4.6092 | 1.3149 | 0.35887 | 2.3744 | 49.5402 | 26.7357 | 1.349 | 0.34088 | 323.3025 | 27.06 | 43.7
2021-01-09 15:45 | 4.2293 | 1.2975 | 0.4007 | 2.3875 | 45.2147 | 28.7748 | 1.3494 | 0.3047 | 324.2718 | 27.07 | 44.4
2021-01-09 15:50 | 4.8134 | 1.288 | 0.37356 | 2.3457 | 44.0549 | 24.4354 | 1.3493 | 0.31194 | 324.2502 | 27.1 | 44.23
2021-01-09 15:55 | 5.3951 | 1.1758 | 0.34835 | 2.1506 | 50.9804 | 24.6676 | 1.3414 | 0.31904 | 323.3273 | 27.11 | 42.9
2021-01-09 16:00 | 5.5885 | 1.2268 | 0.37359 | 2.2561 | 51.2825 | 48.285 | 1.3567 | 0.39177 | 324.1727 | 27.15 | 44.3
2021-01-09 16:05 | 5.6124 | 1.3653 | 0.35053 | 2.4412 | 60.2791 | 33.248 | 1.3636 | 0.42793 | 323.7491 | 27.13 | 43.61
2021-01-09 16:10 | 6.168 | 1.3496 | 0.31907 | 2.3878 | 57.7914 | 52.1057 | 1.3701 | 0.42771 | 324.4248 | 27.15 | 42.16
2021-01-09 16:15 | 5.4599 | 1.3231 | 0.32966 | 2.3577 | 52.06 | 32.7698 | 1.3635 | 0.36264 | 323.7345 | 27.15 | 43.5
2021-01-09 16:20 | 6.2226 | 1.3137 | 0.36309 | 2.3789 | 60.7121 | 51.2944 | 1.3637 | 0.34818 | 323.1507 | 27.16 | 43.82
2021-01-09 16:25 | 5.4107 | 1.126 | 0.44455 | 2.1706 | 67.1134 | 56.4342 | 1.3639 | 0.29745 | 324.1508 | 27.17 | 44.25
2021-01-09 16:30 | 5.697 | 1.0677 | 0.40864 | 2.0453 | 65.9375 | 27.0206 | 1.3625 | 0.28265 | 325.0741 | 27.12 | 41.52
2021-01-09 16:35 | 4.2508 | 1.0882 | 0.41492 | 2.0829 | 54.6738 | 19.4698 | 1.3626 | 0.21744 | 323.9883 | 27.12 | 41.69
2021-01-09 16:40 | 4.5937 | 1.0352 | 0.38785 | 1.9726 | 53.6427 | 10.0504 | 1.3555 | 0.2392 | 324.4738 | 27.14 | 41.86
2021-01-09 16:45 | 4.3546 | 0.88735 | 0.3004 | 1.6606 | 48.3752 | 17.6011 | 1.3488 | 0.26106 | 323.7634 | 27.17 | 43.02
2021-01-09 16:50 | 4.3667 | 1.124 | 0.28785 | 2.0087 | 47.7491 | 35.949 | 1.3559 | 0.29003 | 324.8835 | 27.16 | 42.67
2021-01-09 16:55 | 4.0995 | 1.0857 | 0.28363 | 1.9479 | 51.7727 | 37.304 | 1.3557 | 0.30448 | 324.3903 | 27.17 | 42.22
2021-01-09 17:00 | 4.3157 | 1.177 | 0.30869 | 2.1128 | 49.1782 | 30.0573 | 1.3558 | 0.30451 | 323.2932 | 27.17 | 42.49
2021-01-09 17:05 | 4.1257 | 1.2765 | 0.35462 | 2.3113 | 48.9097 | 33.727 | 1.356 | 0.28279 | 324.3105 | 27.18 | 42.78
2021-01-09 17:10 | 3.3379 | 1.0517 | 0.33368 | 1.9478 | 41.7504 | 18.6821 | 1.3556 | 0.26098 | 323.8318 | 27.2 | 42.09
2021-01-09 17:15 | 3.2371 | 1.0397 | 0.32541 | 1.9191 | 42.1458 | 31.1371 | 1.3487 | 0.26104 | 324.3014 | 27.19 | 42.74
2021-01-09 17:20 | 3.9471 | 1.0027 | 0.26277 | 1.7977 | 39.182 | 23.1904 | 1.3557 | 0.26098 | 324.3824 | 27.18 | 42.17
2021-01-09 17:25 | 4.4929 | 1.0449 | 0.24818 | 1.8519 | 33.8616 | 25.8709 | 1.3557 | 0.36248 | 324.9367 | 27.16 | 42.22
2021-01-09 17:30 | 4.7987 | 1.1758 | 0.2545 | 2.0548 | 40.157 | 41.0406 | 1.356 | 0.44234 | 323.798 | 27.15 | 42.96
2021-01-09 17:35 | 4.0764 | 1.0959 | 0.27545 | 1.9532 | 40.6677 | 20.6843 | 1.3564 | 0.40621 | 324.2051 | 27.17 | 43.79
2021-01-09 17:40 | 4.153 | 1.081 | 0.26504 | 1.9221 | 39.2494 | 30.4607 | 1.3493 | 0.39174 | 324.1721 | 27.17 | 44.07
2021-01-09 17:45 | 4.5599 | 1.0117 | 0.26089 | 1.8117 | 43.562 | 23.9403 | 1.3567 | 0.33374 | 323.5839 | 27.19 | 44.31
2021-01-09 17:50 | 4.2171 | 0.88237 | 0.27969 | 1.6322 | 34.8042 | 18.8603 | 1.3568 | 0.24669 | 324.1146 | 27.18 | 44.44
2021-01-09 17:55 | 3.0235 | 0.69046 | 0.28599 | 1.3423 | 29.6253 | 12.5209 | 1.3497 | 0.15964 | 323.5641 | 27.16 | 44.83
2021-01-09 18:00 | 2.7187 | 0.67006 | 0.25051 | 1.2776 | 30.6124 | 20.5505 | 1.3497 | 0.14513 | 324.6582 | 27.12 | 45.05
2021-01-09 18:05 | 4.0279 | 0.63747 | 0.23176 | 1.2089 | 26.1852 | 16.2539 | 1.3572 | 0.24677 | 323.5537 | 27.11 | 45.51
2021-01-09 18:10 | 5.2365 | 0.7739 | 0.2172 | 1.4035 | 28.5311 | 13.8182 | 1.3649 | 0.28314 | 323.5179 | 27.06 | 46.41
2021-01-09 18:15 | 4.6015 | 0.95113 | 0.24647 | 1.7044 | 29.1851 | 29.9884 | 1.365 | 0.28317 | 323.5038 | 27.04 | 46.77
2021-01-09 18:20 | 3.496 | 0.96897 | 0.23397 | 1.7192 | 30.3686 | 16.0081 | 1.3652 | 0.23963 | 323.4511 | 27.05 | 47.1
2021-01-09 18:25 | 3.6363 | 0.82595 | 0.21101 | 1.4771 | 38.6612 | 26.6896 | 1.3653 | 0.18882 | 323.4406 | 27.03 | 47.43
2021-01-09 18:30 | 3.8906 | 0.72784 | 0.18385 | 1.2995 | 38.581 | 27.7584 | 1.3654 | 0.20335 | 324.5386 | 26.99 | 47.62
2021-01-09 18:35 | 4.9466 | 0.68023 | 0.19851 | 1.2412 | 27.9352 | 17.284 | 1.3655 | 0.2397 | 323.994 | 26.96 | 48.09
2021-01-09 18:40 | 3.2936 | 0.60799 | 0.18179 | 1.1138 | 27.4576 | 7.3451 | 1.3656 | 0.19612 | 324.5296 | 26.95 | 48.18
2021-01-09 18:45 | 3.3956 | 0.60258 | 0.19017 | 1.1138 | 22.9321 | 19.0151 | 1.3657 | 0.19613 | 325.5927 | 26.93 | 48.43
2021-01-09 18:50 | 3.1282 | 0.52209 | 0.17552 | 0.9758 | 14.0589 | 21.6071 | 1.3583 | 0.16706 | 325.1182 | 26.91 | 48.18
2021-01-09 18:55 | 2.4788 | 0.45377 | 0.14204 | 0.8355 | 13.1488 | 17.5318 | 1.3505 | 0.12343 | 324.2229 | 26.86 | 47.33
2021-01-09 19:00 | 2.3644 | 0.4933 | 0.16919 | 0.92742 | 25.8913 | 26.1048 | 1.3505 | 0.13796 | 324.7613 | 26.85 | 47.4
2021-01-09 19:05 | 2.0593 | 0.45514 | 0.16502 | 0.86268 | 21.8643 | 26.41 | 1.3505 | 0.12344 | 325.3137 | 26.83 | 47.47
2021-01-09 19:10 | 2.2373 | 0.44289 | 0.17337 | 0.85225 | 23.0241 | 27.6411 | 1.3578 | 0.15248 | 325.3397 | 26.8 | 47.61
2021-01-09 19:15 | 2.8605 | 0.49064 | 0.19428 | 0.94635 | 33.2176 | 19.3956 | 1.358 | 0.26869 | 323.7512 | 26.76 | 48.02
2021-01-09 19:20 | 2.3139 | 0.58878 | 0.20473 | 1.1072 | 32.9949 | 26.7702 | 1.358 | 0.24691 | 324.8601 | 26.71 | 48.25
2021-01-09 19:25 | 2.4918 | 0.5983 | 0.17548 | 1.0905 | 24.7859 | 26.7793 | 1.3652 | 0.25416 | 323.8618 | 26.66 | 48.28
2021-01-09 19:30 | 2.2757 | 0.54787 | 0.18384 | 1.0236 | 24.2671 | 16.5985 | 1.358 | 0.22512 | 325.5037 | 26.62 | 48.39
2021-01-09 19:35 | 1.8181 | 0.59152 | 0.15669 | 1.0634 | 25.7539 | 15.3384 | 1.3653 | 0.18882 | 324.9587 | 26.61 | 48.62
2021-01-09 19:40 | 1.8943 | 0.51243 | 0.16503 | 0.95051 | 23.0262 | 27.7148 | 1.3652 | 0.13071 | 325.8615 | 26.59 | 48.51
2021-01-09 19:45 | 1.6782 | 0.51244 | 0.1525 | 0.93799 | 18.2869 | 23.2501 | 1.358 | 0.12345 | 325.3579 | 26.56 | 48.62
2021-01-09 19:50 | 2.1104 | 0.52469 | 0.13579 | 0.94006 | 22.3445 | 0.94585 | 1.3507 | 0.1888 | 324.8742 | 26.52 | 48.68
2021-01-09 19:55 | 2.0471 | 0.46616 | 0.12745 | 0.84199 | 19.8352 | 8.5444 | 1.3581 | 0.16704 | 324.8823 | 26.47 | 49.23
2021-01-09 20:00 | 2.6578 | 0.47168 | 0.11284 | 0.83585 | 13.7952 | 18.7294 | 1.3583 | 0.18886 | 325.4089 | 26.43 | 49.79
2021-01-09 20:05 | 2.0349 | 0.46901 | 0.12957 | 0.84848 | 16.1368 | 20.1456 | 1.3585 | 0.20341 | 324.8847 | 26.39 | 50.21
2021-01-09 20:10 | 1.8827 | 0.42137 | 0.11915 | 0.76295 | 31.5882 | 34.0102 | 1.3515 | 0.18892 | 326.4301 | 26.38 | 50.82
2021-01-09 20:15 | 2.0995 | 0.45696 | 0.12545 | 0.82589 | 28.9403 | 32.2181 | 1.3591 | 0.1599 | 325.8367 | 26.35 | 51.73
2021-01-09 20:20 | 1.8072 | 0.56482 | 0.094105 | 0.96197 | 26.5222 | 27.0924 | 1.3521 | 0.15993 | 326.3133 | 26.35 | 52.23
2021-01-09 20:25 | 1.4128 | 0.46117 | 0.10666 | 0.81356 | 25.9236 | 17.391 | 1.3522 | 0.16721 | 324.7306 | 26.31 | 52.59
2021-01-09 20:30 | 1.3492 | 0.47349 | 0.092029 | 0.81781 | 23.7874 | -1.4256 | 1.3596 | 0.13814 | 324.7683 | 26.25 | 53.02
2021-01-09 20:35 | 1.502 | 0.58539 | 0.14432 | 1.0416 | 16.2319 | 15.1016 | 1.3596 | 0.14542 | 325.8723 | 26.21 | 53.2
2021-01-09 20:40 | 1.5274 | 0.47348 | 0.12549 | 0.84917 | 14.4902 | 14.5818 | 1.3596 | 0.14541 | 325.381 | 26.18 | 53.21
2021-01-09 20:45 | 1.4638 | 0.45438 | 0.12549 | 0.82407 | 19.7647 | 14.877 | 1.3596 | 0.15995 | 325.9609 | 26.14 | 53.31
2021-01-09 20:50 | 1.4893 | 0.42847 | 0.10667 | 0.76346 | 20.9268 | 18.106 | 1.3669 | 0.14542 | 325.4416 | 26.11 | 53.57
2021-01-09 20:55 | 1.7056 | 0.42025 | 0.0983 | 0.74248 | 13.889 | 26.3117 | 1.3668 | 0.14541 | 326.0218 | 26.09 | 53.41
2021-01-09 21:00 | 2.1764 | 0.4407 | 0.11084 | 0.78637 | 15.1918 | 12.7888 | 1.3595 | 0.15994 | 324.968 | 26.09 | 53.29
2021-01-09 21:05 | 1.7691 | 0.4134 | 0.10875 | 0.74033 | 20.3025 | 10.976 | 1.3667 | 0.12359 | 326.6021 | 26.07 | 53.25
2021-01-09 21:10 | 2.2527 | 0.33017 | 0.10248 | 0.60858 | 6.8422 | -5.1723 | 1.3667 | 0.10905 | 325.0772 | 26 | 53.47
2021-01-09 21:15 | 3.1055 | 0.3984 | 0.11712 | 0.7278 | 6.0786 | -0.30546 | 1.3813 | 0.13813 | 325.127 | 25.95 | 53.67
2021-01-09 21:20 | 3.4363 | 0.42295 | 0.11293 | 0.75915 | 16.2195 | 23.927 | 1.374 | 0.18901 | 325.6897 | 25.93 | 53.67
2021-01-09 21:25 | 1.7564 | 0.39021 | 0.1213 | 0.71943 | 19.1317 | 14.5091 | 1.3667 | 0.13813 | 326.2625 | 25.89 | 53.84
2021-01-09 21:30 | 1.5019 | 0.39705 | 0.11503 | 0.72574 | 9.4187 | -10.4573 | 1.3668 | 0.10178 | 326.2338 | 25.9 | 53.97
2021-01-09 21:35 | 1.8964 | 0.39293 | 0.12339 | 0.72569 | 6.5469 | 14.4377 | 1.374 | 0.1454 | 325.764 | 25.86 | 53.91
2021-01-09 21:40 | 1.8582 | 0.30288 | 0.081561 | 0.54583 | 16.8303 | 16.0361 | 1.3667 | 0.1672 | 325.2666 | 25.83 | 53.97
2021-01-09 21:45 | 1.7183 | 0.29472 | 0.10039 | 0.55424 | 11.6487 | -2.3318 | 1.3668 | 0.11632 | 325.8311 | 25.78 | 54.35
2021-01-09 21:50 | 1.451 | 0.26879 | 0.11921 | 0.52914 | 3.6249 | -1.9754 | 1.3668 | 0.10178 | 325.3515 | 25.73 | 54.51
2021-01-09 21:55 | 1.5655 | 0.27288 | 0.094113 | 0.5124 | 11.6891 | 9.3167 | 1.374 | 0.11632 | 325.9593 | 25.67 | 54.63
2021-01-09 22:00 | 1.8964 | 0.41205 | 0.13594 | 0.76754 | 16.0265 | 18.9589 | 1.374 | 0.19629 | 325.4616 | 25.64 | 54.69
2021-01-09 22:05 | 1.4 | 0.33699 | 0.1192 | 0.63576 | 8.6849 | -1.6291 | 1.374 | 0.15266 | 324.9725 | 25.61 | 54.67
2021-01-09 22:10 | 1.1581 | 0.33971 | 0.12338 | 0.64411 | 4.8667 | -6.2514 | 1.3739 | 0.15993 | 326.1129 | 25.55 | 54.81
2021-01-09 22:15 | 0.97995 | 0.33698 | 0.1192 | 0.63574 | 10.3442 | 11.9936 | 1.3739 | 0.12358 | 325.1128 | 25.49 | 54.97
2021-01-09 22:20 | 0.91634 | 0.33426 | 0.092017 | 0.60438 | 15.985 | 16.2294 | 1.374 | 0.10904 | 325.1266 | 25.47 | 55.11
2021-01-09 22:25 | 1.0691 | 0.31108 | 0.096205 | 0.57305 | 8.2679 | -4.195 | 1.374 | 0.10905 | 326.735 | 25.45 | 55.34
2021-01-09 22:30 | 0.86553 | 0.32338 | 0.075295 | 0.57099 | 7.2704 | 4.8775 | 1.3741 | 0.087245 | 325.1126 | 25.45 | 55.51
2021-01-09 22:35 | 0.6237 | 0.25926 | 0.058564 | 0.45596 | 15.8548 | 4.9489 | 1.3669 | 0.087247 | 326.7205 | 25.44 | 55.61
2021-01-09 22:40 | 0.72552 | 0.24015 | 0.060654 | 0.42876 | 16.16 | 14.5919 | 1.3814 | 0.079975 | 326.2678 | 25.37 | 55.79
2021-01-09 22:45 | 1.6038 | 0.27427 | 0.064838 | 0.48733 | 2.7494 | 0.56006 | 1.3814 | 0.10179 | 326.2963 | 25.34 | 55.93
2021-01-09 22:50 | 1.7056 | 0.23606 | 0.056473 | 0.41622 | 4.0935 | -0.16293 | 1.3741 | 0.10906 | 325.2345 | 25.33 | 55.99
2021-01-09 22:55 | 1.2601 | 0.18694 | 0.071112 | 0.35765 | 12.7488 | 14.4493 | 1.3814 | 0.094516 | 325.2736 | 25.3 | 56.03
2021-01-09 23:00 | 1.4766 | 0.23607 | 0.056475 | 0.41624 | 12.0673 | 10.7842 | 1.3887 | 0.10179 | 325.7895 | 25.3 | 56.21
2021-01-09 23:05 | 1.7313 | 0.39848 | 0.08158 | 0.69239 | 7.9435 | 3.1774 | 1.4034 | 0.13816 | 325.1892 | 25.34 | 56.28
2021-01-09 23:10 | 1.5021 | 0.31113 | 0.054385 | 0.5313 | 13.748 | 11.752 | 1.3961 | 0.10907 | 325.746 | 25.33 | 56.21
2021-01-09 23:15 | 1.1838 | 0.29748 | 0.058568 | 0.51456 | 17.7705 | 13.4017 | 1.4033 | 0.094525 | 325.8127 | 25.27 | 56.4
2021-01-09 23:20 | 0.98023 | 0.36437 | 0.05648 | 0.615 | 12.1396 | 1.2221 | 1.4107 | 0.1018 | 325.848 | 25.22 | 56.75
2021-01-09 23:25 | 0.75109 | 0.35891 | 0.062755 | 0.61291 | 6.5688 | 5.3773 | 1.4107 | 0.087259 | 326.9398 | 25.2 | 56.82
2021-01-09 23:30 | 0.63652 | 0.27157 | 0.058572 | 0.47485 | 13.3617 | 21.3258 | 1.4034 | 0.072715 | 325.9139 | 25.16 | 56.95
2021-01-09 23:35 | 0.40737 | 0.26748 | 0.060664 | 0.47067 | 17.079 | 0.52958 | 1.4034 | 0.065444 | 326.5027 | 25.11 | 57.13
2021-01-09 23:40 | 0.26734 | 0.20471 | 0.062757 | 0.37654 | 8.2291 | 7.73 | 1.4034 | 0.065445 | 327.0865 | 25.06 | 57.36
2021-01-09 23:45 | 0.22915 | 0.20198 | 0.054389 | 0.36399 | 4.7256 | -0.41756 | 1.418 | 0.08726 | 326.1152 | 24.97 | 57.66
2021-01-09 23:50 |  | 0.22108 | 0.04602 | 0.38489 | 8.351 | -3.5746 | 1.4179 | 0.1018 | 326.7047 | 24.93 | 57.7
2021-01-09 23:55 | 0.49642 | 0.20195 | 0.037649 | 0.34511 | 17.7286 | 16.9852 | 1.4323 | 0.10179 | 326.7847 | 24.89 | 57.49
2021-01-10 | 0.61097 | 0.20467 | 0.029282 | 0.34301 | 12.2703 | 17.9218 | 1.4468 | 0.10906 | 326.8345 | 24.85 | 57.57
2021-01-10 00:05
2021-01-10 00:10
2021-01-10 00:15 | 0.45813 | 0.28922 | 0.043914 | 0.48723 | 7.1469 | -7.0858 | 1.4465 | 0.10177 | 327.601 | 24.7 | 57.45
2021-01-10 00:20 | 0.47088 | 0.25921 | 0.037642 | 0.43288 | -3.9809 | -10.9754 | 1.4393 | 0.094502 | 326.8236 | 24.61 | 57.85
2021-01-10 00:25 | 0.54724 | 0.31651 | 0.043915 | 0.52908 | -3.0951 | -11.2298 | 1.4393 | 0.094501 | 326.3565 | 24.55 | 58.03
2021-01-10 00:30 | 0.36906 | 0.32606 | 0.064827 | 0.56671 | 3.8179 | -10.7715 | 1.432 | 0.072693 | 326.9288 | 24.52 | 58.1
2021-01-10 00:35 | 0.33089 | 0.3097 | 0.046008 | 0.51863 | 4.0216 | -0.64143 | 1.4321 | 0.072695 | 326.9406 | 24.5 | 58.27
2021-01-10 00:40 | 0.26726 | 0.17736 | 0.050191 | 0.32206 | -5.9052 | 7.4936 | 1.4248 | 0.058156 | 325.8875 | 24.48 | 58.37
2021-01-10 00:45 | 0.30544 | 0.1337 | 0.041824 | 0.24676 | -5.6506 | 3.3903 | 1.4175 | 0.043616 | 327.0345 | 24.42 | 58.49
2021-01-10 00:50 | 0.25453 | 0.10778 | 0.039732 | 0.20703 | 6.9536 | -6.9536 | 1.4175 | 0.036346 | 327.1056 | 24.36 | 58.65
2021-01-10 00:55 | 0.2418 | 0.12961 | 0.048098 | 0.24676 | 11.0465 | 2.6675 | 1.4248 | 0.050885 | 326.5988 | 24.33 | 58.79
2021-01-10 01:00 | 0.44543 | 0.15417 | 0.027186 | 0.2635 | -0.62106 | -1.4865 | 1.4321 | 0.050886 | 326.6043 | 24.32 | 58.88
2021-01-10 01:05 |  |  |  |  | -3.3191 | 3.0748 |  |  | 327.1732 | 24.29 | 58.99
2021-01-10 01:10 |  |  |  |  | 1.8937 | -1.6697 |  |  | 327.2013 | 24.27 | 59
2021-01-10 01:15 |  |  |  |  | 8.4705 | -3.6855 |  |  | 327.2871 | 24.2 | 59.16
2021-01-10 01:20 |  |  |  |  | 1.9548 | 3.2681 |  |  | 327.3581 | 24.13 | 59.47
2021-01-10 01:25 |  |  |  |  | -0.68212 | 1.2217 |  |  | 327.4054 | 24.09 | 59.58
2021-01-10 01:30 |  |  |  |  | 5.0396 | 0.79411 |  |  | 326.3646 | 24.06 | 59.69
2021-01-10 01:35 |  |  |  |  | 10.1501 | -13.4791 |  |  | 326.9557 | 24.02 | 59.73
2021-01-10 01:40 |  |  |  |  | -2.5756 | -8.7754 |  |  | 327.0437 | 23.95 | 59.87
2021-01-10 01:45 |  |  |  |  | -7.8689 | 1.7102 |  |  | 327.1058 | 23.91 | 59.83
2021-01-10 01:50 |  |  |  |  | 2.4836 | 2.5854 |  |  | 326.6299 | 23.88 | 59.65
2021-01-10 01:55 |  |  |  |  | 12.133 | -12.2348 |  |  | 328.2339 | 23.89 | 59.58
2021-01-10 02:00 |  |  |  |  | 2.0053 | 2.5142 |  |  | 326.6481 | 23.86 | 59.76
2021-01-10 02:05 |  |  |  |  | -5.0794 | 14.6988 |  |  | 326.3369 | 23.84 | 59.86
2021-01-10 02:10 | 0.22902 | 0.1023 | 0.033451 | 0.19025 | 3.8577 | 3.8577 | 1.4826 | -0.087211 | 326.8575 | 23.87 | 59.58
2021-01-10 02:15 | 0.34351 | 0.083196 | 0.039721 | 0.16725 | 9.3231 | -9.659 | 1.4389 | -0.043603 | 326.8655 | 23.88 | 59.35
2021-01-10 02:20 | 0.17812 | 0.065468 | 0.039722 | 0.14007 | -5.1808 | -2.7889 | 1.4099 | 0.014535 | 326.3613 | 23.84 | 59.61
2021-01-10 02:25 | 0.19086 | 0.073655 | 0.037634 | 0.15054 | -9.3545 | 0.37662 | 1.41 | 0.036339 | 327.9985 | 23.8 | 59.93
2021-01-10 02:30 | 0.34351 | 0.099562 | 0.025087 | 0.1777 | -2.3918 | -11.491 | 1.4171 | 0.036336 | 326.9658 | 23.79 | 59.66
2021-01-10 02:35 | 0.15266 | 0.099556 | 0.027176 | 0.17978 | 1.3536 | -8.488 | 1.4025 | 0.036333 | 326.9969 | 23.78 | 59.49
2021-01-10 02:40 | 0.15266 | 0.058642 | 0.029266 | 0.11706 | -4.0913 | -19.8765 | 1.4097 | 0.036333 | 327.0413 | 23.74 | 59.63
2021-01-10 02:45 | 0.2926 | 0.051824 | 0.022995 | 0.10243 | -9.7398 | 3.7657 | 1.417 | 0.0218 | 327.0731 | 23.71 | 59.75
2021-01-10 02:50 | 0.26715 | 0.053186 | 0.027175 | 0.11079 | -3.9487 | 9.4953 | 1.4097 | 0.058132 | 327.6306 | 23.7 | 59.69
2021-01-10 02:55 | 0.2417 | 0.092733 | 0.012542 | 0.15469 | 7.012 | -4.5389 | 1.4242 | 0.072664 | 326.5284 | 23.73 | 59.53
2021-01-10 03:00 | [9 empty] | 23.76 | 59.52
2021-01-10 03:05 | 0.22899 | 0.090009 | 0.029266 | 0.16723 | -3.4807 | 4.0709 | 1.4097 | 0.0436 | 327.0654 | 23.72 | 59.68
2021-01-10 03:10 | 0.21626 | 0.14592 | 0.037627 | 0.25921 | 0.54957 | 12.64 | 1.417 | 0.050865 | 327.105 | 23.69 | 59.72
2021-01-10 03:15 | 0.15265 | 0.14183 | 0.035536 | 0.25293 | 9.8716 | 4.0911 | 1.4097 | 0.043598 | 327.1128 | 23.69 | 59.64
2021-01-10 03:20 | 0.22897 | 0.12137 | 0.025083 | 0.21112 | 16.0382 | -1.1907 | 1.4023 | 0.043596 | 327.7061 | 23.65 | 59.66
2021-01-10 03:25 | 0.27988 | 0.10774 | 0.031356 | 0.1965 | 5.74 | 1.7709 | 1.4097 | 0.036333 | 326.6181 | 23.64 | 59.95
2021-01-10 03:30 | 0.43259 | 0.13094 | 0.060629 | 0.26133 | 1.3436 | -1.4657 | 1.4099 | 0.043605 | 327.106 | 23.65 | 60.31
2021-01-10 03:35 | 0.47076 | 0.25505 | 0.066901 | 0.45786 | 12.5196 | 8.2955 | 1.4099 | 0.043605 | 327.0391 | 23.71 | 60.1
2021-01-10 03:40 | 0.3562 | 0.23729 | 0.071073 | 0.4348 | 16.3751 | 4.6204 | 1.4024 | 0.029066 | 328.6824 | 23.72 | 59.62
2021-01-10 03:45 | 0.2926 | 0.18411 | 0.064804 | 0.34493 | 3.9692 | -2.5444 | 1.4098 | 0.050867 | 326.5119 | 23.73 | 59.7
2021-01-10 03:50 | 0.34348 | 0.28503 | 0.091978 | 0.52888 | 1.7403 | 8.5693 | 1.4461 | 0.029066 | 326.5081 | 23.74 | 59.59
2021-01-10 03:55 | 0.52154 | 0.34636 | 0.094061 | 0.62498 | 9.9322 | 5.8107 | 1.4314 | 0.050862 | 327.0079 | 23.8 | 59.08
2021-01-10 04:00 | 0.41976 | 0.20317 | 0.056434 | 0.36786 | 19.4971 | 21.9394 | 1.4095 | 0.050859 | 327.0004 | 23.82 | 58.86
2021-01-10 04:05 | 0.34347 | 0.22228 | 0.081522 | 0.42224 | 6.5233 | -3.226 | 1.4314 | 0.029065 | 326.975 | 23.82 | 59.12
2021-01-10 04:10 | 0.35615 | 0.22089 | 0.083603 | 0.4222 | 2.6457 | 7.6928 | 1.4095 | 0.036327 | 326.4838 | 23.81 | 58.8
2021-01-10 04:15 | 0.29253 | 0.20452 | 0.066878 | 0.38037 | 10.3988 | 8.7301 | 1.4167 | 0.050854 | 328.1404 | 23.79 | 58.63
2021-01-10 04:20 | 0.26709 | 0.21679 | 0.087776 | 0.42007 | 16.7173 | 8.2213 | 1.4166 | 0.050854 | 326.5427 | 23.78 | 58.64
2021-01-10 04:25 | 0.25438 | 0.24679 | 0.12749 | 0.50578 | 8.3336 | 1.0277 | 1.424 | 0.079917 | 325.4205 | 23.81 | 58.69
2021-01-10 04:30 | 0.29254 | 0.3027 | 0.14839 | 0.61238 | 5.8407 | -5.0266 | 1.453 | 0.10171 | 326.4485 | 23.85 | 58.57
2021-01-10 04:35 | 0.53419 | 0.37768 | 0.14212 | 0.72104 | 15.8222 | 8.4657 | 1.453 | 0.079915 | 326.3818 | 23.92 | 58.22
2021-01-10 04:40 | 0.57231 | 0.26041 | 0.091953 | 0.49111 | 27.583 | 22.4042 | 1.4529 | 0.1235 | 326.9488 | 23.91 | 58.06
2021-01-10 04:45 | 0.5087 | 0.19768 | 0.073141 | 0.37825 | 20.9789 | 10.9168 | 1.4529 | 0.087171 | 327.017 | 23.86 | 58.1
2021-01-10 04:50 | 0.80125 | 0.19906 | 0.068965 | 0.37618 | 4.5379 | 0.16279 | 1.4457 | 0.094441 | 327.0329 | 23.83 | 58.38
2021-01-10 04:55 | 0.61045 | 0.19905 | 0.071053 | 0.37407 | 8.1089 | 14.3253 | 1.4529 | 0.058115 | 327.6364 | 23.78 | 58.44
2021-01-10 05:00 | 0.496 | 0.19633 | 0.071054 | 0.37199 | 14.4477 | 18.4564 | 1.4529 | 0.072645 | 327.1155 | 23.76 | 58.57
2021-01-10 05:05 | 0.64867 | 0.22906 | 0.07106 | 0.42218 | 18.8344 | 12.2917 | 1.4458 | 0.065386 | 327.5714 | 23.81 | 58.66
2021-01-10 05:10 | 0.55967 | 0.21681 | 0.054343 | 0.38458 | 9.5958 | 8.4459 | 1.4313 | 0.06539 | 326.9842 | 23.84 | 58.73
2021-01-10 05:15 | 0.8904 | 0.24408 | 0.058524 | 0.43266 | 11.7227 | 16.3731 | 1.4459 | 0.072656 | 327.5258 | 23.83 | 58.83
2021-01-10 05:20 | 0.81406 | 0.25635 | 0.058523 | 0.45146 | 27.7901 | 24.6152 | 1.4386 | 0.058124 | 327.0168 | 23.81 | 58.84
2021-01-10 05:25 | 0.78861 | 0.29725 | 0.081513 | 0.53715 | 32.8063 | 17.3393 | 1.4531 | 0.043593 | 326.4838 | 23.81 | 58.8
2021-01-10 05:30 | 0.55967 | 0.33271 | 0.085695 | 0.59569 | 23.2519 | 19.731 | 1.4459 | 0.050859 | 326.2201 | 23.85 | 58.79
2021-01-10 05:35 | 0.49604 | 0.32996 | 0.09196 | 0.59774 | 24.0441 | 15.1306 | 1.4385 | 0.087182 | 326.7444 | 23.88 | 58.48
2021-01-10 05:40 | 0.53416 | 0.33676 | 0.098223 | 0.61442 | 30.3506 | 31.2969 | 1.4457 | 0.1017 | 326.724 | 23.92 | 58.1
2021-01-10 05:45 | 0.6232 | 0.36948 | 0.094044 | 0.6604 | 33.6171 | 28.2957 | 1.4457 | 0.18888 | 327.2134 | 23.96 | 58
2021-01-10 05:50 | 1.1448 | 0.38997 | 0.098234 | 0.69391 | 24.8999 | 22.8037 | 1.4458 | 0.20343 | 327.1139 | 24.02 | 58.13
2021-01-10 05:55 | 1.2338 | 0.34226 | 0.087785 | 0.61241 | 11.8651 | -0.60038 | 1.4386 | 0.17437 | 327.6115 | 24.05 | 58.09
2021-01-10 06:00 | 1.2719 | 0.38176 | 0.071057 | 0.65623 | 13.6648 | 2.6353 | 1.4384 | 0.19615 | 327.0976 | 24.06 | 57.71
2021-01-10 06:05 | 1.1701 | 0.39813 | 0.077328 | 0.6876 | 20.0856 | 12.9528 | 1.453 | 0.15983 | 326.5202 | 24.09 | 57.68
2021-01-10 06:10 | 1.1702 | 0.39407 | 0.11287 | 0.71691 | 18.9779 | 8.1915 | 1.4531 | 0.13804 | 326.4745 | 24.11 | 57.85
2021-01-10 06:15 | 0.83952 | 0.3409 | 0.11078 | 0.63332 | 14.4195 | 10.0845 | 1.4386 | 0.10172 | 326.4447 | 24.13 | 57.86
2021-01-10 06:20 | 0.71228 | 0.30952 | 0.13167 | 0.60611 | 17.4611 | -2.0961 | 1.4313 | 0.12351 | 325.9256 | 24.13 | 57.68
2021-01-10 06:25 | 0.81403 | 0.29724 | 0.11495 | 0.57058 | 25.9676 | 31.8694 | 1.4313 | 0.10171 | 327.528 | 24.14 | 57.62
2021-01-10 06:30 | 1.4883 | 0.30682 | 0.09406 | 0.56436 | 22.673 | 24.0773 | 1.4387 | 0.18891 | 327.4856 | 24.15 | 57.9
2021-01-10 06:35 | 1.6918 | 0.44455 | 0.10033 | 0.78384 | 19.4676 | 14.1453 | 1.4459 | 0.14532 | 326.3432 | 24.21 | 57.72
2021-01-10 06:40 | 1.3485 | 0.53321 | 0.11079 | 0.93021 | 32.8412 | 27.7731 | 1.446 | 0.17439 | 325.7012 | 24.29 | 57.62
2021-01-10 06:45 | 1.2212 | 0.66274 | 0.091972 | 1.1078 | 49.835 | 29.0441 | 1.446 | 0.19619 | 325.1331 | 24.33 | 57.36
2021-01-10 06:50 | 1.1194 | 0.62726 | 0.11078 | 1.0702 | 41.6004 | 46.6274 | 1.4459 | 0.14532 | 326.1757 | 24.37 | 57.09
2021-01-10 06:55 | 1.1703 | 0.60549 | 0.096156 | 1.0243 | 29.3706 | 31.9963 | 1.446 | 0.13806 | 326.4442 | 24.4 | 57.27
2021-01-10 07:00 | 1.2467 | 0.56184 | 0.12124 | 0.98245 | 33.3799 | 21.992 | 1.4532 | 0.13079 | 325.9009 | 24.41 | 57.19
2021-01-10 07:05 | 1.3103 | 0.57002 | 0.1296 | 1.0034 | 42.9258 | 13.5453 | 1.4605 | 0.13079 | 324.7498 | 24.48 | 56.96
2021-01-10 07:10 | 1.6412 | 0.44325 | 0.11498 | 0.79441 | 37.9029 | 30.0353 | 1.4462 | 0.15988 | 331.0742 | 24.55 | 57.1
2021-01-10 07:15 | 2.1119 | 0.51552 | 0.14842 | 0.93863 |  |  | 1.4461 | 0.16714 | 447.01 | 24.6 | 56.76
2021-01-10 07:20 | 1.8322 | 0.50332 | 0.1359 | 0.90532 |  |  | 1.439 | 0.14536 | 448.9369 | 24.7 | 56.89
2021-01-10 07:25 | 1.3107 | 0.34922 | 0.10037 | 0.63567 |  | 5.6602 | 1.4392 | 0.13084 | 448.3361 | 24.71 | 57.21
2021-01-10 07:30 | 1.6544 | 0.36835 | 0.12129 | 0.68591 | -13.3373 | 11.4741 | 1.4248 | 0.10904 | 445.6214 | 24.71 | 57.47
2021-01-10 07:35 | 1.5782 | 0.47752 | 0.13803 | 0.87 | 13.9287 | 6.944 | 1.4103 | 0.13813 | 446.024 | 24.78 | 57.43
2021-01-10 07:40 | 1.3872 | 0.55798 | 0.15684 | 1.0121 | 23.1313 | 12.9604 | 1.403 | 0.14539 | 447.0226 | 24.85 | 56.96
2021-01-10 07:45 | 1.3236 | 0.50479 | 0.1422 | 0.91805 | 17.6034 | 3.8078 | 1.403 | 0.14539 | 446.9377 | 24.9 | 56.86
2021-01-10 07:50 | 1.3109 | 0.46388 | 0.13803 | 0.84909 | 21.7789 | 21.0458 | 1.4031 | 0.1454 | 447.3877 | 24.94 | 56.9
2021-01-10 07:55 | 1.6416 | 0.4652 | 0.12128 | 0.83226 | 24.3726 | 0.42759 | 1.4029 | 0.10177 | 447.4067 | 24.96 | 56.49
2021-01-10 08:00 | 1.6417 | 0.42973 | 0.12129 | 0.78208 | 24.047 | 31.3161 | 1.3884 | 0.10177 | 446.8081 | 25 | 56.38
2021-01-10 08:05 | 1.4254 | 0.38201 | 0.11502 | 0.70058 | 21.6765 | 9.8964 | 1.3885 | 0.087235 | 445.1404 | 25.02 | 56.54
2021-01-10 08:10 | 1.0309 | 0.32062 | 0.11711 | 0.60858 | 22.4712 | 17.5636 | 1.3958 | 0.079968 | 445.0545 | 25.07 | 56.45
2021-01-10 08:15 | 1.2474 | 0.44755 | 0.12758 | 0.8136 | 33.6231 | 30.0388 | 1.3886 | 0.087245 | 443.3231 | 25.13 | 56.51
2021-01-10 08:20 | 2.0617 | 0.52934 | 0.1673 | 0.97868 | 24.0478 | 20.7695 | 1.3812 | 0.12358 | 444.3694 | 25.19 | 55.85
2021-01-10 08:25 | 2.316 | 0.56203 | 0.1861 | 1.0476 | 25.6237 | 5.4973 | 1.3738 | 0.16718 | 444.8079 | 25.28 | 55.29
2021-01-10 08:30 | 3.6646 | 0.5879 | 0.21745 | 1.1186 | 23.2804 | 15.0045 | 1.3809 | 0.21804 | 444.7538 | 25.34 | 54.85
2021-01-10 08:35 | 3.4996 | 0.57705 | 0.17774 | 1.0623 | 26.3167 | 8.7043 | 1.3738 | 0.19626 | 444.1132 | 25.38 | 55.04
2021-01-10 08:40 | 2.4685 | 0.57699 | 0.18609 | 1.0705 | 30.233 | 14.5363 | 1.3737 | 0.14536 | 445.1691 | 25.42 | 54.59
2021-01-10 08:45 | 2.0741 | 0.59063 | 0.17354 | 1.0789 | 29.5002 | 34.6612 | 1.3737 | 0.13083 | 444.0394 | 25.46 | 54.47
2021-01-10 08:50 | 2.1636 | 0.53891 | 0.15476 | 0.98082 | 43.18 | 25.627 | 1.374 | 0.13085 | 442.1984 | 25.56 | 54.76
2021-01-10 08:55 | 2.545 | 0.55382 | 0.161 | 1.0099 | 32.2089 | 16.9392 | 1.3665 | 0.17444 | 443.7724 | 25.63 | 54.02
2021-01-10 09:00 | 3.1679 | 0.60283 | 0.18606 | 1.1101 | 29.6182 | 29.4961 | 1.359 | 0.18895 | 444.2774 | 25.7 | 53.29
2021-01-10 09:05 | 3.2449 | 0.63841 | 0.21119 | 1.1898 | 32.9632 | 8.7956 | 1.3665 | 0.21806 | 443.5668 | 25.76 | 53.69
2021-01-10 09:10 | 2.8375 | 0.59881 | 0.16727 | 1.0872 | 35.8415 | 28.4207 | 1.3591 | 0.1817 | 443.5256 | 25.81 | 53.31
2021-01-10 09:15 | 2.3145 | 0.58893 | 0.17971 | 1.0804 | 31.1719 | 20.103 | 1.3584 | 0.14528 | 443.7614 | 25.82 | 51.6
2021-01-10 09:20 | 2.6195 | 0.58751 | 0.19223 | 1.0928 | 28.3207 | 5.1575 | 1.3582 | 0.18885 | 444.2477 | 25.88 | 51.14
2021-01-10 09:25 | 2.6581 | 0.54945 | 0.13793 | 0.98014 | 29.2316 | 34.2578 | 1.3585 | 0.15982 | 444.1189 | 25.91 | 51.61
2021-01-10 09:30 | 2.5948 | 0.50179 | 0.14631 | 0.91547 | 31.2805 | 21.1963 | 1.3587 | 0.17437 | 443.9751 | 25.97 | 51.79
2021-01-10 09:35 | 2.3404 | 0.66268 | 0.19647 | 1.2123 | 38.6271 | 15.2127 | 1.3586 | 0.17437 | 442.2895 | 26.03 | 51.58
2021-01-10 09:40 | 2.2258 | 0.81671 | 0.23408 | 1.486 | 37.9936 | 34.7885 | 1.3586 | 0.17436 | 442.2603 | 26.07 | 51.26
2021-01-10 09:45 | 2.4036 | 0.74164 | 0.20479 | 1.3395 | 42.2016 | 16.6243 | 1.3584 | 0.15981 | 443.8781 | 26.09 | 50.89
2021-01-10 09:50 | 2.6573 | 0.61742 | 0.17758 | 1.124 | 40.4923 | 38.8242 | 1.3653 | 0.16703 | 442.36 | 26.11 | 50.09
2021-01-10 09:55 | 3.4454 | 0.62421 | 0.18384 | 1.1406 | 46.7351 | 17.7176 | 1.3725 | 0.23965 | 443.3763 | 26.16 | 49.79
2021-01-10 10:00 | 2.9745 | 0.67589 | 0.19843 | 1.2365 | 59.8051 | 44.3377 | 1.365 | 0.22509 | 441.7445 | 26.23 | 49.11
2021-01-10 10:05 | 2.7584 | 0.81624 | 0.24438 | 1.4976 | 60.1911 | 36.6089 | 1.365 | 0.19604 | 442.6961 | 26.31 | 48.86
2021-01-10 10:10 | 2.0973 | 0.88024 | 0.29032 | 1.6396 | 46.0947 | 10.1382 | 1.3722 | 0.20329 | 441.5895 | 26.35 | 48.62
2021-01-10 10:15 | 3.3176 | 0.86254 | 0.3133 | 1.6354 | 44.224 | 41.9157 | 1.3795 | 0.31946 | 443.112 | 26.4 | 48.5
2021-01-10 10:20 | 4.0801 | 0.79711 | 0.20468 | 1.4265 | 48.2699 | 14.0529 | 1.3795 | 0.34123 | 441.9981 | 26.44 | 48.31
2021-01-10 10:25 | 5.5793 | 0.74661 | 0.19422 | 1.3386 | 44.7769 | 18.1284 | 1.3793 | 0.48638 | 440.9536 | 26.46 | 47.92
2021-01-10 10:30 | 4.8042 | 0.7548 | 0.23181 | 1.3888 | 48.4686 | 28.4589 | 1.3793 | 0.40654 | 441.4486 | 26.48 | 47.92
2021-01-10 10:35 | 4.3974 | 0.79293 | 0.22763 | 1.441 | 46.7191 | 16.9083 | 1.3793 | 0.42105 | 442.4922 | 26.5 | 47.82
2021-01-10 10:40 | 3.5712 | 0.9605 | 0.23807 | 1.7104 | 44.634 | 28.824 | 1.372 | 0.28312 | 444.0251 | 26.55 | 47.63
2021-01-10 10:45 | 3.394 | 0.88438 | 0.2235 | 1.5791 | 44.1651 | 16.4437 | 1.3578 | 0.23235 | 443.3582 | 26.58 | 48.12
2021-01-10 10:50 | 4.5052 | 0.97137 | 0.23631 | 1.7253 | 44.6139 | 37.2937 | 1.3666 | 0.31985 | 442.7648 | 26.63 | 51.3
2021-01-10 10:55 | 4.8375 | 0.93891 | 0.27612 | 1.7153 | 59.0585 | 32.7831 | 1.3743 | 0.35631 | 442.0405 | 26.67 | 52.03
2021-01-10 11:00 | 5.7551 | 0.93224 | 0.2678 | 1.6968 | 60.0768 | 26.29 | 1.3891 | 0.37818 | 442.971 | 26.71 | 52.38
2021-01-10 11:05 | 5.5772 | 0.96916 | 0.26154 | 1.7471 | 48.3053 | 21.4124 | 1.3965 | 0.32003 | 442.3482 | 26.75 | 52.46
2021-01-10 11:10 | 4.062 | 0.90365 | 0.28038 | 1.6634 | 42.4991 | 23.8981 | 1.3747 | 0.29821 | 442.2723 | 26.8 | 52.32
2021-01-10 11:15 | 3.9604 | 0.96652 | 0.27203 | 1.7515 | 44.4179 | 28.9124 | 1.3748 | 0.24731 | 442.1467 | 26.86 | 52.37
2021-01-10 11:20 | 4.189 | 0.82578 | 0.27199 | 1.5357 | 40.754 | 41.3143 | 1.3746 | 0.25455 | 442.7198 | 26.88 | 51.86
2021-01-10 11:25 | 5.1691 | 0.74247 | 0.25523 | 1.3933 | 42.5747 | 21.3383 | 1.3745 | 0.30544 | 442.1266 | 26.94 | 51.51
2021-01-10 11:30 | 5.0295 | 0.78895 | 0.23852 | 1.4499 | 49.4241 | 12.9876 | 1.3746 | 0.30547 | 441.9949 | 27 | 51.6
2021-01-10 11:35 | 5.6413 | 0.80543 | 0.25947 | 1.4941 | 46.9034 | 9.8208 | 1.3748 | 0.29096 | 441.8403 | 27.07 | 51.71
2021-01-10 11:40 | 4.8659 | 0.81385 | 0.23234 | 1.4798 | 50.3917 | 51.4005 | 1.3679 | 0.34197 | 443.2188 | 27.13 | 52.31
2021-01-10 11:45 | 4.5102 | 0.7867 | 0.25751 | 1.4634 | 56.1912 | 29.9149 | 1.3682 | 0.35659 | 442.0092 | 27.17 | 52.74
2021-01-10 11:50 | 4.8282 | 0.93684 | 0.33075 | 1.7668 | 58.3359 | 41.3977 | 1.3753 | 0.64035 | 441.42 | 27.24 | 52.25
2021-01-10 11:55 | 4.9039 | 0.98722 | 0.32023 | 1.8335 | 45.5286 | 39.2007 | 1.3751 | 0.64753 | 440.9115 | 27.27 | 51.75
2021-01-10 12:00 | 4.1794 | 0.90837 | 0.29523 | 1.6855 | 48.3694 | 20.7341 | 1.3611 | 0.45126 | 441.2174 | 27.31 | 52.65
2021-01-10 12:05 | 3.4275 | 0.89058 | 0.28056 | 1.6457 | 36.6045 | 25.0656 | 1.3464 | 0.3639 | 441.7492 | 27.32 | 52.52
2021-01-10 12:10 | 3.3242 | 0.79462 | 0.22812 | 1.4461 | 43.996 | 31.973 | 1.3459 | 0.2619 | 440.4563 | 27.31 | 51.32
2021-01-10 12:15 | 3.0949 | 0.72773 | 0.23231 | 1.3478 | 44.0476 | 25.5849 | 1.3459 | 0.22553 | 439.8612 | 27.35 | 51.24
2021-01-10 12:20 | 2.9426 | 0.67868 | 0.25327 | 1.2936 | 44.2275 | 36.2176 | 1.3461 | 0.21101 | 440.8396 | 27.36 | 51.62
2021-01-10 12:25 | 3.1462 | 0.73053 | 0.25954 | 1.3793 | 39.0589 | 37.4897 | 1.346 | 0.22555 | 441.9059 | 27.37 | 51.46
2021-01-10 12:30 | 4.2923 | 0.75915 | 0.24487 | 1.4085 | 37.0282 | 30.0994 | 1.3459 | 0.31283 | 441.3662 | 27.4 | 51.16
2021-01-10 12:35 | 5.2727 | 0.8888 | 0.21765 | 1.58 | 34.774 | 23.8619 | 1.3531 | 0.49468 | 442.4261 | 27.42 | 50.92
2021-01-10 12:40 | 5.0686 | 0.79591 | 0.22391 | 1.4439 | 38.6027 | 16.9937 | 1.3603 | 0.41464 | 442.4229 | 27.44 | 50.7
2021-01-10 12:45 | 4.1643 | 0.64436 | 0.20507 | 1.1928 | 39.5495 | 25.0521 | 1.3603 | 0.32006 | 440.8415 | 27.44 | 50.65
2021-01-10 12:50 | 3.2977 | 0.55415 | 0.22805 | 1.0754 | 31.7493 | 16.6946 | 1.3455 | 0.24 | 441.4452 | 27.45 | 50.08
2021-01-10 12:55 | 2.7754 | 0.60051 | 0.19874 | 1.1192 | 43.3473 | 13.7701 | 1.3381 | 0.22543 | 441.4538 | 27.47 | 49.79
2021-01-10 13:00 | 3.1826 | 0.69872 | 0.24474 | 1.3137 | 44.6169 | 11.1109 | 1.3452 | 0.34176 | 440.3993 | 27.49 | 49.52
2021-01-10 13:05 | 3.1954 | 0.84613 | 0.22593 | 1.5229 | 52.9597 | 16.9165 | 1.3525 | 0.31269 | 441.9292 | 27.52 | 49.53
2021-01-10 13:10 | 3.6792 | 0.82703 | 0.25312 | 1.5208 | 55.6994 | 14.7371 | 1.3453 | 0.25451 | 441.8694 | 27.56 | 49.42
2021-01-10 13:15 | 3.4627 | 0.76152 | 0.23848 | 1.4058 | 58.2454 | 22.5791 | 1.338 | 0.21815 | 441.8711 | 27.56 | 49.41
2021-01-10 13:20 | 3.0806 | 0.70824 | 0.23427 | 1.3199 | 57.7416 | 26.61 | 1.3379 | 0.19632 | 440.3323 | 27.55 | 49.22
2021-01-10 13:25 | 2.9532 | 0.75053 | 0.32631 | 1.4767 | 58.7593 | 10.5502 | 1.3306 | 0.21086 | 440.8381 | 27.57 | 49.13
2021-01-10 13:30 | 3.9209 | 0.86111 | 0.32632 | 1.6463 | 61.787 | 22.2319 | 1.3307 | 0.23996 | 440.2563 | 27.59 | 49.21
2021-01-10 13:35 | 5.0025 | 0.87741 | 0.24891 | 1.5938 | 56.3949 | 4.8472 | 1.3451 | 0.31265 | 441.8821 | 27.59 | 48.99
2021-01-10 13:40 | 5.2318 | 0.83513 | 0.22799 | 1.5081 | 63.1478 | 22.7601 | 1.3451 | 0.36355 | 442.3875 | 27.6 | 49.02
2021-01-10 13:45 | 5.3339 | 0.87885 | 0.23637 | 1.5835 | 60.6972 | 19.0341 | 1.3525 | 0.39266 | 439.6689 | 27.63 | 49.09
2021-01-10 13:50 | 5.2195 | 0.95665 | 0.2573 | 1.7237 | 65.7193 | 15.1441 | 1.3598 | 0.38539 | 440.6896 | 27.65 | 49.09
2021-01-10 13:55 | 4.6081 | 0.8911 | 0.24473 | 1.6106 | 69.005 | 24.1049 | 1.3452 | 0.35629 | 440.1991 | 27.64 | 48.97
2021-01-10 14:00 | 3.8697 | 0.86652 | 0.23009 | 1.5604 | 72.904 | 41.3554 | 1.3451 | 0.31266 | 441.7966 | 27.64 | 48.92
2021-01-10 14:05 | 3.8436 | 0.81043 | 0.23423 | 1.4765 | 72.0053 | 13.3788 | 1.3449 | 0.28352 | 440.8148 | 27.64 | 48.45
2021-01-10 14:10 | 4.2629 | 0.74345 | 0.21955 | 1.3591 | 63.2385 | 27.7508 | 1.3447 | 0.23259 | 441.4479 | 27.62 | 48.06
2021-01-10 14:15 | 4.11 | 0.7134 | 0.18818 | 1.2817 | 61.8102 | 11.0346 | 1.3373 | 0.29073 | 440.925 | 27.63 | 47.9
2021-01-10 14:20 | 4.1352 | 0.75155 | 0.19026 | 1.3443 | 53.541 | 12.2758 | 1.3445 | 0.29798 | 443.0731 | 27.63 | 47.73
2021-01-10 14:25 | 3.9316 | 0.81702 | 0.19653 | 1.4489 | 61.4295 | 22.3223 | 1.3445 | 0.31978 | 440.5005 | 27.64 | 47.65
2021-01-10 14:30 | 3.5497 | 0.83743 | 0.20906 | 1.4927 | 71.3298 | 20.204 | 1.3372 | 0.24709 | 441.0388 | 27.65 | 47.48
2021-01-10 14:35 | 3.5738 | 0.75667 | 0.21734 | 1.3772 | 67.5581 | 27.6948 | 1.3439 | 0.23246 | 440.6498 | 27.67 | 46.4
2021-01-10 14:40 | 3.4734 | 0.71469 | 0.22161 | 1.3171 | 60.5922 | 14.9623 | 1.3372 | 0.20349 | 441.4616 | 27.72 | 47.31
2021-01-10 14:45 | 3.2828 | 0.67928 | 0.21954 | 1.2608 | 63.1115 | 36.2178 | 1.3446 | 0.19624 | 440.3664 | 27.72 | 47.53
2021-01-10 14:50 | 3.4358 | 0.74074 | 0.26138 | 1.3968 | 52.7745 | 12.7253 | 1.3447 | 0.18899 | 441.3817 | 27.72 | 47.79
2021-01-10 14:55 | 3.2836 | 0.8691 | 0.27187 | 1.6041 | 77.4837 | 36.0742 | 1.3449 | 0.20355 | 440.2122 | 27.75 | 48.11
2021-01-10 15:00 | 2.8513 | 0.91971 | 0.25936 | 1.667 | 81.3442 | 33.0041 | 1.3451 | 0.23267 | 439.561 | 27.79 | 48.38
2021-01-10 15:05 | 3.3221 | 0.8869 | 0.28026 | 1.6397 | 65.423 | 16.3837 | 1.3377 | 0.23992 | 441.1796 | 27.79 | 48.19
2021-01-10 15:10 | 2.8893 | 0.86506 | 0.24052 | 1.5644 | 52.6638 | 19.6726 | 1.3377 | 0.21084 | 440.654 | 27.79 | 48.17
2021-01-10 15:15 | 2.2913 | 0.69457 | 0.20917 | 1.2738 | 49.3996 | -4.2974 | 1.3379 | 0.19632 | 439.0573 | 27.77 | 48.46
2021-01-10 15:20 | 2.0622 | 0.6441 | 0.19872 | 1.186 | 42.9245 | 18.6057 | 1.3306 | 0.17451 | 441.2014 | 27.74 | 48.64
2021-01-10 15:25 | 2.024 | 0.62773 | 0.18198 | 1.1421 | 35.0935 | 13.7889 | 1.3306 | 0.18178 | 441.7271 | 27.74 | 48.66
2021-01-10 15:30 | 2.7113 | 0.60177 | 0.19871 | 1.1211 | 53.9511 | 19.5723 | 1.3306 | 0.25448 | 440.7211 | 27.72 | 48.58
2021-01-10 15:35 | [9 empty] | 27.71 | 48.45
2021-01-10 15:40 | 4.7482 | 0.78739 | 0.21754 | 1.4245 | 45.7046 | 20.9174 | 1.3379 | 0.34175 | 442.29 | 27.72 | 48.69
2021-01-10 15:45 | 3.6535 | 0.6755 | 0.2029 | 1.2383 | 50.0639 | 6.9352 | 1.3379 | 0.34175 | 439.6094 | 27.74 | 48.67
2021-01-10 15:50 | 2.4698 | 0.58957 | 0.23011 | 1.1317 | 53.1439 | 13.3522 | 1.3235 | 0.27633 | 441.1148 | 27.77 | 48.81
2021-01-10 15:55 | 2.3553 | 0.63872 | 0.23012 | 1.2092 | 43.0622 | 21.1848 | 1.3235 | 0.21089 | 441.1032 | 27.77 | 48.88
2021-01-10 16:00 | 2.5464 | 0.76978 | 0.20293 | 1.3829 | 45.2237 | 15.5125 | 1.3236 | 0.20363 | 440.567 | 27.76 | 49.04
2021-01-10 16:05 | 2.3683 | 0.76027 | 0.21968 | 1.3851 | 44.0855 | 31.7094 | 1.3237 | 0.23273 | 442.1124 | 27.77 | 49.17
2021-01-10 16:10 | 2.241 | 0.76438 | 0.22387 | 1.3976 | 38.6367 | 4.9709 | 1.3237 | 0.25456 | 441.5897 | 27.76 | 49.25
2021-01-10 16:15 | 2.8521 | 0.75617 | 0.22596 | 1.385 | 42.5266 | 22.2768 | 1.3309 | 0.29819 | 439.502 | 27.75 | 49.2
2021-01-10 16:20 | 3.1704 | 0.83125 | 0.25107 | 1.5252 | 43.6781 | 13.1401 | 1.3309 | 0.2691 | 441.0547 | 27.77 | 49.17
2021-01-10 16:25 | 3.145 | 0.85583 | 0.24898 | 1.5608 | 48.7008 | 52.3882 | 1.331 | 0.25456 | 440.5031 | 27.78 | 49.19
2021-01-10 16:30 | 3.5911 | 0.77266 | 0.24273 | 1.4271 | 56.2248 | 27.6081 | 1.3311 | 0.25459 | 438.3364 | 27.78 | 49.5
2021-01-10 16:35 | 3.6551 | 0.74405 | 0.23019 | 1.3707 | 66.2546 | 41.8129 | 1.3312 | 0.27643 | 440.4164 | 27.78 | 49.71
2021-01-10 16:40 | 3.719 | 0.80554 | 0.21765 | 1.4524 | 71.1595 | 66.6662 | 1.3313 | 0.26917 | 439.3179 | 27.79 | 49.84
2021-01-10 16:45 | 2.7383 | 0.74 | 0.20928 | 1.3436 | 69.0606 | 39.3293 | 1.3313 | 0.19642 | 439.8755 | 27.77 | 49.9
2021-01-10 16:50 | 2.7767 | 0.63355 | 0.24069 | 1.2118 | 42.3174 | 29.2645 | 1.3314 | 0.14551 | 439.3474 | 27.75 | 50.13
2021-01-10 16:55 | 2.4967 | 0.78519 | 0.22815 | 1.4317 | 34.2099 | 11.1078 | 1.317 | 0.16007 | 440.3761 | 27.74 | 50.42
2021-01-10 17:00 | 1.8852 | 0.75787 | 0.20094 | 1.3626 | 37.8476 | 27.2189 | 1.317 | 0.1528 | 440.9226 | 27.73 | 50.43
2021-01-10 17:05 | 2.2672 | 0.71139 | 0.1779 | 1.2704 | 28.4093 | 10.037 | 1.3242 | 0.16006 | 440.482 | 27.69 | 50.37
2021-01-10 17:10 | 2.5474 | 0.92847 | 0.1779 | 1.6011 | 34.2063 | 17.6279 | 1.3314 | 0.24736 | 441.0386 | 27.68 | 50.32
2021-01-10 17:15 | 3.7322 | 0.87119 | 0.16535 | 1.5028 | 33.8317 | 25.17 | 1.3315 | 0.31286 | 440.5074 | 27.66 | 50.57
2021-01-10 17:20 | 6.3565 | 0.8248 | 0.20095 | 1.4652 | 40.5999 | 39.5808 | 1.3388 | 0.50206 | 439.4445 | 27.65 | 50.72
2021-01-10 17:25 | 6.522 | 0.84391 | 0.21769 | 1.5113 | 40.2531 | 35.2699 | 1.3388 | 0.50205 | 441.0489 | 27.64 | 50.73
2021-01-10 17:30 | 5.5671 | 0.86037 | 0.25957 | 1.5784 | 41.4694 | 34.0601 | 1.3389 | 0.42933 | 440.4966 | 27.63 | 50.99
2021-01-10 17:35 | 4.0384 | 0.78799 | 0.18421 | 1.3921 | 36.3634 | 17.9779 | 1.3316 | 0.29835 | 441.0546 | 27.61 | 51.05
2021-01-10 17:40 | 3.4394 | 0.65001 | 0.20304 | 1.1994 | 27.1076 | 4.4636 | 1.3243 | 0.22556 | 441.6589 | 27.58 | 50.95
2021-01-10 17:45 | 3.0575 | 0.64598 | 0.20306 | 1.1953 | 27.9357 | 19.3134 | 1.3244 | 0.23286 | 442.1758 | 27.56 | 51.26
2021-01-10 17:50 | 2.6756 | 0.64877 | 0.22192 | 1.2164 | 22.8625 | 17.6845 | 1.3245 | 0.1965 | 441.1176 | 27.53 | 51.62
2021-01-10 17:55 | 2.5481 | 0.59549 | 0.19679 | 1.1096 | 20.9559 | 15.2889 | 1.3318 | 0.21105 | 442.2148 | 27.51 | 51.62
2021-01-10 18:00 | 1.86 | 0.52033 | 0.19678 | 0.99645 | 13.9728 | 18.9769 | 1.3317 | 0.10915 | 440.1659 | 27.49 | 51.45
2021-01-10 18:05 | 1.9236 | 0.53122 | 0.19258 | 1.0069 | 15.6842 | 19.7607 | 1.3316 | 0.11642 | 442.3641 | 27.45 | 51.43
2021-01-10 18:10 | 1.7833 | 0.5189 | 0.1214 | 0.9168 | 9.0288 | 23.6625 | 1.3242 | 0.13825 | 443.5226 | 27.4 | 51.42
2021-01-10 18:15 | 1.8978 | 0.51749 | 0.11511 | 0.90834 | 9.9145 | 10.7806 | 1.3314 | 0.16733 | 442.0509 | 27.35 | 51.31
2021-01-10 18:20 | 2.5224 | 0.57358 | 0.15491 | 1.0341 | 18.192 | 15.5218 | 1.3389 | 0.18192 | 441.9939 | 27.33 | 51.9
2021-01-10 18:25 | 3.5673 | 0.74297 | 0.18423 | 1.3231 | 18.3051 | 17.6732 | 1.3463 | 0.29109 | 441.4532 | 27.32 | 52.09
2021-01-10 18:30 | 3.9749 | 0.70609 | 0.19678 | 1.2812 | 19.3139 | 26.9274 | 1.3463 | 0.34202 | 443.5903 | 27.31 | 52.09
2021-01-10 18:35 | 3.2358 | 0.62137 | 0.17584 | 1.1283 | 13.3201 | 8.6015 | 1.3316 | 0.24741 | 440.5171 | 27.26 | 52.06
2021-01-10 18:40 | 2.6116 | 0.6924 | 0.19049 | 1.2539 | -0.22421 | 7.5927 | 1.3389 | 0.23286 | 444.288 | 27.21 | 52.27
2021-01-10 18:45 | 3.4654 | 0.62415 | 0.14864 | 1.1033 | 3.8323 | 21.1183 | 1.3608 | 0.34931 | 442.7445 | 27.16 | 52.6
2021-01-10 18:50 | 3.0075 | 0.60519 | 0.14868 | 1.0784 | 2.3244 | 2.8546 | 1.3539 | 0.33484 | 443.1874 | 27.14 | 53.38
2021-01-10 18:55 | 2.6892 | 0.50825 | 0.14241 | 0.91937 | -3.7929 | 14.5496 | 1.3541 | 0.36399 | 443.2171 | 27.09 | 53.81
2021-01-10 19:00 | 1.8736 | 0.52329 | 0.17592 | 0.97804 | -0.76472 | 24.8074 | 1.3468 | 0.24752 | 441.1161 | 27.07 | 53.95
2021-01-10 19:05 | 1.3512 | 0.57801 | 0.19479 | 1.0829 | 0.61184 | 8.4944 | 1.347 | 0.10921 | 443.1843 | 27.07 | 54.26
2021-01-10 19:10 | 1.4915 | 0.95524 | 0.25137 | 1.7156 | -2.6006 | 7.5672 | 1.3398 | 0.10194 | 442.097 | 27.06 | 54.56
2021-01-10 19:15 | 1.7211 | 0.83775 | 0.18016 | 1.4643 | 2.4885 | 37.9805 | 1.3399 | 0.11651 | 443.7232 | 27.02 | 54.82
2021-01-10 19:20 | 1.7594 | 0.67516 | 0.16341 | 1.1983 | -2.4275 | -6.4256 | 1.34 | 0.10195 | 443.1696 | 27.02 | 54.97
2021-01-10 19:25 | 1.7465 | 0.52752 | 0.16549 | 0.97618 | 5.028 | 25.4967 | 1.3399 | 0.10923 | 443.819 | 26.96 | 54.97
2021-01-10 19:30 | 2.0272 | 0.5098 | 0.15084 | 0.93228 | 0.82617 | 22.1129 | 1.3327 | 0.10924 | 443.8348 | 26.92 | 55.37
2021-01-10 19:35 | 1.5808 | 0.53024 | 0.16758 | 0.97826 | 2.9066 | 23.3853 | 1.3398 | 0.11651 | 441.8244 | 26.88 | 55.19
2021-01-10 19:40 | 2.5374 | 0.58367 | 0.15086 | 1.0455 | 6.0185 | 24.9307 | 1.3401 | 0.11653 | 443.8614 | 26.87 | 55.83
2021-01-10 19:45 | 3.8122 | 0.54262 | 0.18437 | 1.0161 | 2.244 | 22.5623 | 1.34 | 0.12381 | 442.8674 | 26.85 | 55.67
2021-01-10 19:50 | 3.2261 | 0.58506 | 0.18648 | 1.0854 | 8.2222 | 17.4032 | 1.3475 | 0.16752 | 443.3719 | 26.83 | 56.08
2021-01-10 19:55 | 2.4099 | 0.60689 | 0.14457 | 1.0748 | 12.6894 | 15.3415 | 1.3401 | 0.16023 | 442.373 | 26.81 | 55.95
2021-01-10 20:00 | 2.2444 | 0.71771 | 0.15507 | 1.2552 | 9.0492 | 23.0973 | 1.333 | 0.1384 | 443.9262 | 26.79 | 56.43
2021-01-10 20:05 | 1.849 | 0.54953 | 0.14249 | 0.98693 | 2.0913 | 7.8041 | 1.3329 | 0.10197 | 444.0218 | 26.74 | 56.46
2021-01-10 20:10 | 1.4154 | 0.48799 | 0.15295 | 0.89886 | 3.3867 | -4.8352 | 1.3329 | 0.06555 | 444.1851 | 26.65 | 56.57
2021-01-10 20:15 | 1.5301 | 0.47841 | 0.13619 | 0.86952 | -5.4268 | 16.5863 | 1.3328 | 0.050983 | 444.8243 | 26.58 | 56.77
2021-01-10 20:20 | 1.2114 | 0.70261 | 0.132 | 1.209 | -2.1014 | 4.2743 | 1.3256 | 0.050985 | 443.7896 | 26.55 | 56.99
2021-01-10 20:25 | 0.86707 | 0.58093 | 0.13619 | 1.0246 | 3.3969 | 23.0945 | 1.3329 | 0.050983 | 444.3359 | 26.49 | 57.15
2021-01-10 20:30 | 0.87984 | 0.41692 | 0.11524 | 0.75431 | 4.06 | 11.4762 | 1.3402 | 0.043701 | 445.43 | 26.46 | 57.33
2021-01-10 20:35 | 0.68851 | 0.3376 | 0.09428 | 0.61177 | 8.5171 | -9.8737 | 1.3401 | 0.036414 | 445.043 | 26.39 | 57.31
2021-01-10 20:40 | 1.0328 | 0.30482 | 0.096382 | 0.56363 | 5.8757 | 13.0878 | 1.3329 | 0.029134 | 444.5226 | 26.36 | 57.63
2021-01-10 20:45 | 0.79058 | 0.31303 | 0.088002 | 0.56782 | 12.5064 | 31.4292 | 1.3329 | 0.065551 | 444.5644 | 26.33 | 57.75
2021-01-10 20:50 | 0.79058 | 0.44015 | 0.096383 | 0.77107 | 4.9169 | 17.6376 | 1.3329 | 0.058268 | 446.7014 | 26.32 | 57.8
2021-01-10 20:55 | 0.71407 | 0.41281 | 0.088001 | 0.72077 | 7.4977 | 7.8343 | 1.3329 | 0.050984 | 445.7027 | 26.28 | 57.91
2021-01-10 21:00 | 0.72681 | 0.44698 | 0.10686 | 0.792 | 3.2643 | 4.6006 | 1.3401 | 0.06555 | 445.754 | 26.25 | 57.97
2021-01-10 21:05 | 0.85426 | 0.30343 | 0.079614 | 0.54473 | 7.1809 | 11.6588 | 1.3473 | 0.080112 | 445.8704 | 26.19 | 58
2021-01-10 21:10 | 1.4917 | 0.26652 | 0.062851 | 0.47138 | 14.0247 | -2.142 | 1.34 | 0.13109 | 446.5528 | 26.1 | 58.2
2021-01-10 21:15 | 2.1802 | 0.28292 | 0.07961 | 0.51328 | 7.4356 | 16.8499 | 1.34 | 0.13109 | 445.0076 | 26.07 | 58.27
2021-01-10 21:20 | 1.4408 | 0.23374 | 0.081713 | 0.43999 | 5.0391 | 0.040802 | 1.3328 | 0.094682 | 446.075 | 26.04 | 58.64
2021-01-10 21:25 | 1.1604 | 0.17224 | 0.058669 | 0.32268 | 7.5489 | 13.0168 | 1.3329 | 0.05827 | 445.0578 | 25.99 | 59
2021-01-10 21:30 | 1.2624 | 0.1572 | 0.054478 | 0.29544 | 5.3454 | 20.0556 | 1.3329 | 0.058269 | 446.7299 | 25.94 | 59.16
2021-01-10 21:35 | 0.8161 | 0.12439 | 0.064955 | 0.25563 | 4.0397 | -1.2854 | 1.3329 | 0.065553 | 447.32 | 25.9 | 59.31
2021-01-10 21:40 | 0.5738 | 0.11619 | 0.073335 | 0.25143 | -0.23462 | 3.2949 | 1.3329 | 0.043701 | 446.8901 | 25.84 | 59.44
2021-01-10 21:45 | 0.68856 | 0.18043 | 0.083811 | 0.36039 | -1.2751 | 8.7728 | 1.3329 | 0.043701 | 445.856 | 25.82 | 59.51
2021-01-10 21:50 | 0.81608 | 0.22965 | 0.079621 | 0.43163 | 5.3555 | -4.8149 | 1.3329 | 0.065552 | 444.803 | 25.81 | 59.57
2021-01-10 21:55 | 0.4845 | 0.14761 | 0.060758 | 0.28703 | 4.2126 | 6.5892 | 1.3328 | 0.05098 | 446.5027 | 25.77 | 59.42
2021-01-10 22:00 | 0.56095 | 0.24054 | 0.077512 | 0.44831 | 9.1792 | 4.4978 | 1.3326 | 0.050975 | 446.6159 | 25.72 | 59.34
2021-01-10 22:05 | 0.47164 | 0.25007 | 0.07331 | 0.45662 | 2.3352 | 3.8139 | 1.3324 | 0.029124 | 447.277 | 25.68 | 59.02
2021-01-10 22:10 | 0.45886 | 0.26098 | 0.064927 | 0.46496 | 10.7985 | 11.2777 | 1.3396 | 0.043683 | 447.414 | 25.61 | 59.05
2021-01-10 22:15 | 0.49709 | 0.21725 | 0.048171 | 0.38118 | 4.9046 | -3.7728 | 1.3396 | 0.043683 | 447.4942 | 25.56 | 59.19
2021-01-10 22:20 | 0.48434 | 0.17763 | 0.046077 | 0.31835 | 4.6089 | -4.1705 | 1.3323 | 0.029122 | 446.4744 | 25.53 | 59.29
2021-01-10 22:25 | 0.57356 | 0.27873 | 0.060737 | 0.48799 | 3.2323 | -5.8018 | 1.3323 | 0.036402 | 446.5717 | 25.47 | 59.45
2021-01-10 22:30 | 0.7393 | 0.41403 | 0.077497 | 0.71213 | 0.93815 | 10.6969 | 1.3324 | 0.050966 | 446.5265 | 25.48 | 59.62
2021-01-10 22:35 | 0.47162 | 0.1995 | 0.050268 | 0.35607 | 6.0673 | -0.96874 | 1.3324 | 0.043685 | 447.1194 | 25.44 | 59.76
2021-01-10 22:40 | 0.42066 | 0.18448 | 0.046082 | 0.32886 | 3.0798 | -1.5297 | 1.3398 | 0.036406 | 447.7277 | 25.37 | 60.21
2021-01-10 22:45 | 0.50993 | 0.18449 | 0.04818 | 0.33098 | 2.5191 | -3.6919 | 1.3399 | 0.036409 | 446.6884 | 25.33 | 60.58
2021-01-10 22:50 | 0.40795 | 0.1353 | 0.037707 | 0.24719 | 2.3865 | 0.8567 | 1.3399 | 0.021846 | 446.759 | 25.28 | 60.79
2021-01-10 22:55 | 0.49723 | 0.18314 | 0.031425 | 0.31215 | 1.0812 | -3.7534 | 1.34 | 0.050977 | 446.7542 | 25.26 | 61.1
2021-01-10 23:00 | 0.44623 | 0.097039 | 0.027235 | 0.17807 | 12.4741 | 16.6457 | 1.3327 | 0.02913 | 447.3018 | 25.25 | 61.14
2021-01-10 23:05 | 0.38248 | 0.094305 | 0.031425 | 0.17807 | -0.84657 | -10.73 | 1.34 | 0.021848 | 447.9088 | 25.2 | 61.33
2021-01-10 23:10 | 0.45898 | 0.10251 | 0.02514 | 0.18226 | 1.7339 | 2.2235 | 1.34 | 0.02913 | 446.8902 | 25.17 | 61.42
2021-01-10 23:15 | 0.44622 | 0.16264 | 0.033519 | 0.28281 | 4.4571 | -1.1831 | 1.3545 | 0.029129 | 447.5105 | 25.12 | 61.52
2021-01-10 23:20 | 0.47171 | 0.123 | 0.039803 | 0.22834 | -6.1398 | -11.1884 | 1.3472 | 0.021846 | 448.5845 | 25.12 | 61.47
2021-01-10 23:25 | 0.42071 | 0.13803 | 0.035613 | 0.24719 | -0.42836 | 6.3131 | 1.3545 | 0.03641 | 448.102 | 25.09 | 61.54
2021-01-10 23:30 | 0.33147 | 0.1066 | 0.035613 | 0.19901 | 0.44876 | 15.2373 | 1.3472 | 0.03641 | 447.5207 | 25.12 | 61.45
2021-01-10 23:35 | 0.28046 | 0.14076 | 0.041895 | 0.25556 | -2.2641 | -19.5097 | 1.3544 | 0.036409 | 447.0843 | 25.07 | 61.48
2021-01-10 23:40 | 0.33146 | 0.1722 | 0.023043 | 0.28699 | 5.5379 | -0.59153 | 1.3617 | 0.050973 | 446.0376 | 25.05 | 61.62
2021-01-10 23:45 | 0.50992 | 0.09156 | 0.023042 | 0.16129 | -1.0606 | -2.2844 | 1.3617 | 0.029126 | 446.7089 | 24.97 | 61.79
2021-01-10 23:50 |  | 0.077894 | 0.025137 | 0.14454 | 5.3439 | 8.0056 | 1.3616 | 0.029126 | 447.3968 | 24.87 | 62.13
2021-01-10 23:55 | 0.50995 | 0.11343 | 0.029328 | 0.20111 | -2.8761 | 5.0485 | 1.3617 | 0.03641 | 447.4561 | 24.81 | 62.57
2021-01-11 | 0.33146 | 0.1681 | 0.071225 | 0.32679 | 3.2432 | 23.0901 | 1.369 | 0.021846 | 448.5282 | 24.81 | 62.54
2021-01-11 00:05 | 0.26769 | 0.077891 | 0.035609 | 0.15291 | 3.2429 | -2.6412 | 1.3689 | 0.014562 | 448.1439 | 24.74 | 62.49
2021-01-11 00:10 | 0.26767 | 0.072419 | 0.035606 | 0.14661 | 2.743 | -17.3656 | 1.3615 | 0.014561 | 449.901 | 24.66 | 62.55
2021-01-11 00:15 | 0.26767 | 0.06422 | 0.031417 | 0.12986 | 0.73418 | -10.1154 | 1.3615 | 0.014561 | 448.9115 | 24.61 | 62.71
2021-01-11 00:20 | 0.15297 | 0.060126 | 0.031419 | 0.12358 | -0.68325 | 15.9084 | 1.3616 | 0.021843 | 449.0116 | 24.58 | 62.99
2021-01-11 00:25 | 0.14022 | 0.054659 | 0.02723 | 0.11101 | -5.4659 | -11.2887 | 1.3616 | 0.014562 | 449.0777 | 24.54 | 63.1
2021-01-11 00:30 | 0.12747 | 0.034162 | 0.025135 | 0.0775 | -1.7438 | -5.6699 | 1.3616 | 0.0072812 | 448.5985 | 24.5 | 63.29
2021-01-11 00:35 | 0.10197 | 0.028695 | 0.02304 | 0.067025 | -6.8832 | 2.6207 | 1.3615 | 0.014562 | 447.6223 | 24.45 | 63.36
2021-01-11 00:40 | 0.16571 | 0.020497 | 0.018851 | 0.050269 | -4.3237 | -17.3048 | 1.3542 | 0.0072809 | 447.6533 | 24.43 | 63.43
2021-01-11 00:45 | 0.14022 | 0.066959 | 0.025136 | 0.12777 | -1.4583 | 5.7516 | 1.3543 | 0.029125 | 449.7662 | 24.43 | 63.6
2021-01-11 00:50 | 0.11472 | 0.046461 | 0.023041 | 0.092163 | -1.1217 | -0.93819 | 1.3543 | 0.021843 | 447.6366 | 24.43 | 63.55
2021-01-11 00:55 | 0.089228 | 0.035528 | 0.027229 | 0.081688 | -4.8846 | -2.8043 | 1.3543 | 0.007281 | 447.1549 | 24.4 | 63.61
2021-01-11 01:00 | 0.16571 | 0.046461 | 0.020946 | 0.092164 | -4.6298 | -8.505 | 1.3616 | 0.014562 | 448.2701 | 24.36 | 63.86
2021-01-11 01:05 |  |  |  |  | 1.7438 | -3.0185 |  |  | 447.2598 | 24.33 | 63.88
2021-01-11 01:10 |  |  |  |  | 2.3251 | -9.1168 |  |  | 448.868 | 24.32 | 63.99
2021-01-11 01:15 |  |  |  |  | -0.97891 | -4.2521 |  |  | 449.5264 | 24.26 | 63.98
2021-01-11 01:20 |  |  |  |  | 4.8026 | 0.53023 |  |  | 447.4465 | 24.23 | 64
2021-01-11 01:25 |  |  |  |  | 1.0503 | 5.7203 |  |  | 448.0135 | 24.21 | 64.06
2021-01-11 01:30 |  |  |  |  | -4.2417 | -13.1433 |  |  | 448.0204 | 24.21 | 64.01
2021-01-11 01:35 |  |  |  |  | -3.7319 | -0.69335 |  |  | 448.6363 | 24.16 | 64.16
2021-01-11 01:40 |  |  |  |  | -0.89726 | 2.131 |  |  | 448.172 | 24.12 | 64.24
2021-01-11 01:45 |  |  |  |  | -0.29568 | -2.7019 |  |  | 449.2905 | 24.09 | 64.33
2021-01-11 01:50 |  |  |  |  | -9.2787 | -10.6756 |  |  | 448.1895 | 24.1 | 64.41
2021-01-11 01:55 |  |  |  |  | -7.0048 | -9.1765 |  |  | 449.4174 | 24.06 | 64.42
2021-01-11 02:00 |  |  |  |  | -6.332 | 2.0495 |  |  | 446.763 | 24.04 | 64.59
2021-01-11 02:05 |  |  |  |  | -3.2323 | -5.9548 |  |  | 447.3787 | 23.98 | 64.89
2021-01-11 02:10 | 0.012746 | 0.058754 | 0.0377 | 0.12567 | 4.5478 | 10.5742 | 1.4343 | -0.065525 | 447.9485 | 23.95 | 65.08
2021-01-11 02:15 | 0.063734 | 0.061491 | 0.027229 | 0.12149 | 6.4244 | -2.3862 | 1.4052 | -0.029124 | 447.9051 | 23.96 | 65.25
2021-01-11 02:20 | 0.17846 | 0.050561 | 0.02723 | 0.10473 | 11.3502 | 0.68326 | 1.3762 | 0 | 449.4322 | 24 | 65.21
2021-01-11 02:25 | 0.15296 | 0.049191 | 0.035606 | 0.11101 | 4.8538 | -4.966 | 1.3761 | 0.014561 | 448.3864 | 23.95 | 65.21
2021-01-11 02:30 | 0.089226 | 0.047825 | 0.031418 | 0.10473 | 1.8253 | -0.87696 | 1.3688 | 0.014562 | 450.0134 | 23.93 | 65.35
2021-01-11 02:35 | 0.050987 | 0.047826 | 0.031418 | 0.10473 | 4.7724 | -11.9514 | 1.3688 | 0.036405 | 448.4437 | 23.9 | 65.54
2021-01-11 02:40 | 0.10198 | 0.047827 | 0.031419 | 0.10473 | 1.2033 | -1.9579 | 1.3688 | 0.036406 | 448.437 | 23.9 | 65.59
2021-01-11 02:45 | 0.14022 | 0.057391 | 0.039797 | 0.12986 | -3.5385 | 16.4281 | 1.3688 | 0.043686 | 448.4587 | 23.89 | 65.58
2021-01-11 02:50 | 0.11472 | 0.16807 | 0.029323 | 0.28695 | 8.7186 | -8.9124 | 1.3761 | 0.014562 | 448.9446 | 23.93 | 65.34
2021-01-11 02:55 | 0.08922 | 0.091545 | 0.035604 | 0.17593 | 4.201 | 6.7909 | 1.3833 | 0.029121 | 448.9744 | 23.93 | 65.12
2021-01-11 03:00 | [9 empty] | 23.91 | 65.17
2021-01-11 03:05 | 0.38237 | 0.18855 | 0.041887 | 0.33091 | -0.12236 | -14.2548 | 1.3978 | 0.043682 | 448.9894 | 23.92 | 65.16
2021-01-11 03:10 | 0.2804 | 0.15576 | 0.050264 | 0.28902 | 2.2738 | -6.5562 | 1.3978 | 0.036401 | 448.5524 | 23.92 | 65.02
2021-01-11 03:15 | 0.17843 | 0.15439 | 0.041886 | 0.27854 | 7.6879 | 12.5004 | 1.3978 | 0.02912 | 449.0965 | 23.92 | 64.95
2021-01-11 03:20 | 0.1402 | 0.11067 | 0.029321 | 0.19896 | 2.906 | -5.3429 | 1.4051 | 0.043681 | 448.6083 | 23.88 | 65.21
2021-01-11 03:25 | 0.20393 | 0.1421 | 0.035604 | 0.25342 | -1.7946 | -14.8765 | 1.4124 | 0.043681 | 449.1593 | 23.87 | 65.24
2021-01-11 03:30 | 0.21666 | 0.11886 | 0.050261 | 0.23246 | -2.8141 | 11.8272 | 1.4123 | 0.036399 | 449.7184 | 23.87 | 65.06
2021-01-11 03:35 | 0.20393 | 0.17626 | 0.050264 | 0.32044 | -1.764 | -4.3845 | 1.4342 | 0.050962 | 449.1416 | 23.88 | 65.22
2021-01-11 03:40 | 0.48432 | 0.17352 | 0.048169 | 0.31205 | 1.2439 | -0.50982 | 1.4342 | 0.065521 | 449.1334 | 23.89 | 65.13
2021-01-11 03:45 | 0.53531 | 0.16532 | 0.037698 | 0.29111 | 2.5899 | 4.0786 | 1.4342 | 0.065522 | 449.6941 | 23.87 | 65.24
2021-01-11 03:50 | 0.63725 | 0.25276 | 0.050262 | 0.4377 | 2.2839 | -1.4274 | 1.4269 | 0.072799 | 447.5904 | 23.86 | 65.13
2021-01-11 03:55 | 0.68822 | 0.31287 | 0.075393 | 0.55497 | 6.9536 | -6.7497 | 1.4341 | 0.094639 | 447.5007 | 23.92 | 64.89
2021-01-11 04:00 | 0.61174 | 0.2992 | 0.06492 | 0.52145 | 9.9407 | 9.2882 | 1.4414 | 0.080076 | 448.5075 | 23.97 | 64.6
2021-01-11 04:05 | 0.9813 | 0.45767 | 0.067012 | 0.77063 | 10.022 | 23.8468 | 1.4559 | 0.094633 | 447.912 | 24.02 | 64.3
2021-01-11 04:10 | 0.73915 | 0.41394 | 0.096328 | 0.72874 | 16.3632 | 7.7789 | 1.4559 | 0.087352 | 447.8444 | 24.07 | 64.05
2021-01-11 04:15 | 0.66271 | 0.51506 | 0.1424 | 0.934 | 17.047 | 30.4949 | 1.4632 | 0.065517 | 446.6367 | 24.15 | 63.88
2021-01-11 04:20 | 0.63724 | 0.57928 | 0.15497 | 1.0429 | 25.3059 | 12.1534 | 1.456 | 0.080078 | 448.6128 | 24.25 | 63.57
2021-01-11 04:25 | 0.65003 | 0.79111 | 0.15289 | 1.3655 | 21.7901 | 13.0312 | 1.4561 | 0.087364 | 446.8406 | 24.34 | 63.48
2021-01-11 04:30 | 0.86671 | 0.83893 | 0.15079 | 1.4346 | 26.7863 | 9.7275 | 1.4342 | 0.11649 | 447.7888 | 24.42 | 63.17
2021-01-11 04:35 | 0.86666 | 0.86348 | 0.16964 | 1.4953 | 36.2265 | 50.3277 | 1.4414 | 0.12376 | 447.2171 | 24.46 | 62.86
2021-01-11 04:40 | 1.0578 | 0.86075 | 0.20733 | 1.5267 | 48.1457 | 56.3331 | 1.4706 | 0.13832 | 446.4749 | 24.54 | 62.62
2021-01-11 04:45 | 1.5802 | 0.80739 | 0.23663 | 1.4742 | 65.2483 | 70.3255 | 1.4704 | 0.16742 | 447.0805 | 24.58 | 62.1
2021-01-11 04:50 | 1.8224 | 0.9577 | 0.2492 | 1.7193 | 75.3033 | 69.1453 | 1.485 | 0.21839 | 446.3671 | 24.63 | 62.09
2021-01-11 04:55 | 1.6058 | 1.7569 | 0.29318 | 2.9884 | 63.4974 | 50.4472 | 1.4923 | 0.18199 | 445.1919 | 24.7 | 61.85
2021-01-11 05:00 | 1.4783 | 1.9126 | 0.37694 | 3.3087 | 61.7736 | 37.7126 | 1.4923 | 0.18927 | 446.1156 | 24.8 | 61.44
2021-01-11 05:05 | 1.8225 | 1.6832 | 0.37904 | 2.9611 | 56.728 | 43.7083 | 1.4778 | 0.21111 | 446.0173 | 24.86 | 61.28
2021-01-11 05:10 | 1.8479 | 2.1081 | 0.46909 | 3.7004 | 58.9404 | 65.4146 | 1.4923 | 0.20383 | 445.8974 | 24.94 | 60.99
2021-01-11 05:15 | 2.7019 | 2.5289 | 0.5801 | 4.4586 | 84.2684 | 78.936 | 1.5069 | 0.24023 | 445.1727 | 25.06 | 60.64
2021-01-11 05:20 | 3.5049 | 3.4594 | 0.72253 | 6.0232 | 114.4518 | 94.4877 | 1.5143 | 0.31304 | 441.6635 | 25.26 | 60.02
2021-01-11 05:25 | 2.9184 | 3.1353 | 0.601 | 5.409 | 148.1656 | 127.4695 | 1.4995 | 0.48043 | 444.0895 | 25.45 | 59.04
2021-01-11 05:30 | 3.0457 | 3.1161 | 0.71407 | 5.4906 | 150.4978 | 116.6608 | 1.5068 | 0.54594 | 442.3217 | 25.57 | 58.57
2021-01-11 05:35 | 3.4661 | 3.3018 | 0.92553 | 5.9887 | 139.5221 | 111.3139 | 1.5213 | 0.39306 | 442.1332 | 25.71 | 57.96
2021-01-11 05:40 | 3.6573 | 2.7567 | 0.68891 | 4.9145 | 136.1274 | 101.3947 | 1.4995 | 0.34939 | 441.9556 | 25.83 | 57.55
2021-01-11 05:45 | 6.1167 | 3.0108 | 0.69937 | 5.3144 | 122.7102 | 112.893 | 1.5067 | 0.53135 | 441.8416 | 25.91 | 57.25
2021-01-11 05:50 | 6.8174 | 3.5899 | 0.78311 | 6.2879 | 124.8788 | 117.5492 | 1.514 | 0.61869 | 440.124 | 26 | 56.88
2021-01-11 05:55 | 5.8368 | 3.2159 | 0.73922 | 5.6687 | 139.1142 | 109.2727 | 1.5068 | 0.495 | 442.5582 | 26.12 | 56.78
2021-01-11 06:00 | 5.1483 | 3.7198 | 0.67007 | 6.3741 | 142.1947 | 132.7341 | 1.5067 | 0.73518 | 443.0571 | 26.16 | 56.47
2021-01-11 06:05 | 5.6835 | 3.907 | 0.6952 | 6.6819 | 170.1901 | 164.5525 | 1.5068 | 0.74974 | 440.8118 | 26.24 | 56.22
2021-01-11 06:10 | 4.5241 | 3.4318 | 0.66383 | 5.9242 | 190.3743 | 168.4649 | 1.4923 | 0.56779 | 441.1602 | 26.35 | 55.99
2021-01-11 06:15 | 4.0905 | 3.1446 | 0.69727 | 5.5175 | 113.0654 | 159.9797 | 1.4921 | 0.51679 | 442.1693 | 26.41 | 55.56
2021-01-11 06:20 | 3.976 | 2.8402 | 0.64078 | 4.9943 | 121.3504 | 110.7476 | 1.5505 | 0.44403 | 441.5092 | 26.48 | 55.5
2021-01-11 06:25 | 4.0139 | 2.6487 | 0.60303 | 4.663 | 116.1705 | 90.3492 | 1.594 | 0.42215 | 440.9615 | 26.52 | 55.1
2021-01-11 06:30 | 4.9696 | 3.0653 | 0.58419 | 5.2828 | 122.5641 | 99.2399 | 1.5212 | 0.43672 | 440.8662 | 26.58 | 54.95
2021-01-11 06:35 | 4.3201 | 2.6079 | 0.45022 | 4.4457 | 124.3478 | 98.524 | 1.485 | 0.50226 | 439.6672 | 26.65 | 54.95
2021-01-11 06:40 | 6.8941 | 2.6529 | 0.52768 | 4.5942 | 122.029 | 88.1218 | 1.4922 | 0.47313 | 440.6565 | 26.71 | 54.65
2021-01-11 06:45 | 5.9128 | 2.3961 | 0.51511 | 4.1879 | 122.8954 | 77.9578 | 1.5213 | 0.49497 | 439.5374 | 26.75 | 54.52
2021-01-11 06:50 | 4.867 | 2.8914 | 0.58829 | 5.0183 | 120.7825 | 117.4801 | 1.5283 | 0.39299 | 439.5774 | 26.78 | 53.89
2021-01-11 06:55 | 5.2495 | 3.1074 | 0.63648 | 5.3996 | 135.7626 | 107.711 | 1.4847 | 0.38573 | 440.468 | 26.88 | 53.72
2021-01-11 07:00 | 6.4207 | 3.1561 | 0.5673 | 5.403 | 133.4897 | 111.3127 | 1.4772 | 0.5021 | 439.9019 | 26.95 | 53.08
2021-01-11 07:05 | 6.2412 | 3.0258 | 0.52533 | 5.1633 | 128.7365 | 104.1691 | 1.4842 | 0.46563 | 440.383 | 27.04 | 52.28
2021-01-11 07:10 | 7.2719 | 2.5939 | 0.50433 | 4.4804 | 139.1511 | 86.7224 | 1.4985 | 0.52376 | 440.7663 | 27.12 | 51.7
2021-01-11 07:15 | 7.4364 | 2.5021 | 0.4938 | 4.3291 | 124.2179 | 83.491 | 1.571 | 0.53096 | 439.7239 | 27.15 | 51.22
2021-01-11 07:20 | 6.2011 | 2.4065 | 0.50634 | 4.193 | 134.7689 | 118.9389 | 1.5347 | 0.45094 | 440.1891 | 27.2 | 51.02
2021-01-11 07:25 | 5.9704 | 2.6884 | 0.56897 | 4.6899 | 132.7804 | 96.5352 | 1.4616 | 0.3563 | 440.2242 | 27.25 | 50.2
2021-01-11 07:30 | 6.2376 | 2.8221 | 0.55641 | 4.8822 | 140.8525 | 120.5867 | 1.4615 | 0.51626 | 440.1046 | 27.34 | 49.86
2021-01-11 07:35 | 6.1621 | 2.5386 | 0.48954 | 4.3808 | 130.9633 | 81.5745 | 1.4399 | 0.45816 | 439.4353 | 27.39 | 50.12
2021-01-11 07:40 | 4.5685 | 2.5688 | 0.55623 | 4.4938 | 116.2214 | 79.1132 | 1.4102 | 0.4216 | 440.172 | 27.39 | 48.85
2021-01-11 07:45 | 5.3828 | 2.596 | 0.6524 | 4.6337 | 128.3226 | 120.2497 | 1.4101 | 0.42886 | 440.6849 | 27.41 | 48.72
2021-01-11 07:50 | 5.9428 | 2.4323 | 0.49767 | 4.226 | 120.7288 | 101.8443 | 1.3956 | 0.50155 | 440.6384 | 27.44 | 48.65
2021-01-11 07:55 | 4.9623 | 2.2288 | 0.40143 | 3.8178 | 110.5547 | 69.2583 | 1.3954 | 0.407 | 441.7114 | 27.47 | 48.22
2021-01-11 08:00 | 4.7589 | 2.5508 | 0.47462 | 4.3845 | 100.3996 | 78.7785 | 1.3809 | 0.32706 | 439.5453 | 27.49 | 48.26
2021-01-11 08:05 | 3.1044 | 2.4878 | 0.52057 | 4.3339 | 95.6264 | 73.8548 | 1.3663 | 0.23982 | 439.0718 | 27.48 | 48.03
2021-01-11 08:10 | 3.0153 | 2.4673 | 0.4913 | 4.2733 | 109.2345 | 72.1445 | 1.359 | 0.22529 | 440.6499 | 27.49 | 47.99
2021-01-11 08:15 | 3.1426 | 2.5178 | 0.54775 | 4.4092 | 97.6111 | 99.4025 | 1.359 | 0.22529 | 442.2247 | 27.5 | 47.97
2021-01-11 08:20 | 3.3083 | 2.2739 | 0.47463 | 3.9601 | 92.9385 | 73.231 | 1.3519 | 0.22531 | 440.5307 | 27.54 | 48.13
2021-01-11 08:25 | 3.7919 | 2.0283 | 0.45999 | 3.5691 | 78.3921 | 41.7867 | 1.3519 | 0.23258 | 441.0895 | 27.52 | 48.19
2021-01-11 08:30 | 3.5495 | 2.0867 | 0.46201 | 3.6605 | 77.3114 | 48.0398 | 1.3444 | 0.26161 | 439.6732 | 27.51 | 47.76
2021-01-11 08:35 | 3.8295 | 2.0131 | 0.52683 | 3.6125 | 71.8981 | 59.4809 | 1.3444 | 0.31249 | 440.7244 | 27.51 | 47.81
2021-01-11 08:40 | 3.8922 | 2.1026 | 0.48699 | 3.7078 | 81.5994 | 69.9583 | 1.3514 | 0.35601 | 440.2378 | 27.55 | 47.08
2021-01-11 08:45 | 3.7899 | 1.8882 | 0.43259 | 3.3269 | 68.7473 | 54.015 | 1.3657 | 0.29784 | 441.3046 | 27.59 | 46.57
2021-01-11 08:50 | 2.9501 | 1.8457 | 0.4179 | 3.2492 | 64.1706 | 35.7068 | 1.3728 | 0.29054 | 440.2886 | 27.6 | 46.19
2021-01-11 08:55 | 3.2173 | 1.7408 | 0.40538 | 3.0738 | 69.7475 | 31.0893 | 1.3583 | 0.26876 | 439.7157 | 27.62 | 46.22
2021-01-11 09:00 | 2.9874 | 1.9951 | 0.42195 | 3.478 | 78.0331 | 61.6597 | 1.3579 | 0.23962 | 439.3464 | 27.61 | 45.36
2021-01-11 09:05 | 2.796 | 1.9265 | 0.378 | 3.331 | 96.6715 | 71.497 | 1.3503 | 0.2323 | 439.9678 | 27.62 | 44.69
2021-01-11 09:10 | 2.3643 | 1.7973 | 0.42401 | 3.179 | 96.3521 | 70.8074 | 1.3505 | 0.23234 | 438.79 | 27.65 | 45.06
2021-01-11 09:15 | 2.4018 | 1.7192 | 0.42808 | 3.0634 | 90.7758 | 48.4836 | 1.3647 | 0.22502 | 440.4816 | 27.66 | 44.33
2021-01-11 09:20 | 2.2492 | 1.7096 | 0.38629 | 3.0068 | 82.6782 | 52.679 | 1.3573 | 0.21775 | 440.4802 | 27.68 | 44.11
2021-01-11 09:25 | 1.9695 | 1.5651 | 0.37582 | 2.7748 | 73.4826 | 70.0164 | 1.3427 | 0.23951 | 440.5288 | 27.67 | 43.93
2021-01-11 09:30 | 2.1472 | 1.3988 | 0.33612 | 2.4802 | 69.8484 | 42.8523 | 1.3353 | 0.26852 | 438.9576 | 27.68 | 43.7
2021-01-11 09:35 | 2.5537 | 2.0062 | 0.43632 | 3.5114 | 72.4783 | 58.8181 | 1.3425 | 0.31205 | 440.549 | 27.69 | 43.58
2021-01-11 09:40 | 2.3505 | 1.9885 | 0.44469 | 3.4928 | 67.8561 | 35.4832 | 1.3426 | 0.28303 | 439.4151 | 27.73 | 43.57
2021-01-11 09:45 | 2.896 | 2.1432 | 0.48422 | 3.7694 | 75.5402 | 47.2507 | 1.3422 | 0.29747 | 439.5189 | 27.74 | 42.83
2021-01-11 09:50 | 2.2102 | 1.5728 | 0.44459 | 2.8554 | 82.922 | 61.0533 | 1.335 | 0.31925 | 439.451 | 27.77 | 42.9
2021-01-11 09:55 | 2.2735 | 1.4228 | 0.42784 | 2.6088 | 74.1539 | 43.773 | 1.3421 | 0.33372 | 440.0602 | 27.75 | 42.65
2021-01-11 10:00 | 2.7312 | 1.5988 | 0.49889 | 2.9495 | 84.8585 | 54.6855 | 1.3496 | 0.33378 | 439.4212 | 27.77 | 43.08
2021-01-11 10:05 | 2.9971 | 1.7086 | 0.53005 | 3.1469 | 79.0529 | 62.4621 | 1.342 | 0.30467 | 440.5802 | 27.79 | 42.26
2021-01-11 10:10 | 3.3146 | 1.4989 | 0.40693 | 2.7045 | 86.4196 | 68.5992 | 1.3348 | 0.29016 | 440.5906 | 27.78 | 42.31
2021-01-11 10:15 | 3.0994 | 1.438 | 0.39032 | 2.5945 | 90.2894 | 51.5112 | 1.3423 | 0.23944 | 439.9811 | 27.77 | 42.9
2021-01-11 10:20 | 2.4776 | 1.4411 | 0.34449 | 2.5534 | 75.4014 | 36.3793 | 1.3499 | 0.21773 | 440.367 | 27.79 | 43.54
2021-01-11 10:25 | 2.4406 | 1.4213 | 0.34673 | 2.5253 | 69.1906 | 43.9712 | 1.3505 | 0.2396 | 440.6599 | 27.82 | 44.62
2021-01-11 10:30 | 2.4267 | 1.5717 | 0.43215 | 2.8414 | 55.7907 | 47.6899 | 1.3571 | 0.23223 | 439.7741 | 27.85 | 43.24
2021-01-11 10:35 | 3.1388 | 1.5353 | 0.42598 | 2.7793 | 53.4031 | 28.6992 | 1.3574 | 0.26857 | 440.1533 | 27.89 | 43.69
2021-01-11 10:40 | 3.4572 | 1.5737 | 0.39056 | 2.8028 | 60.5315 | 52.702 | 1.3576 | 0.27588 | 438.9482 | 27.93 | 44.11
2021-01-11 10:45 | 3.1272 | 1.6707 | 0.376 | 2.9391 | 66.1143 | 43.6491 | 1.3579 | 0.30497 | 439.3344 | 27.98 | 44.4
2021-01-11 10:50 | 3.128 | 2.0624 | 0.39072 | 3.552 | 65.6731 | 42.185 | 1.3655 | 0.31231 | 439.1224 | 28.05 | 44.87
2021-01-11 10:55 | 2.9764 | 1.8176 | 0.40966 | 3.1958 | 77.2235 | 47.256 | 1.3659 | 0.26882 | 438.349 | 28.12 | 45.53
2021-01-11 11:00 | 2.3404 | 1.7126 | 0.47864 | 3.1038 | 76.7563 | 46.1779 | 1.3587 | 0.23976 | 439.3578 | 28.15 | 45.48
2021-01-11 11:05 | 1.7557 | 1.308 | 0.42648 | 2.4335 | 73.4154 | 49.4254 | 1.359 | 0.26889 | 438.1689 | 28.17 | 46.03
2021-01-11 11:10 | 1.8071 | 1.2537 | 0.39522 | 2.317 | 71.092 | 28.5671 | 1.4029 | 0.28349 | 439.6315 | 28.18 | 46.64
2021-01-11 11:15 | 2.7234 | 1.2292 | 0.37641 | 2.2605 | 67.4889 | 46.1702 | 1.4393 | 0.31984 | 438.6596 | 28.18 | 46.63
2021-01-11 11:20 | 3.678 | 1.4175 | 0.39942 | 2.5722 | 59.7433 | 42.3029 | 1.4248 | 0.24716 | 438.6161 | 28.2 | 46.66
2021-01-11 11:25 | 3.3852 | 1.6098 | 0.44124 | 2.9088 | 51.4753 | 24.689 | 1.3812 | 0.26169 | 438.0951 | 28.2 | 46.62
2021-01-11 11:30 | 2.889 | 1.5758 | 0.44962 | 2.865 | 64.9477 | 47.5373 | 1.3667 | 0.32713 | 437.5048 | 28.23 | 46.65
2021-01-11 11:35 | 2.6724 | 1.5566 | 0.44331 | 2.8272 | 68.7497 | 43.1251 | 1.3666 | 0.3271 | 438.0263 | 28.26 | 46.35
2021-01-11 11:40 | 2.2272 | 1.8186 | 0.51445 | 3.3021 | 70.628 | 38.7706 | 1.3667 | 0.34894 | 438.4497 | 28.31 | 46.4
2021-01-11 11:45 | 2.2277 | 1.7358 | 0.46436 | 3.125 | 63.1177 | 25.1941 | 1.367 | 0.24722 | 437.2268 | 28.36 | 46.82
2021-01-11 11:50 | 2.0626 | 1.6979 | 0.41215 | 3.0147 | 69.6897 | 27.3075 | 1.36 | 0.19636 | 438.6931 | 28.38 | 47.27
2021-01-11 11:55 | 2.4701 | 1.7621 | 0.4017 | 3.1006 | 63.5296 | 55.0141 | 1.3527 | 0.19636 | 438.7076 | 28.36 | 47.41
2021-01-11 12:00 | 2.9928 | 1.6874 | 0.36204 | 2.9507 | 60.0505 | 45.6951 | 1.3458 | 0.22551 | 437.5165 | 28.38 | 47.98
2021-01-11 12:05 | 3.6045 | 1.607 | 0.35579 | 2.8191 | 61.9 | 33.7775 | 1.3532 | 0.23281 | 438.4602 | 28.43 | 48.06
2021-01-11 12:10 | 3.0442 | 1.588 | 0.38302 | 2.8172 | 57.9086 | 25.6375 | 1.346 | 0.22554 | 437.9409 | 28.41 | 48.24
2021-01-11 12:15 | 2.5859 | 1.4488 | 0.3977 | 2.6185 | 49.0881 | 30.0826 | 1.3461 | 0.24011 | 438.4192 | 28.42 | 48.41
2021-01-11 12:20 | 2.5861 | 1.2127 | 0.35796 | 2.2189 | 45.8408 | 36.2813 |  |  | 437.2883 | 28.45 | 48.52
2021-01-11 12:25 | 2.7008 | 1.225 | 0.4082 | 2.288 | 53.8828 | 20.8316 | 1.3389 | 0.24013 | 437.8065 | 28.45 | 48.57
2021-01-11 12:30 | 2.8538 | 1.6034 | 0.39985 | 2.8576 | 56.5356 | 52.2957 | 1.3317 | 0.26926 | 437.7397 | 28.48 | 48.62
2021-01-11 12:35 | 2.2678 | 1.9394 | 0.44174 | 3.4146 | 60.5434 | 45.0712 | 1.3318 | 0.20377 | 437.1531 | 28.51 | 48.63
2021-01-11 12:40 | 2.3187 | 1.9721 | 0.40404 | 3.427 | 55.0374 | 49.4011 | 1.3244 | 0.20376 | 436.0728 | 28.54 | 48.45
2021-01-11 12:45 | 2.8156 | 1.5556 | 0.38101 | 2.7654 | 49.9716 | 29.3021 | 1.3317 | 0.22559 | 437.1902 | 28.56 | 48.33
2021-01-11 12:50 | 2.5095 | 1.3915 | 0.41237 | 2.5475 | 50.7 | 29.2786 | 1.3316 | 0.20374 | 436.725 | 28.55 | 48.09
2021-01-11 12:55 | 2.2037 | 1.3328 | 0.40189 | 2.4448 | 57.7305 | 29.869 | 1.3315 | 0.24739 | 435.185 | 28.53 | 48.09
2021-01-11 13:00 | 2.2035 | 1.319 | 0.38928 | 2.4131 | 63.2973 | 27.6136 | 1.3314 | 0.21826 | 435.2368 | 28.53 | 47.79
2021-01-11 13:05 | 2.1397 | 1.2056 | 0.38508 | 2.2309 | 59.7784 | 33.5521 | 1.324 | 0.1746 | 436.3293 | 28.52 | 47.67
2021-01-11 13:10 | 1.6173 | 0.92283 | 0.31179 | 1.7263 | 57.0705 | 0.78444 | 1.3311 | 0.15275 | 435.8774 | 28.51 | 47.35
2021-01-11 13:15 | 1.9482 | 0.93915 | 0.30967 | 1.7492 | 63.3116 | 32.7 | 1.3383 | 0.19638 | 437.0001 | 28.48 | 47.28
2021-01-11 13:20 | 2.929 | 1.0662 | 0.33272 | 1.967 | 67.7787 | 30.4306 | 1.3384 | 0.29096 | 435.3582 | 28.5 | 47.42
2021-01-11 13:25 | 2.458 | 1.1332 | 0.34739 | 2.0843 | 74.5796 | 36.5562 | 1.3312 | 0.25461 | 434.7553 | 28.53 | 47.53
2021-01-11 13:30 | 2.4195 | 1.2341 | 0.40176 | 2.2934 | 80.0119 | 46.3935 | 1.3311 | 0.26186 | 435.3125 | 28.54 | 47.24
2021-01-11 13:35 | 2.4067 | 1.4251 | 0.39337 | 2.5778 | 81.1496 | 29.0024 | 1.3238 | 0.34913 | 437.4651 | 28.52 | 47.19
2021-01-11 13:40 | 2.4703 | 1.4497 | 0.37453 | 2.5966 | 76.4617 | 48.9371 | 1.3237 | 0.30548 | 436.4227 | 28.52 | 47.13
2021-01-11 13:45 | 2.2285 | 1.503 | 0.42896 | 2.7307 | 77.1601 | 30.0327 | 1.3238 | 0.27641 | 437.9409 | 28.54 | 47.26
2021-01-11 13:50 | 2.6489 | 1.5003 | 0.49386 | 2.7957 | 77.7957 | 41.1902 | 1.3166 | 0.2546 | 436.2815 | 28.58 | 47.28
2021-01-11 13:55 | 3.655 | 1.5126 | 0.38295 | 2.7016 | 85.9264 | 41.8731 | 1.3239 | 0.31279 | 436.278 | 28.58 | 47.3
2021-01-11 14:00 | 3.9988 | 1.4921 | 0.4248 | 2.712 | 81.7684 | 42.6976 | 1.3239 | 0.37826 | 437.3375 | 28.58 | 47.26
2021-01-11 14:05 | 3.6426 | 1.5947 | 0.39973 | 2.8442 | 92.0076 | 40.8787 | 1.3313 | 0.40013 | 436.2206 | 28.59 | 47.52
2021-01-11 14:10 | 2.8787 | 1.5744 | 0.42489 | 2.8361 | 93.6468 | 56.6976 | 1.3242 | 0.34923 | 436.121 | 28.63 | 47.65
2021-01-11 14:15 | 2.8024 | 1.5963 | 0.3935 | 2.8403 | 90.6333 | 34.9021 | 1.3242 | 0.32742 | 435.5529 | 28.65 | 47.67
2021-01-11 14:20 | 2.3566 | 1.6059 | 0.47725 | 2.9388 | 85.7556 | 48.0598 | 1.3243 | 0.32743 | 436.5436 | 28.68 | 47.69
2021-01-11 14:25 | 2.2417 | 1.3708 | 0.4416 | 2.5429 | 94.7103 | 48.7664 | 1.3605 | 0.26918 | 436.0928 | 28.67 | 47.37
2021-01-11 14:30 | 3.057 | 1.3095 | 0.40396 | 2.4091 | 107.9948 | 42.5641 | 1.3678 | 0.21827 | 434.9954 | 28.68 | 47.52
2021-01-11 14:35 | 3.5418 | 1.6225 | 0.43335 | 2.9204 | 104.0632 | 67.1875 | 1.3536 | 0.2256 | 436.541 | 28.7 | 47.95
2021-01-11 14:40 | 4.0514 | 2.05 | 0.46894 | 3.6134 | 105.5211 | 55.008 | 1.3681 | 0.27654 | 435.4167 | 28.75 | 47.82
2021-01-11 14:45 | 3.9879 | 2.4831 | 0.50455 | 4.3107 | 107.9204 | 66.9865 | 1.39 | 0.31294 | 435.3711 | 28.77 | 47.86
2021-01-11 14:50 | 4.4214 | 2.1404 | 0.43759 | 3.7206 | 69.3056 | 69.4993 | 1.3974 | 0.34935 | 434.7689 | 28.8 | 47.97
2021-01-11 14:55 | 4.3837 | 2.0929 | 0.50256 | 3.7106 | 75.4616 | 87.471 | 1.3757 | 0.313 | 434.6724 | 28.83 | 48.19
2021-01-11 15:00 | 4.8938 | 2.19 | 0.49002 | 3.849 | 105.2159 | 72.5093 | 1.3394 | 0.37853 | 435.6396 | 28.87 | 48.22
2021-01-11 15:05 | 5.0599 | 2.2653 | 0.45656 | 3.9289 | 113.811 | 67.7951 | 1.3832 | 0.41497 | 435.5269 | 28.92 | 48.31
2021-01-11 15:10 | 4.4739 | 2.1562 | 0.45868 | 3.7637 | 111.6355 | 73.0607 | 1.4416 | 0.39315 | 435.9829 | 28.95 | 48.37
2021-01-11 15:15 | 4.5502 | 2.04 | 0.37908 | 3.5039 | 113.7634 | 51.6764 | 1.4342 | 0.41498 | 434.4213 | 28.95 | 48.3
2021-01-11 15:20 | 3.9635 | 1.7077 | 0.37695 | 2.9946 | 98.1717 | 49.2541 | 1.354 | 0.37854 | 436.0889 | 28.92 | 48.1
2021-01-11 15:25 | 3.5046 | 1.694 | 0.33086 | 2.9275 | 97.078 | 55.4411 | 1.3831 | 0.3858 | 436.1593 | 28.88 | 48.14
2021-01-11 15:30 | 3.0969 | 1.5876 | 0.35392 | 2.7874 | 91.9449 | 46.2579 | 1.405 | 0.30575 | 434.0352 | 28.88 | 48.28
2021-01-11 15:35 | [9 empty] | 28.89 | 48.37
2021-01-11 15:40 | 3.4286 | 1.6943 | 0.39794 | 2.995 | 101.2529 | 50.1676 | 1.3396 | 0.25481 | 434.9863 | 28.92 | 48.4
2021-01-11 15:45 | 4.9833 | 1.6395 | 0.41676 | 2.9299 | 94.9255 | 47.3302 | 1.3177 | 0.3276 | 434.0526 | 28.92 | 48.21
2021-01-11 15:50 | 5.7861 | 1.7269 | 0.42303 | 3.068 | 87.7555 | 58.3711 | 1.3176 | 0.36399 | 434.0632 | 28.92 | 48.15
2021-01-11 15:55 | 5.1873 | 1.7133 | 0.42933 | 3.0556 | 104.7858 | 98.3521 | 1.325 | 0.35672 | 434.035 | 28.93 | 48.2
2021-01-11 16:00 | 5.7232 | 1.928 | 0.40214 | 3.3575 | 124.3749 | 68.0355 | 1.3251 | 0.39316 | 434.9392 | 29 | 48.25
2021-01-11 16:05 | 5.0477 | 2.0237 | 0.36445 | 3.4665 | 126.2637 | 71.9832 | 1.3397 | 0.41501 | 434.9022 | 29.02 | 48.24
2021-01-11 16:10 | 4.8053 | 1.9608 | 0.3791 | 3.3847 | 123.4756 | 82.7079 | 1.4052 | 0.38588 | 433.3166 | 29.04 | 48.1
2021-01-11 16:15 | 3.9003 | 1.6902 | 0.42098 | 3.0118 | 116.6836 | 93.608 | 1.3906 | 0.32035 | 433.348 | 29.02 | 48.14
2021-01-11 16:20 | 3.7856 | 1.4115 | 0.36443 | 2.528 | 102.3858 | 31.4876 | 1.3542 | 0.31306 | 433.8791 | 29.02 | 48.1
2021-01-11 16:25 | 3.6452 | 1.5754 | 0.38745 | 2.8043 | 86.2819 | 49.2486 | 1.325 | 0.30577 | 433.9527 | 28.98 | 48.12
2021-01-11 16:30 | 3.735 | 1.782 | 0.36657 | 3.098 | 96.0656 | 76.1182 | 1.3252 | 0.32038 | 433.3299 | 29 | 48.46
2021-01-11 16:35 | 3.8881 | 1.7506 | 0.40009 | 3.0834 | 100.952 | 67.9506 | 1.3252 | 0.32767 | 434.8666 | 29.02 | 48.44
2021-01-11 16:40 | 4.066 | 1.5522 | 0.38957 | 2.7668 | 92.2416 | 71.9802 | 1.3542 | 0.30579 | 434.92 | 29.02 | 48.14
2021-01-11 16:45 | 3.8873 | 1.5699 | 0.31624 | 2.7247 | 83.9342 | 37.2973 | 1.3468 | 0.34216 | 434.4613 | 29 | 47.99
2021-01-11 16:50 | 3.6707 | 1.5603 | 0.30158 | 2.6933 | 79.1025 | 53.2448 | 1.325 | 0.29121 | 433.4061 | 29 | 48.03
2021-01-11 16:55 | 3.7342 | 1.5479 | 0.36649 | 2.7392 | 76.295 | 62.4389 | 1.3104 | 0.31303 | 434.5034 | 28.98 | 47.97
2021-01-11 17:00 | 3.3263 | 1.4482 | 0.30994 | 2.5298 | 72.5623 | 51.753 | 1.3103 | 0.32031 | 436.6352 | 28.96 | 47.99
2021-01-11 17:05 | 3.7469 | 1.4892 | 0.27853 | 2.5612 | 74.113 | 44.9735 | 1.3176 | 0.39311 | 435.6675 | 28.9 | 48.19
2021-01-11 17:10 | 3.4794 | 1.395 | 0.30367 | 2.4419 | 65.9684 | 43.323 | 1.3177 | 0.364 | 435.6991 | 28.87 | 48.34
2021-01-11 17:15 | 3.046 | 1.2979 | 0.2911 | 2.2806 | 57.474 | 44.5049 | 1.3177 | 0.29119 | 435.2979 | 28.79 | 48.52
2021-01-11 17:20 | 3.2883 | 1.2734 | 0.30577 | 2.2577 | 54.4793 | 23.1356 | 1.3104 | 0.29121 | 435.3473 | 28.74 | 48.79
2021-01-11 17:25 | 4.015 | 1.2256 | 0.25971 | 2.1384 | 54.2164 | 48.8121 | 1.3105 | 0.32034 | 435.3298 | 28.74 | 48.89
2021-01-11 17:30 | 3.6199 | 1.0822 | 0.24505 | 1.9038 | 47.4153 | 25.7368 | 1.3323 | 0.28394 | 435.3563 | 28.72 | 48.96
2021-01-11 17:35 | 2.9442 | 1.0534 | 0.22828 | 1.843 | 41.5914 | 21.1577 | 1.3541 | 0.21841 | 436.4938 | 28.67 | 49.01
2021-01-11 17:40 | 1.9754 | 0.83337 | 0.22198 | 1.4994 | 36.265 | 36.4179 | 1.3394 | 0.22566 | 436.642 | 28.6 | 48.94
2021-01-11 17:45 | 3.0333 | 0.90311 | 0.22409 | 1.6084 | 50.7154 | 45.7397 | 1.3322 | 0.22568 | 436.2457 | 28.49 | 49.43
2021-01-11 17:50 | 3.365 | 0.82666 | 0.20735 | 1.4745 | 46.4262 | 29.7544 | 1.3178 | 0.18201 | 436.3001 | 28.43 | 49.79
2021-01-11 17:55 | 2.5999 | 0.69266 | 0.178 | 1.2397 | 29.9034 | 24.8566 | 1.303 | 0.16743 | 437.5091 | 28.36 | 49.66
2021-01-11 18:00 | 3.1737 | 0.78291 | 0.18849 | 1.3886 | 39.787 | 42.1934 | 1.3105 | 0.18201 | 437.5504 | 28.3 | 50.1
2021-01-11 18:05 | 1.899 | 0.84297 | 0.19895 | 1.4911 | 30.7506 | 50.245 | 1.2958 | 0.15288 | 438.1227 | 28.29 | 49.94
2021-01-11 18:10 | 1.453 | 0.95913 | 0.19477 | 1.665 | 41.5799 | 36.9305 | 1.2958 | 0.11648 | 438.1521 | 28.26 | 50.11
2021-01-11 18:15 | 1.1088 | 0.98779 | 0.18848 | 1.7026 | 45.8607 | 32.9324 | 1.2958 | 0.1092 | 437.1599 | 28.23 | 50.11
2021-01-11 18:20 | 1.0705 | 0.86071 | 0.20523 | 1.5225 | 38.4783 | 28.2113 | 1.2958 | 0.10192 | 437.809 | 28.15 | 50.3
2021-01-11 18:25 | 1.1853 | 0.75281 | 0.22199 | 1.3759 | 26.377 | 24.0218 | 1.2958 | 0.10192 | 437.8802 | 28.09 | 50.57
2021-01-11 18:30 | 1.096 | 0.5492 | 0.19056 | 1.0324 | 14.7831 | 11.5308 | 1.2957 | 0.10191 | 438.9073 | 28.07 | 50.48
2021-01-11 18:35 | 2.6891 | 0.56015 | 0.22617 | 1.0848 | 12.0513 | 18.495 | 1.3031 | 0.17471 | 437.3659 | 28.03 | 50.72
2021-01-11 18:40 | 2.3703 | 0.49454 | 0.18009 | 0.94023 | 3.9149 | 9.3081 | 1.3103 | 0.13831 | 439.6162 | 27.95 | 50.79
2021-01-11 18:45 | 2.9058 | 0.59705 | 0.18848 | 1.1058 | 14.7534 | 46.6563 | 1.3177 | 0.16744 | 438.6295 | 27.88 | 51.21
2021-01-11 18:50 | 2.4598 | 0.53969 | 0.1822 | 1.0095 | 12.4292 | 25.776 | 1.3177 | 0.15288 | 439.1994 | 27.84 | 51.42
2021-01-11 18:55 | 2.1032 | 0.68321 | 0.16547 | 1.2127 | 18.7425 | 13.3278 | 1.3178 | 0.18202 | 439.7556 | 27.79 | 51.83
2021-01-11 19:00 | 1.211 | 0.61081 | 0.14452 | 1.0829 | 16.7239 | 11.8597 | 1.3106 | 0.13834 | 439.3492 | 27.7 | 52.17
2021-01-11 19:05 | 1.0198 | 0.82676 | 0.17386 | 1.4432 | 12.819 | 15.96 | 1.3179 | 0.10922 | 439.9082 | 27.66 | 52.45
2021-01-11 19:10 | 0.85408 | 0.57257 | 0.17176 | 1.0494 | 9.6166 | 21.1709 | 1.3106 | 0.10194 | 440.5598 | 27.58 | 52.65
2021-01-11 19:15 | 0.96884 | 0.59856 | 0.17177 | 1.0893 | 6.119 | 18.7548 | 1.3107 | 0.094661 | 440.1165 | 27.51 | 52.98
2021-01-11 19:20 | 0.68833 | 0.42224 | 0.13615 | 0.78336 | 5.3231 | 1.8457 | 1.3106 | 0.058248 | 439.233 | 27.42 | 53.02
2021-01-11 19:25 | 0.71384 | 0.46324 | 0.16966 | 0.87973 | 4.5686 | 23.9136 | 1.3179 | 0.058249 | 440.3651 | 27.36 | 53.27
2021-01-11 19:30 | 0.84131 | 0.88959 | 0.23669 | 1.6003 | 17.6421 | 30.838 | 1.3252 | 0.072812 | 438.7945 | 27.35 | 53.32
2021-01-11 19:35 | 0.67548 | 0.58749 | 0.1445 | 1.045 | 9.0744 | 16.5888 | 1.3249 | 0.0364 | 440 | 27.3 | 53
2021-01-11 19:40 | 0.91773 | 0.64494 | 0.1508 | 1.1415 | 14.0718 | 24.3911 | 1.3251 | 0.036403 | 439.5027 | 27.25 | 53.42
2021-01-11 19:45 | 0.58625 | 0.43173 | 0.12984 | 0.7916 | 4.4045 | 11.6129 | 1.3103 | 0.036399 | 439.0301 | 27.25 | 53.08
2021-01-11 19:50 | 0.80291 | 0.40577 | 0.13612 | 0.75601 | 9.4922 | 16.3132 | 1.3104 | 0.043679 | 441.1673 | 27.23 | 53.16
2021-01-11 19:55 | 0.6626 | 0.24998 | 0.09841 | 0.48158 | 3.5373 | 13.8026 | 1.3028 | 0.029114 | 440.3082 | 27.15 | 52.92
2021-01-11 20:00 | 0.35679 | 0.24998 | 0.1026 | 0.48578 | 6.1267 | 17.1363 | 1.3029 | 0.029114 | 440.4455 | 27.05 | 53.29
2021-01-11 20:05 | 0.56064 | 0.22538 | 0.098405 | 0.44387 | 11.8957 | 6.6257 | 1.3028 | 0.021834 | 440.0948 | 26.95 | 53.41
2021-01-11 20:10 | 0.64987 | 0.35516 | 0.11935 | 0.66375 | 11.3663 | 29.7869 | 1.3029 | 0.036393 | 440.6707 | 26.9 | 53.73
2021-01-11 20:15 | 0.94307 | 0.65986 | 0.14031 | 1.1518 | 13.9064 | 13.6413 | 1.3103 | 0.058236 | 442.1698 | 26.92 | 54.02
2021-01-11 20:20 | 0.56068 | 0.4139 | 0.11935 | 0.7538 | -0.85631 | 2.2631 | 1.3102 | 0.036393 | 441.6628 | 26.94 | 53.64
2021-01-11 20:25 | 0.59889 | 0.48629 | 0.12144 | 0.86684 | 3.2722 | 6.2284 | 1.3101 | 0.036392 | 441.7787 | 26.87 | 53.78
2021-01-11 20:30 | 0.59891 | 0.51772 | 0.12982 | 0.92549 | 118.0076 | 239.0224 | 1.3174 | 0.036393 | 303.8761 | 26.84 | 53.96
2021-01-11 20:35 | 0.85384 | 0.60247 | 0.14868 | 1.0722 | 164.8238 | 70.866 | 1.303 | 0.050955 | 286.9389 | 26.84 | 54.21
2021-01-11 20:40 | 1.3891 | 0.55193 | 0.14868 | 0.9968 | 88.2709 | 22.032 | 1.303 | 0.087353 | 286.3945 | 26.85 | 54.24
2021-01-11 20:45 | 0.99412 | 0.48503 | 0.13194 | 0.87541 | 35.7577 | 15.3349 | 1.3031 | 0.05824 | 285.8056 | 26.89 | 54.33
2021-01-11 20:50 | 1.1216 | 0.4946 | 0.15498 | 0.91313 | 22.2484 | 11.4403 | 1.3032 | 0.050961 | 286.8082 | 26.94 | 54.23
2021-01-11 20:55 | 1.1088 | 0.43855 | 0.16125 | 0.83557 | 18.4232 | 19.6365 | 1.3103 | 0.043677 | 285.2474 | 26.94 | 54
2021-01-11 21:00 | 0.99409 | 0.62027 | 0.1445 | 1.0953 | 12.8466 | 13.0709 | 1.3031 | 0.072798 | 285.5342 | 26.93 | 54.16
2021-01-11 21:05 | 1.0705 | 0.49047 | 0.12984 | 0.88165 | 17.251 | 12.4692 | 1.3103 | 0.058237 | 286.0855 | 26.91 | 54.19
2021-01-11 21:10 | 0.38229 | 0.33742 | 0.11517 | 0.63237 | 124.3012 | 390.4585 | 1.3029 | 0.029115 | 73.0009 | 26.84 | 54.1
2021-01-11 21:15 | 0.39499 | 0.26225 | 0.090029 | 0.49411 | 169.963 | 171.7265 | 1.31 | 0.021834 | 7.4097 | 26.72 | 54.16
2021-01-11 21:20 | 0.53512 | 0.25951 | 0.087932 | 0.48572 | 76.4361 | 17.6438 | 1.3027 | 0.029111 | 6.8828 | 26.63 | 54.32
2021-01-11 21:25 | 0.53505 | 0.20758 | 0.075359 | 0.39354 | 36.1589 | 2.4561 | 1.3025 | 0.014553 | 7.9458 | 26.52 | 54.26
2021-01-11 21:30 | 0.35668 | 0.16114 | 0.079541 | 0.32654 | 10.2621 | 9.7016 | 1.2952 | 0.0072762 | 9.5381 | 26.44 | 54.34
2021-01-11 21:35 | 0.35666 | 0.18844 | 0.071165 | 0.3621 | -3.3526 | 8.2643 | 1.2951 | 0.014552 | 7.4221 | 26.31 | 54.63
2021-01-11 21:40 | 0.29297 | 0.13928 | 0.062792 | 0.27629 | -1.233 | -11.9124 | 1.2951 | 0.0072759 | 9.5439 | 26.27 | 54.76
2021-01-11 21:45 | 0.26749 | 0.12016 | 0.066978 | 0.24907 | 3.2914 | -8.1827 | 1.2951 | 0.014552 | 6.3644 | 26.19 | 55
2021-01-11 21:50 | 0.3312 | 0.10788 | 0.062795 | 0.22815 | 6.5526 | 1.1617 | 1.3024 | 0.014552 | 10.0771 | 26.17 | 55.19
2021-01-11 21:55 | 0.25475 | 0.088755 | 0.062791 | 0.19884 | -7.5406 | 5.7472 | 1.3024 | 0.0072757 | 10.6102 | 26.11 | 55.22
2021-01-11 22:00 | 0.21656 | 0.10788 | 0.062798 | 0.22817 | -9.6511 | 6.5937 | 1.3025 | 0.014553 | 6.8961 | 26.1 | 55.58
2021-01-11 22:05 | 0.50962 | 0.084679 | 0.062806 | 0.19051 | -0.85617 | -11.9048 | 1.2954 | 0.014555 | 9.0145 | 26.18 | 55.68
2021-01-11 22:10 | 0.5096 | 0.080579 | 0.058617 | 0.18213 | 9.0302 | -3.3736 | 1.3026 | 0.0072771 | 9.5457 | 26.16 | 55.63
2021-01-11 22:15 | 0.31851 | 0.080581 | 0.058619 | 0.18214 | 5.1166 | 3.7916 | 1.2954 | 0.0072774 | 6.3634 | 26.17 | 55.7
2021-01-11 22:20 | 0.14015 | 0.055997 | 0.052338 | 0.13817 | -10.6816 | 5.086 | 1.2954 | 0 | 7.9468 | 26.15 | 55.7
2021-01-11 22:25 | 0.30576 | 0.069652 | 0.050243 | 0.15701 | -7.1446 | -4.3418 | 1.2953 | 0 | 7.9487 | 26.09 | 55.79
2021-01-11 22:30 | 0.2166 | 0.071026 | 0.052342 | 0.16121 | -1.3047 | -11.0697 | 1.2955 | 0 | 6.3579 | 26.11 | 56.04
2021-01-11 22:35 | 0.063707 | 0.061464 | 0.048154 | 0.14237 | 6.9822 | -2.5788 | 1.2955 | 0.0072778 | 8.4767 | 26.13 | 55.95
2021-01-11 22:40 | 0.10193 | 0.057365 | 0.050246 | 0.14027 | -3.2209 | 1.5799 | 1.2954 | 0.0072777 | 5.298 | 26.13 | 55.88
2021-01-11 22:45 | 0.11466 | 0.043702 | 0.048148 | 0.11514 | -13.5245 | 1.5899 | 1.3026 | 0.0072769 | 8.4791 | 26.08 | 55.75
2021-01-11 22:50 | 0.16561 | 0.054626 | 0.05024 | 0.13397 | -9.7533 | -7.6334 | 1.3025 | 0.0072767 | 10.0709 | 26.03 | 55.84
2021-01-11 22:55 | 0.25479 | 0.055993 | 0.052334 | 0.13816 | 1.3045 | -10.6911 | 1.2953 | 0 | 7.9506 | 26.03 | 55.9
2021-01-11 23:00 | 0.38219 | 0.054627 | 0.046054 | 0.12979 | 10.5076 | -1.4574 | 1.2953 | 0.0072768 | 8.4798 | 26.06 | 55.78
2021-01-11 23:05 | 0.17836 | 0.060091 | 0.048148 | 0.14235 | -2.3849 | 6.1864 | 1.2953 | 0.007277 | 6.8893 | 26.08 | 55.77
2021-01-11 23:10 | 0.17834 | 0.057354 | 0.043957 | 0.13187 | -10.5067 | 4.6368 | 1.2952 | 0 | 6.3604 | 26.06 | 55.55
2021-01-11 23:15 | 0.15287 | 0.053258 | 0.046051 | 0.12978 | -5.3707 | -13.4725 | 1.2952 | 0.014553 | 7.4203 | 26.06 | 55.6
2021-01-11 23:20 | 0.063693 | 0.051892 | 0.043957 | 0.1235 | 5.6865 | -9.9157 | 1.2952 | 0.0072763 | 7.9505 | 26.06 | 55.55
2021-01-11 23:25 | 0.14011 | 0.049156 | 0.04186 | 0.11721 | 7.4998 | 0.49931 | 1.2951 | 0.0072756 | 10.6026 | 26.03 | 55.39
2021-01-11 23:30 | 0.19104 | 0.050517 | 0.046042 | 0.12348 | -7.5704 | 2.9752 | 1.3022 | 0.0072749 | 10.6068 | 25.94 | 55.42
2021-01-11 23:35 | 0.30566 | 0.039594 | 0.043948 | 0.10464 | -12.573 | -4.9721 | 1.2949 | 0.0072748 | 12.2009 | 25.87 | 55.59
2021-01-11 23:40 | 0.38207 | 0.046419 | 0.050225 | 0.11929 | -7.621 | -14.0093 | 1.2949 | 0.0072746 | 6.3673 | 25.8 | 55.75
2021-01-11 23:45 | 0.17831 | 0.047788 | 0.043951 | 0.1172 | 4.5648 | -7.1937 | 1.295 | 0.01455 | 11.6714 | 25.83 | 55.87
2021-01-11 23:50 |  | 0.045056 | 0.048136 | 0.1172 | 5.1149 | 1.1616 | 1.295 | 0.007275 | 10.6105 | 25.83 | 55.82
2021-01-11 23:55 | 0.17831 | 0.05325 | 0.043951 | 0.12557 | -5.9506 | 2.8123 | 1.2877 | 0.01455 | 4.7746 | 25.83 | 55.88
2021-01-12 | 0.076417 | 0.04369 | 0.039763 | 0.10673 | -5.1556 | 3.2197 | 1.2949 | 0 | 13.2639 | 25.82 | 55.78
2021-01-12 00:05 | 0.16557 | 0.055978 | 0.043949 | 0.12975 | -0.34643 | -11.269 | 1.2949 | 0.01455 | 5.837 | 25.77 | 55.98
2021-01-12 00:10 | -0.012737 | 0.040962 | 0.052323 | 0.11511 | 5.3291 | -9.8227 | 1.3023 | 0.014551 | 6.8975 | 25.79 | 56.05
2021-01-12 00:15 | 0.25474 | 0.043692 | 0.043951 | 0.11092 | 5.8385 | -5.7978 | 1.295 | 0.0072752 | 4.7754 | 25.78 | 56.07
2021-01-12 00:20 | 0.12737 | 0.040962 | 0.043951 | 0.10674 | -7.1938 | 5.2476 | 1.2877 | 0.0072753 | 11.1448 | 25.72 | 56.28
2021-01-12 00:25 | 0.42032 | 0.043693 | 0.043952 | 0.11093 | -8.651 | 8.9975 | 1.295 | 0.0072754 | 6.9004 | 25.66 | 56.54
2021-01-12 00:30 | 0.24203 | 0.047795 | 0.043957 | 0.11722 | -1.763 | -13.4314 | 1.2952 | 0.0072762 | 11.1345 | 25.66 | 56.81
2021-01-12 00:35 | 0.15287 | 0.05326 | 0.037679 | 0.11932 | 7.2358 | -7.5416 | 1.3025 | 0.014553 | 12.7249 | 25.65 | 57
2021-01-12 00:40 | 0.26752 | 0.051894 | 0.041866 | 0.12141 | 8.7136 | -1.9058 | 1.2952 | 0.014553 | 7.4238 | 25.61 | 57.14
2021-01-12 00:45 | 0.67519 | 0.050529 | 0.03768 | 0.11723 | -2.5988 | 0.63187 | 1.2953 | 0.0072767 | 10.0764 | 25.57 | 57.32
2021-01-12 00:50 | 0.21658 | 0.050532 | 0.039776 | 0.11723 | -4.0259 | 17.2654 | 1.2953 | 0.014554 | 10.6068 | 25.55 | 57.56
2021-01-12 00:55 | 0.36946 | 0.050532 | 0.041869 | 0.11933 | 1.1415 | -5.8706 | 1.2953 | 0.014554 | 9.0167 | 25.52 | 57.66
2021-01-12 01:00 | 0.58605 | 0.049167 | 0.041869 | 0.11723 | 6.9408 | -14.1874 | 1.2881 | 0.014554 | 12.1999 | 25.5 | 57.74
2021-01-12 01:05 |  |  |  |  | 8.1947 | -0.23443 |  |  | 6.8956 | 25.49 | 57.87
2021-01-12 01:10 |  |  |  |  | -1.4677 | 3.4553 |  |  | 11.1393 | 25.48 | 57.94
2021-01-12 01:15 |  |  |  |  | -9.5712 | 5.9425 |  |  | 8.4864 | 25.49 | 58.02
2021-01-12 01:20 |  |  |  |  | -1.59 | -6.2684 |  |  | 9.5479 | 25.48 | 57.94
2021-01-12 01:25 |  |  |  |  | 6.0642 | -5.5444 |  |  | 9.0195 | 25.43 | 57.94
2021-01-12 01:30 |  |  |  |  | 13.7187 | 4.0973 |  |  | 4.2444 | 25.43 | 58.02
2021-01-12 01:35 |  |  |  |  | 6.1052 | 9.5808 |  |  | 6.3658 | 25.46 | 57.96
2021-01-12 01:40 |  |  |  |  | -6.3901 | 6.2372 |  |  | 7.9582 | 25.45 | 57.75
2021-01-12 01:45 |  |  |  |  | -5.0751 | -7.5719 |  |  | 11.6746 | 25.4 | 57.75
2021-01-12 01:50 |  |  |  |  | 3.3627 | -11.0765 |  |  | 12.2094 | 25.33 | 57.69
2021-01-12 01:55 |  |  |  |  | 10.6893 | -0.47893 |  |  | 15.9258 | 25.32 | 57.73
2021-01-12 02:00 |  |  |  |  | 9.7004 | 16.9146 |  |  | 9.5562 | 25.31 | 57.63
2021-01-12 02:05 |  |  |  |  | -3.6681 | 7.3463 |  |  | 6.9029 | 25.27 | 57.63
2021-01-12 02:10 | 0.92975 | 0.075094 | 0.039764 | 0.15487 | -5.2779 | -3.5967 | 1.4405 | -0.007275 | 8.497 | 25.23 | 57.77
2021-01-12 02:15 | 1.0699 | 0.079191 | 0.041857 | 0.16324 | 3.7089 | -16.0073 | 1.4114 | 0.021825 | 12.7454 | 25.23 | 57.81
2021-01-12 02:20 | 0.91705 | 0.084654 | 0.037672 | 0.16743 | 10.7193 | 3.5663 | 1.3823 | 0.072753 | 6.3721 | 25.25 | 57.81
2021-01-12 02:25 | 0.92975 | 0.075093 | 0.043949 | 0.15905 | 8.8441 | 4.0654 | 1.3822 | 0.065475 | 8.4971 | 25.23 | 57.75
2021-01-12 02:30 | 0.95523 | 0.07919 | 0.039764 | 0.16115 | -3.607 | 6.0422 | 1.375 | 0.07275 | 9.029 | 25.2 | 57.89
2021-01-12 02:35 | 0.96801 | 0.077828 | 0.039766 | 0.16116 | -5.8692 | -0.071327 | 1.3678 | 0.072753 | 7.4348 | 25.22 | 57.95
2021-01-12 02:40 | 1.0063 | 0.083294 | 0.041861 | 0.16954 | -1.2024 | -16.4774 | 1.3678 | 0.072757 | 6.9032 | 25.23 | 58.07
2021-01-12 02:45 | 1.0573 | 0.083297 | 0.039769 | 0.16745 | 9.7624 | 0.66238 | 1.3606 | 0.065484 | 7.9647 | 25.24 | 58.14
2021-01-12 02:50 | 1.0318 | 0.080564 | 0.039768 | 0.16326 | 13.1556 | 7.072 | 1.3606 | 0.058207 | 6.3719 | 25.24 | 58.08
2021-01-12 02:55 | 0.95531 | 0.081927 | 0.035581 | 0.16116 | 6.8476 | 10.2817 | 1.3605 | 0.058205 | 9.0273 | 25.23 | 58.03
2021-01-12 03:00 | [9 empty] | 25.2 | 57.98
2021-01-12 03:05 | 1.9233 | 0.22939 | 0.050231 | 0.40185 | -0.3974 |  | 1.3605 | 0.065479 | 66.9233 | 25.17 | 58.18
2021-01-12 03:10 | 1.911 | 0.60776 | 0.14236 | 1.074 |  |  | 1.3608 | 0.13827 | 319.4708 | 25.55 | 57.55
2021-01-12 03:15 | 0.95532 | 0.35639 | 0.085815 | 0.63419 |  |  | 1.3678 | 0.10186 | 319.7563 | 25.84 | 55.96
2021-01-12 03:20 | 0.2547 | 0.098294 | 0.064871 | 0.21763 |  | 4.8189 | 1.3676 | 0.05092 | 320.5013 | 25.7 | 55.82
2021-01-12 03:25 | 0.25467 | 0.079173 | 0.050218 | 0.17367 |  | 0.38711 | 1.3674 | 0.029094 | 320.7386 | 25.51 | 56.14
2021-01-12 03:30 | 0.24192 | 0.077801 | 0.048121 | 0.16738 | -9.0758 | -8.9434 | 1.3673 | 0.036364 | 320.4182 | 25.34 | 56.45
2021-01-12 03:35 | 0.17826 | 0.085992 | 0.054398 | 0.18621 | -2.1391 | 9.738 | 1.3673 | 0.043638 | 319.4719 | 25.23 | 56.85
2021-01-12 03:40 | 0.15279 | 0.10919 | 0.054398 | 0.21968 | -1.3548 | 5.6227 | 1.3746 | 0.036364 | 319.5609 | 25.15 | 57.09
2021-01-12 03:45 | 0.20371 | 0.096906 | 0.046027 | 0.19666 | 2.2205 |  | 1.3745 | 0.050908 | 353.1043 | 25.08 | 57.17
2021-01-12 03:50 | 0.28009 | 0.083253 | 0.043932 | 0.17155 |  |  | 1.3744 | 0.058177 | 476.4107 | 25.02 | 57.23
2021-01-12 03:55 | 0.22916 | 0.050498 | 0.046024 | 0.12343 |  |  | 1.3817 | 0.050905 | 477.1021 | 24.92 | 57.57
2021-01-12 04:00 | 0.25465 | 0.09418 | 0.046028 | 0.19039 |  | 12.5899 | 1.3964 | 0.05091 | 476.5932 | 24.88 | 57.98
2021-01-12 04:05 | 0.28012 | 0.17744 | 0.066952 | 0.33894 | -3.993 | -2.1799 | 1.4182 | 0.065457 | 476.4855 | 24.94 | 57.85
2021-01-12 04:10 | 0.30559 | 0.22385 | 0.079505 | 0.42263 | 10.1251 | 22.644 | 1.4255 | 0.043638 | 476.39 | 25 | 57.64
2021-01-12 04:15 | 1.8081 | 0.48731 | 0.11089 | 0.85786 | 20.9132 | 20.8826 | 1.4328 | 0.072733 | 478.881 | 25.09 | 57.46
2021-01-12 04:20 | 1.477 | 0.5569 | 0.12763 | 0.98126 | 23.7847 | 7.0896 | 1.4255 | 0.094548 | 475.6539 | 25.13 | 57.18
2021-01-12 04:25 | 1.3115 | 0.5146 | 0.13809 | 0.92688 | 33.1975 | 29.0517 | 1.4328 | 0.20365 | 475.0957 | 25.14 | 57.22
2021-01-12 04:30 | 1.1077 | 0.51594 | 0.14018 | 0.93103 | 20.9526 | 26.3104 | 1.44 | 0.21091 | 473.9747 | 25.19 | 56.92
2021-01-12 04:35 | 1.0313 | 0.79162 | 0.17365 | 1.3892 | 32.8383 | 13.231 | 1.44 | 0.12363 | 474.382 | 25.28 | 56.49
2021-01-12 04:40 | 1.1968 | 1.2147 | 0.26988 | 2.1319 | 39.8664 | 34.1727 | 1.469 | 0.14545 | 472.6457 | 25.37 | 56.2
2021-01-12 04:45 | 1.7189 | 1.1383 | 0.25734 | 2.0022 | 53.9849 | 45.052 | 1.4618 | 0.15273 | 472.9752 | 25.49 | 55.87
2021-01-12 04:50 | 2.8774 | 0.94856 | 0.25314 | 1.7092 | 53.5751 | 43.5629 | 1.4908 | 0.19635 | 472.9172 | 25.54 | 55.57
2021-01-12 04:55 | 2.8643 | 1.1081 | 0.29704 | 1.9935 | 53.11 | 40.6956 | 1.4906 | 0.23996 | 473.9659 | 25.55 | 55.21
2021-01-12 05:00 | 2.2787 | 1.2023 | 0.27194 | 2.1148 | 52.8459 | 51.2164 | 1.4979 | 0.22542 | 471.2588 | 25.58 | 55.15
2021-01-12 05:05 | 1.9732 | 1.3674 | 0.33051 | 2.4286 | 71.3715 | 59.354 | 1.4907 | 0.22542 | 472.1903 | 25.66 | 54.91
2021-01-12 05:10 | 1.7186 | 1.7236 | 0.37234 | 3.0164 | 89.4678 | 72.0936 | 1.4761 | 0.2036 | 472.1173 | 25.71 | 54.71
2021-01-12 05:15 | 1.6551 | 1.822 | 0.49162 | 3.2844 | 92.4287 | 92.9278 | 1.469 | 0.1818 | 472.5301 | 25.76 | 54.79
2021-01-12 05:20 | 2.126 | 1.7742 | 0.45813 | 3.1776 | 101.1531 | 77.7286 | 1.4616 | 0.18907 | 472.4392 | 25.83 | 54.44
2021-01-12 05:25 | 2.674 | 2.1267 | 0.50634 | 3.7662 | 109.6894 | 103.2107 | 1.4692 | 0.24002 | 474.322 | 25.92 | 54.74
2021-01-12 05:30 | 4.7751 | 2.9812 | 0.6591 | 5.2288 | 139.2945 | 142.6154 | 1.4692 | 0.39276 | 471.3788 | 26.1 | 54.22
2021-01-12 05:35 | 5.5394 | 3.537 | 0.79515 | 6.2147 | 159.5041 | 128.1269 | 1.4766 | 0.51644 | 469.9158 | 26.34 | 53.62
2021-01-12 05:40 | 4.6224 | 3.8905 | 0.78885 | 6.7523 | 153.1743 | 139.8189 | 1.462 | 0.50188 | 469.1153 | 26.52 | 52.99
2021-01-12 05:45 | 4.355 | 3.7349 | 0.76165 | 6.4866 | 178.3273 | 155.2227 | 1.4693 | 0.39278 | 470.4796 | 26.66 | 52.57
2021-01-12 05:50 | 4.266 | 3.5835 | 0.76586 | 6.2587 | 193.3393 | 168.2983 | 1.4984 | 0.40734 | 469.2352 | 26.77 | 52.32
2021-01-12 05:55 | 3.2727 | 3.219 | 0.79725 | 5.7335 | 186.3294 | 137.2256 | 1.462 | 0.34915 | 470.1375 | 26.87 | 52
2021-01-12 06:00 | 3.6681 | 3.4106 | 0.85806 | 6.086 | 166.8872 | 145.8671 | 1.4623 | 0.36375 | 470.4821 | 26.94 | 52.22
2021-01-12 06:05 | 3.63 | 3.2674 | 0.83298 | 5.8392 | 150.0391 | 109.6585 | 1.4769 | 0.48017 | 470.3264 | 27.03 | 52.03
2021-01-12 06:10 | 4.9167 | 3.4014 | 0.80372 | 6.0175 | 164.1003 | 124.0025 | 1.477 | 0.54568 | 469.5981 | 27.14 | 51.86
2021-01-12 06:15 | 5.4261 | 3.161 | 0.72837 | 5.5737 | 163.6904 | 160.3685 | 1.4697 | 0.53839 | 469.4638 | 27.23 | 51.55
2021-01-12 06:20 | 6.1769 | 2.9954 | 0.69898 | 5.2905 | 169.6926 | 142.6213 | 1.5277 | 0.56015 | 469.3942 | 27.31 | 50.99
2021-01-12 06:25 | 5.6926 | 2.8123 | 0.63616 | 4.947 | 151.426 | 97.6327 | 1.5567 | 0.45828 | 469.8386 | 27.38 | 50.63
2021-01-12 06:30 | 4.9923 | 2.9189 | 0.66966 | 5.1438 | 139.7534 | 116.1471 | 1.5131 | 0.37827 | 469.2542 | 27.41 | 50.6
2021-01-12 06:35 | 3.7187 | 2.4984 | 0.51899 | 4.3486 | 131.0321 | 106.7635 | 1.4331 | 0.3419 | 468.1067 | 27.47 | 50.42
2021-01-12 06:40 | 4.33 | 2.7277 | 0.58594 | 4.7692 | 126.7511 | 101.1992 | 1.4403 | 0.42191 | 468.6409 | 27.47 | 50.38
2021-01-12 06:45 | 6.6097 | 2.5612 | 0.56921 | 4.493 | 126.5898 | 94.2114 | 1.4403 | 0.50921 | 468.0139 | 27.53 | 50.24
2021-01-12 06:50 | 6.5457 | 2.3891 | 0.49594 | 4.158 | 112.352 | 80.2499 | 1.4767 | 0.53829 | 470.0638 | 27.58 | 49.98
2021-01-12 06:55 | 5.1961 | 2.4656 | 0.52108 | 4.3005 | 129.108 | 108.5477 | 1.4913 | 0.40737 | 468.9371 | 27.61 | 50.04
2021-01-12 07:00 | 4.4069 | 2.7089 | 0.54625 | 4.6986 | 122.7826 | 98.4095 | 1.4551 | 0.40014 | 468.2717 | 27.67 | 50.12
2021-01-12 07:05 | 5.3235 | 2.6281 | 0.50225 | 4.5307 | 129.3936 | 111.9713 | 1.4476 | 0.4874 | 470.2251 | 27.76 | 49.66
2021-01-12 07:10 | 5.2985 | 2.7868 | 0.57555 | 4.8472 | 137.497 | 117.1486 | 1.4696 | 0.44379 | 469.0147 | 27.83 | 49.72
2021-01-12 07:15 | 3.9231 | 2.8565 | 0.60488 | 4.9856 | 152.6351 | 118.9573 | 1.4551 | 0.38561 | 467.8472 | 27.89 | 49.66
2021-01-12 07:20 | 4.3437 | 2.5754 | 0.56305 | 4.5107 | 156.4847 | 108.9768 | 1.4479 | 0.34925 | 468.2567 | 27.95 | 49.62
2021-01-12 07:25 | 6.6861 | 2.6008 | 0.50643 | 4.493 | 139.2654 | 94.8541 | 1.4404 | 0.44375 | 467.2507 | 27.98 | 49.01
2021-01-12 07:30 | 6.2917 | 2.6037 | 0.50437 | 4.4975 | 126.0893 | 75.9593 | 1.4404 | 0.48742 | 467.64 | 28.05 | 48.97
2021-01-12 07:35 | 5.3619 | 2.7907 | 0.50227 | 4.7778 | 113.8399 | 89.1829 | 1.4404 | 0.50924 | 467.014 | 28.12 | 48.72
2021-01-12 07:40 | 4.5215 | 2.6092 | 0.56089 | 4.5583 | 116.932 | 93.731 | 1.455 | 0.40013 | 467.5054 | 28.13 | 48.8
2021-01-12 07:45 | 4.5598 | 2.5 | 0.56718 | 4.3993 | 97.5432 | 81.7191 | 1.4332 | 0.37104 | 467.4677 | 28.15 | 48.78
2021-01-12 07:50 | 4.3308 | 2.3759 | 0.56512 | 4.2091 | 97.865 | 79.6452 | 1.4333 | 0.39289 | 468.4456 | 28.18 | 48.85
2021-01-12 07:55 | 4.1776 | 2.1163 | 0.43113 | 3.6751 | 101.6071 | 62.1136 | 1.4332 | 0.34193 | 469.5501 | 28.17 | 48.68
2021-01-12 08:00 | 4.4833 | 1.9538 | 0.39346 | 3.3905 | 97.715 | 70.581 | 1.4332 | 0.35648 | 467.9234 | 28.2 | 48.6
2021-01-12 08:05 | 5.6046 | 2.0933 | 0.51698 | 3.7256 | 91.7314 | 84.3741 | 1.4551 | 0.62571 | 467.3114 | 28.23 | 48.73
2021-01-12 08:10 | 5.2101 | 2.0538 | 0.56726 | 3.7134 | 105.0583 | 84.4115 | 1.4698 | 0.8295 | 468.8211 | 28.25 | 48.88
2021-01-12 08:15 | 4.0639 | 1.9952 | 0.54008 | 3.5985 | 116.9277 | 81.9197 | 1.4335 | 0.73495 | 467.2762 | 28.21 | 49.15
2021-01-12 08:20 | 3.9488 | 2.0674 | 0.47514 | 3.6442 | 103.8927 | 66.6258 | 1.4261 | 0.49477 | 468.359 | 28.22 | 48.87
2021-01-12 08:25 | 3.7707 | 2.0976 | 0.47517 | 3.6883 | 104.1437 | 45.5648 | 1.4116 | 0.36383 | 468.3145 | 28.23 | 49
2021-01-12 08:30 | 3.6304 | 2.1412 | 0.53585 | 3.8179 | 97.9113 | 73.6271 | 1.4116 | 0.35653 | 468.3524 | 28.26 | 48.72
2021-01-12 08:35 | 3.2098 | 2.0222 | 0.50859 | 3.6083 | 95.2131 | 57.4295 | 1.4187 | 0.27647 | 465.6548 | 28.33 | 48.31
2021-01-12 08:40 | 3.2482 | 2.2695 | 0.55886 | 4.0397 | 88.6869 | 79.9537 | 1.4043 | 0.26193 | 466.0435 | 28.4 | 48.27
2021-01-12 08:45 | 4.5986 | 2.8322 | 0.64262 | 4.9839 | 113.6898 | 80.2127 | 1.3898 | 0.32016 | 466.4054 | 28.49 | 48.15
2021-01-12 08:50 | 5.0302 | 2.374 | 0.58383 | 4.2228 | 106.0342 | 71.7524 | 1.3893 | 0.30551 | 465.9624 | 28.53 | 47.26
2021-01-12 08:55 | 5.3602 | 2.1155 | 0.52931 | 3.7721 | 99.2176 | 55.1854 | 1.389 | 0.3709 | 467.0517 | 28.57 | 46.61
2021-01-12 09:00 | 3.7557 | 1.5954 | 0.39957 | 2.8451 | 92.5499 | 59.0009 | 1.3817 | 0.31997 | 466.543 | 28.58 | 46.41
2021-01-12 09:05 | 2.4829 | 1.2244 | 0.39334 | 2.2701 | 76.2339 | 40.032 | 1.3746 | 0.25455 | 468.1176 | 28.54 | 46.86
2021-01-12 09:10 | 3.0938 | 1.399 | 0.3975 | 2.5419 | 88.0229 | 66.939 | 1.3745 | 0.23999 | 466.0978 | 28.51 | 46.75
2021-01-12 09:15 | 3.717 | 1.6075 | 0.45809 | 2.9221 | 87.9157 | 36.1113 | 1.367 | 0.31266 | 465.5775 | 28.56 | 46.17
2021-01-12 09:20 | 4.4176 | 1.6978 | 0.45814 | 3.0605 | 91.7441 | 59.8149 | 1.3671 | 0.31996 | 466.5337 | 28.59 | 46.35
2021-01-12 09:25 | 3.0542 | 1.663 | 0.48513 | 3.0342 | 86.4435 | 53.7027 | 1.352 | 0.26168 | 467.743 | 28.61 | 45.28
2021-01-12 09:30 | 3.4483 | 1.6014 | 0.46417 | 2.9188 | 86.831 | 51.101 | 1.3519 | 0.30526 | 466.7588 | 28.6 | 45.03
2021-01-12 09:35 | 4.7337 | 1.7542 | 0.50601 | 3.1929 | 93.6348 | 69.3659 | 1.3665 | 0.38523 | 466.6775 | 28.64 | 45.03
2021-01-12 09:40 | 5.1924 | 1.6726 | 0.48725 | 3.0511 | 94.0432 | 57.0551 | 1.3739 | 0.37074 | 467.5948 | 28.69 | 45.2
2021-01-12 09:45 | 4.0856 | 1.7778 | 0.48521 | 3.2082 | 95.8349 | 60.5841 | 1.4031 | 0.3635 | 467.5146 | 28.71 | 45.41
2021-01-12 09:50 | 3.4895 | 1.5591 | 0.50015 | 2.89 | 97.4504 | 36.3516 | 1.3603 | 0.27643 | 467.6704 | 28.77 | 46.72
2021-01-12 09:55 | 3.1978 | 1.5965 | 0.45847 | 2.9078 | 86.3981 | 51.368 | 1.3535 | 0.26925 | 466.9235 | 28.8 | 47.57
2021-01-12 10:00 | 3.5413 | 1.7329 | 0.4605 | 3.1188 | 93.3272 | 54.4188 | 1.3607 | 0.2765 | 466.9202 | 28.84 | 47.15
2021-01-12 10:05 | 3.4642 | 1.8636 | 0.39553 | 3.2543 | 98.5051 | 61.6625 | 1.3531 | 0.29827 | 466.4099 | 28.89 | 46.53
2021-01-12 10:10 | 3.5912 | 1.8594 | 0.45619 | 3.3063 | 88.1155 | 60.7507 | 1.3457 | 0.32734 | 466.9111 | 28.93 | 46.22
2021-01-12 10:15 | 3.6051 | 2.0853 | 0.46889 | 3.6632 | 89.3465 | 52.2912 | 1.3462 | 0.34927 | 467.2538 | 28.95 | 46.96
2021-01-12 10:20 | 3.3506 | 2.192 | 0.42287 | 3.7849 | 110.0208 | 101.1743 | 1.339 | 0.37113 | 467.1339 | 29.01 | 46.94
2021-01-12 10:25 | 3.1987 | 1.9358 | 0.37484 | 3.3422 | 122.0874 | 58.2248 | 1.3321 | 0.32757 | 466.9023 | 29.06 | 47.61
2021-01-12 10:30 | 3.3523 | 1.8856 | 0.4922 | 3.3846 | 113.421 | 59.6116 | 1.3324 | 0.29851 | 465.2333 | 29.07 | 48.01
2021-01-12 10:35 | 2.307 | 1.8036 | 0.4524 | 3.217 | 102.2028 | 45.6818 | 1.3251 | 0.21842 | 467.2896 | 29.1 | 47.89
2021-01-12 10:40 | 2.6895 | 1.6124 | 0.46498 | 2.9386 | 89.0724 | 45.092 | 1.3251 | 0.24755 | 466.1946 | 29.12 | 47.92
2021-01-12 10:45 | 2.7149 | 1.6451 | 0.45659 | 2.9783 | 81.3097 | 40.4917 | 1.3323 | 0.24026 | 466.672 | 29.16 | 47.73
2021-01-12 10:50 | 3.1097 | 1.3936 | 0.45654 | 2.5927 | 92.8846 | 50.4901 | 1.3322 | 0.24752 | 467.7171 | 29.19 | 47.42
2021-01-12 10:55 | 3.1317 | 1.3456 | 0.4372 | 2.4977 | 91.3529 | 82.7879 | 1.3307 | 0.22542 | 465.614 | 29.2 | 44.63
2021-01-12 11:00 | 2.9646 | 1.4213 | 0.39097 | 2.5695 | 101.0971 | 62.7734 | 1.3227 | 0.21076 | 466.321 | 29.24 | 43.26
2021-01-12 11:05 | 3.0901 | 1.5554 | 0.51403 | 2.9003 | 99.2073 | 77.0912 | 1.3147 | 0.21064 | 466.5301 | 29.28 | 41.76
2021-01-12 11:10 | 2.5558 | 1.5198 | 0.48682 | 2.8185 | 95.2826 | 31.1065 | 1.3073 | 0.18884 | 466.5078 | 29.32 | 41.46
2021-01-12 11:15 | 2.6071 | 1.5705 | 0.42003 | 2.8253 | 98.4427 | 48.2447 | 1.3148 | 0.21066 | 465.857 | 29.35 | 41.8
2021-01-12 11:20 | 3.6178 | 1.5581 | 0.41446 | 2.8007 | 89.8838 | 52.473 | 1.317 | 0.25467 | 467.1286 | 29.38 | 45.73
2021-01-12 11:25 | 4.168 | 1.6137 | 0.46496 | 2.9385 | 98.0531 | 45.529 | 1.3323 | 0.32034 | 466.8091 | 29.41 | 47.05
2021-01-12 11:30 | 3.6848 | 1.8411 | 0.51749 | 3.3396 | 101.1337 | 56.1106 | 1.34 | 0.32773 | 466.6008 | 29.45 | 47.69
2021-01-12 11:35 | 2.7549 | 1.9715 | 0.53651 | 3.5565 | 112.7862 | 25.9365 | 1.3332 | 0.26226 | 465.95 | 29.44 | 48.45
2021-01-12 11:40 | 2.3087 | 2.1016 | 0.54494 | 3.7685 | 86.5206 |  | 1.3406 | 0.26229 | 463.2944 | 29.44 | 48.66
2021-01-12 11:45 | 2.3733 | 2.1803 | 0.53464 | 3.8725 | 86.2334 | 38.7479 | 1.3337 | 0.2478 | 464.6601 | 29.47 | 49.38
2021-01-12 11:50 | 2.2715 | 1.8085 | 0.52005 | 3.2922 | 73.149 | 43.5627 | 1.3267 | 0.24055 | 464.0892 | 29.49 | 49.66
2021-01-12 11:55 | 2.3481 | 1.5404 | 0.45714 | 2.8183 | 79.121 | 49.5553 | 1.3339 | 0.22597 | 464.5981 | 29.5 | 49.62
2021-01-12 12:00 | 2.5651 | 1.4624 | 0.43827 | 2.6799 | 66.0132 | 46.2378 | 1.3267 | 0.22597 | 463.5031 | 29.53 | 49.56
2021-01-12 12:05 | 2.3609 | 1.6512 | 0.45924 | 2.9903 | 73.9453 | 49.3615 | 1.3194 | 0.24784 | 464.5038 | 29.56 | 49.46
2021-01-12 12:10 | 2.8714 | 1.6362 | 0.42779 | 2.9358 | 94.722 | 74.8138 | 1.3267 | 0.24784 | 465.0519 | 29.54 | 49.54
2021-01-12 12:15 | 3.1141 | 2.0085 | 0.55576 | 3.6365 | 104.3901 | 77.4962 | 1.3341 | 0.24787 | 465.0067 | 29.54 | 49.77
2021-01-12 12:20 | 2.5271 | 1.724 | 0.5348 | 3.1773 | 98.0932 | 68.9726 | 1.3341 | 0.24058 | 464.456 | 29.55 | 49.81
2021-01-12 12:25 | 3.0502 | 1.535 | 0.49702 | 2.85 | 88.5302 | 42.4528 | 1.3413 | 0.25515 | 465.5463 | 29.54 | 49.68
2021-01-12 12:30 | 3.2036 | 1.501 | 0.55159 | 2.8523 | 84.7286 | 50.5227 | 1.3342 | 0.24059 | 462.8845 | 29.55 | 49.84
2021-01-12 12:35 | 3.0889 | 1.6762 | 0.51386 | 3.0832 | 95.1891 | 98.0074 | 1.3342 | 0.22602 | 464.3963 | 29.57 | 49.9
2021-01-12 12:40 | 3.0513 | 1.656 | 0.42587 | 2.9622 | 139.8037 | 94.8128 | 1.3418 | 0.27712 | 464.2125 | 29.62 | 50.3
2021-01-12 12:45 | 3.4222 | 1.5851 | 0.38398 | 2.8137 | 127.4678 | 79.4759 | 1.3494 | 0.29175 | 464.6208 | 29.64 | 50.66
2021-01-12 12:50 | 3.5891 | 1.6485 | 0.44494 | 2.974 | 127.8074 | 73.0591 | 1.3497 | 0.29912 | 464.976 | 29.67 | 51.18
2021-01-12 12:55 | 4.5726 | 1.5199 | 0.44705 | 2.7767 | 114.4436 | 76.6466 | 1.3643 | 0.31372 | 462.8849 | 29.67 | 51.21
2021-01-12 13:00 | 4.4594 | 1.5588 | 0.44722 | 2.8366 | 110.2551 | 75.9294 | 1.3648 | 0.34303 | 464.2266 | 29.7 | 52.01
2021-01-12 13:05 | 3.706 | 1.4343 | 0.44098 | 2.6396 | 100.9464 | 46.0464 | 1.3796 | 0.30658 | 465.6798 | 29.73 | 52.24
2021-01-12 13:10 | 2.863 | 1.177 | 0.36544 | 2.1695 | 91.4007 | 53.6094 | 1.3871 | 0.29932 | 464.0804 | 29.71 | 52.64
2021-01-12 13:15 | 2.5947 | 1.3277 | 0.40325 | 2.4384 | 93.8071 | 48.2431 | 1.4018 | 0.30664 | 462.5615 | 29.67 | 52.85
2021-01-12 13:20 | 2.4422 | 1.59 | 0.50005 | 2.9372 | 95.7229 | 63.788 | 1.4023 | 0.27023 | 465.489 | 29.69 | 53.63
2021-01-12 13:25 | 2.3272 | 1.4612 | 0.47485 | 2.7125 | 101.8324 | 69.8761 | 1.4096 | 0.25563 | 464.9099 | 29.72 | 53.6
2021-01-12 13:30 | 2.3397 | 1.4679 | 0.44539 | 2.6955 | 110.5178 | 92.4442 | 1.4314 | 0.2264 | 464.9496 | 29.72 | 53.4
2021-01-12 13:35 | 3.1567 | 1.8482 | 0.49562 | 3.3286 | 118.7141 | 70.2613 | 1.4527 | 0.2555 | 464.1102 | 29.71 | 52.49
2021-01-12 13:40 | 3.4762 | 2.2126 | 0.60691 | 3.9985 | 114.0918 | 71.8148 | 1.4527 | 0.3139 | 463.4706 | 29.79 | 52.23
2021-01-12 13:45 | 3.3482 | 2.2618 | 0.52498 | 3.994 | 111.1912 | 81.1545 | 1.4453 | 0.29928 | 462.4132 | 29.82 | 51.99
2021-01-12 13:50 | 2.7616 | 1.8434 | 0.41388 | 3.2396 | 109.0848 | 69.3377 | 1.4241 | 0.27021 | 462.6421 | 29.87 | 52.92
2021-01-12 13:55 | 3.3505 | 2.3415 | 0.49801 | 4.085 | 95.8692 | 62.0168 | 1.4317 | 0.35062 | 463.082 | 29.86 | 53.43
2021-01-12 14:00 | 3.8748 | 1.863 | 0.43287 | 3.2886 | 114.3659 | 73.9762 | 1.4317 | 0.31409 | 462.5309 | 29.88 | 53.37
2021-01-12 14:05 | 3.8616 | 1.7367 | 0.41392 | 3.076 | 110.3344 |  | 1.4169 | 0.33597 | 464.6582 | 29.88 | 53.14
2021-01-12 14:10 | 3.7204 | 1.5775 | 0.40756 | 2.8235 | 98.9865 | 41.8734 | 1.4313 | 0.35784 | 463.1765 | 29.87 | 52.85
2021-01-12 14:15 | 3.6183 | 1.7009 | 0.43069 | 3.04 | 97.1083 | 55.5811 | 1.4387 | 0.35055 | 462.6228 | 29.88 | 52.91
2021-01-12 14:20 | 3.976 | 2.0146 | 0.49998 | 3.5881 | 106.7259 | 75.3883 | 1.4532 | 0.35052 | 464.1699 | 29.91 | 52.66
2021-01-12 14:25 | 3.8477 | 1.8308 | 0.53563 | 3.3419 | 126.4194 | 108.2367 | 1.453 | 0.29937 | 462.1138 | 29.93 | 52.32
2021-01-12 14:30 | 3.7971 | 1.62 | 0.45377 | 2.9369 | 128.7069 | 87.6013 | 1.4313 | 0.2629 | 463.5821 | 29.95 | 52.57
2021-01-12 14:35 | 3.0302 | 1.5625 | 0.51473 | 2.9119 | 124.2252 | 72.0803 | 1.4022 | 0.30673 | 462.5371 | 29.97 | 52.61
2021-01-12 14:40 | 3.0048 | 1.6709 | 0.50215 | 3.0633 | 127.905 | 70.7651 | 1.4169 | 0.38709 | 462.4936 | 29.98 | 52.72
2021-01-12 14:45 | 3.1323 | 1.5378 | 0.5 | 2.8571 | 118.0011 | 74.8796 | 1.446 | 0.37975 | 463.031 | 30 | 52.42
2021-01-12 14:50 | 3.1833 | 1.7597 | 0.53149 | 3.2309 | 126.8827 | 105.5788 | 1.4605 | 0.36512 | 464.0487 | 30.03 | 52.21
2021-01-12 14:55 | 4.4361 | 2.1749 | 0.53357 | 3.8673 | 144.4805 | 105.7294 | 1.4312 | 0.49655 | 463.9997 | 30.07 | 52.03
2021-01-12 15:00 | 4.32 | 2.8704 | 0.58595 | 4.9858 | 150.6015 | 102.1768 | 1.3871 | 0.47453 | 464.0179 | 30.13 | 51.31
2021-01-12 15:05 | 4.8681 | 2.1559 | 0.4913 | 3.796 | 149.7498 | 96.7905 | 1.3794 | 0.51819 | 463.1146 | 30.13 | 50.64
2021-01-12 15:10 | 3.9735 | 1.6422 | 0.47237 | 2.9896 | 133.2018 | 77.2309 | 1.3574 | 0.3357 | 463.7272 | 30.09 | 50.6
2021-01-12 15:15 | 3.999 | 1.686 | 0.43457 | 3.0189 | 115.6404 | 44.5125 | 1.3939 | 0.40868 | 463.7484 | 30.08 | 50.6
2021-01-12 15:20 | 3.7434 | 1.9161 | 0.47656 | 3.4136 | 113.7392 | 82.0337 | 1.3939 | 0.30651 | 462.6785 | 30.1 | 50.54
2021-01-12 15:25 | 4.1652 | 1.9641 | 0.46188 | 3.4725 | 117.0655 | 87.6381 | 1.3866 | 0.33571 | 462.6 | 30.14 | 50.51
2021-01-12 15:30 | 4.3562 | 1.7365 | 0.41983 | 3.0795 | 105.8267 | 42.6679 | 1.3426 | 0.40863 | 462.684 | 30.13 | 50.2
2021-01-12 15:35 | [9 empty] | 30.09 | 50.23
2021-01-12 15:40 | 5.211 | 1.8648 | 0.45752 | 3.3139 | 110.9738 | 71.4622 | 1.4372 | 0.37207 | 463.3353 | 30.11 | 49.76
2021-01-12 15:45 | 4.5578 | 1.8764 | 0.45733 | 3.3356 | 111.8685 | 63.0582 | 1.3783 | 0.2917 | 462.4368 | 30.14 | 48.75
2021-01-12 15:50 | 3.9464 | 1.7607 | 0.49107 | 3.1899 | 111.2035 | 83.4537 | 1.3423 | 0.36475 | 461.2009 | 30.16 | 49.51
2021-01-12 15:55 | 4.6362 | 1.6361 | 0.49109 | 2.9969 | 107.3455 | 70.2763 | 1.3642 | 0.37206 | 462.7126 | 30.18 | 49.54
2021-01-12 16:00 | 5.5565 | 1.7664 | 0.46807 | 3.1757 | 110.8345 | 87.8419 | 1.3571 | 0.42319 | 462.6347 | 30.19 | 49.82
2021-01-12 16:05 | 5.5952 | 1.8391 | 0.44921 | 3.2662 | 116.0223 | 90.5348 | 1.3426 | 0.56915 | 462.5464 | 30.23 | 49.84
2021-01-12 16:10 | 5.913 | 1.5566 | 0.4302 | 2.8162 | 121.8055 | 94.8943 | 1.3423 | 0.48146 | 462.6517 | 30.24 | 49.22
2021-01-12 16:15 | 4.7901 | 1.4159 | 0.43868 | 2.609 | 112.7757 | 77.4592 | 1.3863 | 0.40859 | 463.0647 | 30.25 | 49.64
2021-01-12 16:20 | 3.5895 | 1.5241 | 0.45969 | 2.7938 | 94.1294 | 48.5516 | 1.3572 | 0.24808 | 463.0185 | 30.27 | 49.66
2021-01-12 16:25 | 3.7172 | 1.6843 | 0.50587 | 3.0856 | 94.3643 | 85.4225 | 1.379 | 0.23349 | 461.4446 | 30.28 | 49.63
2021-01-12 16:30 | 5.0202 | 1.709 | 0.45759 | 3.0772 | 92.7699 | 70.6351 | 1.3644 | 0.29186 | 461.4765 | 30.26 | 49.68
2021-01-12 16:35 | 5.3278 | 1.8504 | 0.53536 | 3.3717 | 106.1072 | 75.6989 | 1.3428 | 0.3503 | 461.8256 | 30.31 | 50
2021-01-12 16:40 | 4.5225 | 1.6174 | 0.47023 | 2.9515 | 100.2506 | 49.8953 | 1.3354 | 0.38676 | 461.2915 | 30.35 | 49.66
2021-01-12 16:45 | 4.5989 | 1.6803 | 0.47021 | 3.048 | 91.7535 | 52.5401 | 1.3353 | 0.40863 | 462.8853 | 30.34 | 49.59
2021-01-12 16:50 | 4.9826 | 1.6695 | 0.47445 | 3.0336 | 102.0956 | 43.9904 | 1.3647 | 0.43786 | 462.3058 | 30.35 | 49.78
2021-01-12 16:55 | 5.2385 | 1.6559 | 0.44299 | 2.9813 | 92.6886 | 76.3751 | 1.3939 | 0.47438 | 462.8243 | 30.33 | 49.99
2021-01-12 17:00 | 4.5994 | 1.6805 | 0.46396 | 3.0378 | 102.771 | 68.1835 | 1.3647 | 0.47435 | 462.883 | 30.31 | 49.91
2021-01-12 17:05 | 3.9087 | 1.6158 | 0.38831 | 2.8651 | 101.2488 | 66.1367 | 1.3206 | 0.33563 | 463.5077 | 30.3 | 49.5
2021-01-12 17:10 | 3.3462 | 1.48 | 0.37146 | 2.6401 | 88.8085 | 62.2845 | 1.3204 | 0.2991 | 463.1382 | 30.25 | 49.28
2021-01-12 17:15 | 3.4097 | 1.4306 | 0.36093 | 2.5538 | 86.6335 | 48.4861 | 1.3203 | 0.32095 | 462.1921 | 30.22 | 49.13
2021-01-12 17:20 | 3.843 | 1.2975 | 0.37344 | 2.3623 | 71.9171 | 57.3416 | 1.32 | 0.31359 | 461.3109 | 30.18 | 48.76
2021-01-12 17:25 | 3.8164 | 1.0905 | 0.3188 | 1.9904 | 65.3305 | 33.523 | 1.3269 | 0.32079 | 462.6073 | 30.1 | 48.32
2021-01-12 17:30 | 3.3307 | 1.0137 | 0.30196 | 1.8537 | 53.5875 | 39.6929 | 1.3194 | 0.29886 | 463.3557 | 30.01 | 48.12
2021-01-12 17:35 | 3.1262 | 1.03 | 0.27467 | 1.8535 | 60.6356 | 32.8902 | 1.3192 | 0.26968 | 465.6097 | 29.93 | 48.1
2021-01-12 17:40 | 3.305 | 1.1792 | 0.29146 | 2.0989 | 58.3721 | 55.8404 | 1.312 | 0.26969 | 464.6393 | 29.87 | 48.37
2021-01-12 17:45 | 2.5775 | 1.1052 | 0.28725 | 1.9793 | 72.7529 | 55.1644 | 1.3047 | 0.24781 | 464.7039 | 29.84 | 48.36
2021-01-12 17:50 | 2.3604 | 0.98342 | 0.27045 | 1.7779 | 68.6737 | 56.8946 | 1.3118 | 0.23321 | 466.9068 | 29.79 | 48.29
2021-01-12 17:55 | 2.0029 | 0.84654 | 0.23898 | 1.5387 | 52.9277 | 28.9949 | 1.3117 | 0.2259 | 468.6148 | 29.7 | 48.3
2021-01-12 18:00 | 1.7466 | 0.72709 | 0.22625 | 1.3429 | 44.2345 | 11.0051 | 1.3108 | 0.17478 | 468.0882 | 29.56 | 47.17
2021-01-12 18:05 | 1.6833 | 0.79562 | 0.22421 | 1.4459 | 53.3861 | 34.1761 | 1.3111 | 0.17482 | 467.5599 | 29.49 | 47.94
2021-01-12 18:10 | 1.4286 | 0.65498 | 0.21798 | 1.222 | 47.1651 | 58.2879 | 1.3042 | 0.14572 | 468.0225 | 29.45 | 48.67
2021-01-12 18:15 | 1.301 | 0.5483 | 0.2054 | 1.0459 | 38.3059 | 33.6427 | 1.3041 | 0.13843 | 469.2118 | 29.37 | 48.79
2021-01-12 18:20 | 1.1861 | 0.50313 | 0.21795 | 0.98916 | 37.8428 | 16.8451 | 1.304 | 0.094704 | 466.8026 | 29.27 | 48.82
2021-01-12 18:25 | 1.0969 | 0.65083 | 0.23683 | 1.2345 | 42.172 | 32.1417 | 1.3041 | 0.094711 | 466.8754 | 29.2 | 49.2
2021-01-12 18:30 | 1.1989 | 0.80533 | 0.23892 | 1.4734 | 46.9159 | 44.212 | 1.3041 | 0.094709 | 466.9608 | 29.15 | 49.3
2021-01-12 18:35 | 1.0841 | 0.6959 | 0.22214 | 1.2909 | 44.6273 | 28.6496 | 1.2967 | 0.087418 | 467.0693 | 29.1 | 49.28
2021-01-12 18:40 | 1.0457 | 0.5195 | 0.1886 | 0.98491 | 30.3315 | 26.7811 | 1.2966 | 0.080129 | 469.3255 | 29.01 | 49.41
2021-01-12 18:45 | 1.0968 | 0.50721 | 0.20747 | 0.98494 | 31.7506 | 26.5268 | 1.2967 | 0.087416 | 468.9282 | 28.92 | 49.74
2021-01-12 18:50 | 1.1096 | 0.54141 | 0.22424 | 1.0541 | 24.0791 | 19.9979 | 1.304 | 0.07285 | 468.4489 | 28.88 | 49.95
2021-01-12 18:55 | 1.2625 | 0.54548 | 0.18231 | 1.0184 | 11.0696 | 3.5912 | 1.3039 | 0.087414 | 469.064 | 28.84 | 49.91
2021-01-12 19:00 | 1.4922 | 0.9707 | 0.19071 | 1.6786 | 9.4479 | 30.2924 | 1.2967 | 0.12384 | 470.2113 | 28.76 | 50.27
2021-01-12 19:05 | 2.3082 | 0.93233 | 0.1844 | 1.6135 | 21.23 | 38.7466 | 1.2966 | 0.16025 | 469.244 | 28.74 | 50.07
2021-01-12 19:10 | 1.4028 | 0.67262 | 0.16345 | 1.1945 | 31.2703 | 38.5956 | 1.2966 | 0.13112 | 469.8836 | 28.65 | 50.46
2021-01-12 19:15 | 1.5565 | 0.66468 | 0.16352 | 1.1824 | 40.417 | 19.7594 | 1.2971 | 0.13117 | 469.2878 | 28.58 | 51.63
2021-01-12 19:20 | 1.2119 | 0.58943 | 0.15932 | 1.0649 | 33.608 | 23.5858 | 1.2971 | 0.10202 | 468.8605 | 28.53 | 51.68
2021-01-12 19:25 | 1.2885 | 0.41713 | 0.1153 | 0.75259 | 15.1664 | 25.4848 | 1.2971 | 0.10202 | 469.0655 | 28.39 | 52.17
2021-01-12 19:30 | 1.1486 | 0.42549 | 0.14051 | 0.7927 | 10.4345 | 21.2161 | 1.3049 | 0.087478 | 469.5606 | 28.3 | 53.36
2021-01-12 19:35 | 1.6339 | 0.63357 | 0.16361 | 1.1369 | 8.5269 | 26.0607 | 1.3051 | 0.094787 | 470.0379 | 28.27 | 53.96
2021-01-12 19:40 | 1.1744 | 0.52958 | 0.14893 | 0.96069 | 15.8083 | 15.9615 | 1.2979 | 0.087497 | 471.1225 | 28.24 | 54.11
2021-01-12 19:45 | 1.0724 | 0.45985 | 0.14685 | 0.85172 | 6.894 | 34.6949 | 1.298 | 0.072924 | 470.5946 | 28.17 | 54.71
2021-01-12 19:50 | 0.91938 | 0.36411 | 0.12589 | 0.68402 | 12.524 | 4.2291 | 1.2983 | 0.05835 | 470.6008 | 28.11 | 55.38
2021-01-12 19:55 | 0.7408 | 0.25878 | 0.12383 | 0.5205 | 1.0933 | 26.8222 | 1.2986 | 0.043774 | 471.6509 | 28.03 | 56.32
2021-01-12 20:00 | 0.70256 | 0.23279 | 0.11335 | 0.47018 | 1.4409 | 20.3564 | 1.2988 | 0.043779 | 471.8036 | 27.9 | 57.03
2021-01-12 20:05 | 0.61319 | 0.29032 | 0.11965 | 0.56467 | 2.1155 | 12.1513 | 1.3061 | 0.043782 | 470.323 | 27.82 | 57.47
2021-01-12 20:10 | 0.63863 | 0.37517 | 0.15531 | 0.73038 | 6.56 | 20.5689 | 1.3059 | 0.05107 | 470.9435 | 27.81 | 57.06
2021-01-12 20:15 | 0.70241 | 0.28476 | 0.1406 | 0.575 | 1.2669 | 12.5974 | 1.3058 | 0.043769 | 472.6196 | 27.78 | 56.86
2021-01-12 20:20 | 0.72813 | 0.31359 | 0.10285 | 0.58354 | 3.1884 |  | 1.3061 | 0.072966 | 470.4821 | 27.73 | 57.67
2021-01-12 20:25 | 0.90715 | 0.38351 | 0.13857 | 0.72642 | 11.5502 |  | 1.3064 | 0.065683 | 471.5156 | 27.68 | 58.37
2021-01-12 20:30 | 1.3673 | 0.33836 | 0.10499 | 0.62364 | 2.9442 | -3.4145 | 1.3066 | 0.065693 | 471.4293 | 27.69 | 58.73
2021-01-12 20:35 | 1.0352 | 0.20413 | 0.1176 | 0.4305 | 10.1216 | 16.1128 | 1.3067 | 0.058399 | 471.992 | 27.64 | 59.13
2021-01-12 20:40 | 0.92032 | 0.27679 | 0.12392 | 0.5482 | 7.6489 | -1.7179 | 1.3069 | 0.051108 | 470.9172 | 27.6 | 59.76
2021-01-12 20:45 | 0.79252 | 0.21651 | 0.13023 | 0.46209 | 22.7836 | 163.0953 | 1.307 | 0.05111 | 436.8376 | 27.56 | 59.98
2021-01-12 20:50 | 0.92023 | 0.24251 | 0.10291 | 0.47464 | 186.2441 | 375.7498 | 1.3141 | 0.080305 | 361.7222 | 27.49 | 59.95
2021-01-12 20:55 | 1.0865 | 0.36448 | 0.13442 | 0.69312 | 119.1703 | 62.6733 | 1.3142 | 0.051108 | 362.2025 | 27.5 | 60.16
2021-01-12 21:00 | 1.1121 | 0.28365 | 0.11762 | 0.55241 | 55.2821 | 26.8639 | 1.3143 | 0.058411 | 361.6761 | 27.49 | 60.29
2021-01-12 21:05 | 1.2784 | 0.30149 | 0.11133 | 0.57347 | 32.4195 | 35.958 | 1.3144 | 0.051114 | 361.6805 | 27.46 | 60.63
2021-01-12 21:10 | 0.9333 | 0.23299 | 0.088235 | 0.44538 | 18.6149 | 16.7023 | 1.3145 | 0.058422 | 360.1394 | 27.4 | 61.11
2021-01-12 21:15 | 0.9716 | 0.12197 | 0.077726 | 0.26469 | 5.7273 | 16.7728 | 1.3144 | 0.036512 | 361.8726 | 27.29 | 61.33
2021-01-12 21:20 | 0.6903 | 0.10415 | 0.067218 | 0.22686 | 71.0349 | 264.1873 | 1.3143 | 0.021906 | 185.4137 | 27.17 | 61.67
2021-01-12 21:25 | 0.5369 | 0.090445 | 0.071419 | 0.21006 | 293.1594 | 250.3912 | 1.307 | 0 | 6.85 | 27.07 | 62.03
2021-01-12 21:30 | 0.48575 | 0.079479 | 0.060914 | 0.18484 | 148.7323 | 30.7609 | 1.2924 | -0.021905 | 7.3788 | 27 | 62.19
2021-01-12 21:35 | 0.48576 | 0.072629 | 0.063016 | 0.17434 | 57.821 | 20.0748 | 1.2705 | 0.058414 | 6.3248 | 26.99 | 62.28
2021-01-12 21:40 | 0.4602 | 0.063037 | 0.060916 | 0.15754 | 11.3004 | 13.182 | 1.2851 | 0.087621 | 5.7977 | 26.99 | 62.28
2021-01-12 21:45 | 0.43466 | 0.05893 | 0.056719 | 0.14915 | -6.1671 | -6.8625 | 1.3071 | 0.043814 | 7.3777 | 27.02 | 62.37
2021-01-12 21:50 | 0.34518 | 0.045227 | 0.05462 | 0.12394 | -3.0069 | -1.3807 | 1.3072 | 0.036513 | 8.9577 | 27.04 | 62.39
2021-01-12 21:55 | 0.37071 | 0.032888 | 0.048312 | 0.098724 | -7.2914 | 3.5486 | 1.3143 | 0.036508 | 6.326 | 26.94 | 62.42
2021-01-12 22:00 | 0.34517 | 0.037002 | 0.050416 | 0.10713 | -19.3804 | 1.3909 | 1.3144 | 0.029209 | 7.9069 | 26.94 | 62.61
2021-01-12 22:05 | 0.30683 | 0.030151 | 0.054619 | 0.10084 | -11.6491 | 5.349 | 1.3144 | 0.02921 | 8.4337 | 26.94 | 62.72
2021-01-12 22:10 | 0.26846 | 0.026038 | 0.052517 | 0.09453 | 2.7204 | -4.459 | 1.3144 | 0.029209 | 11.5975 | 26.92 | 62.7
2021-01-12 22:15 | 0.26843 | 0.027405 | 0.048309 | 0.088216 | -2.8121 | 1.0533 | 1.3215 | 0.0073013 | 7.9095 | 26.88 | 62.49
2021-01-12 22:20 | 0.2812 | 0.026034 | 0.048308 | 0.088214 | -18.6004 | 1.3089 | 1.3142 | 0.014602 | 11.6001 | 26.9 | 62.35
2021-01-12 22:25 | 0.29398 | 0.021923 | 0.046207 | 0.079812 | -10.7981 | 4.7037 | 1.3069 | 0.014602 | 6.8542 | 26.92 | 62.25
2021-01-12 22:30 | 0.34511 | 0.021923 | 0.046207 | 0.079812 | 0.6442 | -7.4953 | 1.2996 | 0.021903 | 17.3992 | 26.92 | 62.24
2021-01-12 22:35 | 0.29393 | 0.017809 | 0.044098 | 0.069297 | 4.7846 | -4.5188 | 1.2993 | 0 | 12.6589 | 26.86 | 61.92
2021-01-12 22:40 | 0.26836 | 0.017809 | 0.044097 | 0.071396 | -10.162 | 0.34759 | 1.292 | -0.036497 | 13.1901 | 26.78 | 62.17
2021-01-12 22:45 | 0.24282 | 0.01644 | 0.042001 | 0.067202 | -8.5679 | 6.0425 | 1.2702 | 0 | 11.0791 | 26.77 | 62.44
2021-01-12 22:50 | 0.24284 | 0.017812 | 0.046204 | 0.071407 | 0.18405 | 7.3517 | 1.263 | 0.094907 | 8.4409 | 26.76 | 62.67
2021-01-12 22:55 | 0.24285 | 0.015072 | 0.044106 | 0.069309 | 8.7119 | -5.174 | 1.2849 | 0.08761 | 6.3294 | 26.81 | 62.58
2021-01-12 23:00 | 0.2045 | 0.016442 | 0.042005 | 0.069309 | 8.4051 | 1.9632 | 1.2995 | 0.080309 | 8.9673 | 26.79 | 62.65
2021-01-12 23:05 | 0.19171 | 0.013701 | 0.037802 | 0.058803 | -3.3843 | 9.3042 | 1.3067 | 0.043801 | 14.2433 | 26.79 | 62.43
2021-01-12 23:10 | 0.20447 | 0.01507 | 0.039899 | 0.062998 | -5.6639 | 10.5815 | 1.3139 | 0.036498 | 8.972 | 26.68 | 62.63
2021-01-12 23:15 | 0.21727 | 0.017811 | 0.042001 | 0.067202 | 2.9753 | 5.8381 | 1.314 | 0.029201 | 11.0831 | 26.66 | 62.87
2021-01-12 23:20 | 0.21727 | 0.016441 | 0.037803 | 0.060904 | 10.6132 | -13.1694 | 1.3214 | 0.021901 | 7.9159 | 26.67 | 62.95
2021-01-12 23:25 | 0.23004 | 0.0137 | 0.0357 | 0.056701 | 6.5638 | 2.7605 | 1.3213 | 0.0219 | 7.9185 | 26.59 | 63.07
2021-01-12 23:30 | 0.19171 | 0.015071 | 0.037803 | 0.058804 | -7.147 | 6.646 | 1.3214 | 0.014601 | 9.5017 | 26.59 | 63.23
2021-01-12 23:35 | 0.21728 | 0.013701 | 0.035704 | 0.056706 | -4.9387 | 11.8303 | 1.3214 | 0.029203 | 10.0299 | 26.57 | 63.4
2021-01-12 23:40 | 0.20452 | 0.013703 | 0.037808 | 0.058813 | 3.4053 | 0.040905 | 1.3216 | -0.014603 | 12.6661 | 26.61 | 63.58
2021-01-12 23:45 | 0.17895 | 0.013703 | 0.037807 | 0.058811 | 9.6634 | -10.4917 | 1.3069 | -0.029205 | 12.667 | 26.6 | 63.52
2021-01-12 23:50 |  | 0.015073 | 0.037807 | 0.058812 | 0.92034 | -2.4951 | 1.285 | 0.043808 | 10.0282 | 26.59 | 63.6
2021-01-12 23:55 | 0.17895 | 0.015073 | 0.035707 | 0.058811 | -6.6162 | 7.3115 | 1.2996 | 0.051109 | 8.9727 | 26.59 | 63.58
2021-01-13 | 0.1534 | 0.015075 | 0.037811 | 0.060918 | -1.9533 | 10.0429 | 1.3071 | 0.029208 | 9.4976 | 26.65 | 63.64
2021-01-13 00:05 | 0.15341 | 0.015075 | 0.037812 | 0.06092 | 6.2489 | -0.71591 | 1.3144 | 0.029209 | 11.0791 | 26.68 | 63.62
2021-01-13 00:10 | 0.19176 | 0.021927 | 0.027309 | 0.060919 | 10.6568 | -4.5818 | 1.3144 | 0.021907 | 8.9689 | 26.68 | 63.6
2021-01-13 00:15 | 0.25569 | 0.020557 | 0.033611 | 0.063021 | -6.1876 | 2.158 | 1.3071 | 0.014605 | 6.8579 | 26.7 | 63.58
2021-01-13 00:20 | 0.24289 | 0.017816 | 0.035711 | 0.06302 | -9.409 | 1.5648 | 1.3071 | 0.014604 | 6.8581 | 26.7 | 63.51
2021-01-13 00:25 | 0.20454 | 0.017816 | 0.039913 | 0.069322 | -0.52159 | 10.3397 | 1.3071 | 0.021907 | 7.9132 | 26.7 | 63.52
2021-01-13 00:30 | 0.21732 | 0.019186 | 0.037811 | 0.06932 | 7.7008 | -5.3896 |  |  | 7.914 | 26.68 | 63.51
2021-01-13 00:35 | 0.23011 | 0.021927 | 0.037811 | 0.071421 | 8.0077 | -7.4452 | 1.2998 | -0.03651 | 6.3311 | 26.68 | 63.52
2021-01-13 00:40 | 0.24289 | 0.019186 | 0.039912 | 0.06722 | -3.7021 | 2.9249 | 1.2779 | 0.021906 | 8.4409 | 26.7 | 63.45
2021-01-13 00:45 | 0.25567 | 0.017815 | 0.037811 | 0.065119 | -5.6043 | 9.4804 | 1.2852 | 0.051114 | 9.4967 | 26.68 | 63.52
2021-01-13 00:50 | 0.23008 | 0.016443 | 0.033607 | 0.058812 | 2.8224 | 5.5732 | 1.2996 | 0.029205 | 7.388 | 26.64 | 63.41
2021-01-13 00:55 | 0.21731 | 0.017814 | 0.039909 | 0.065114 | 9.4796 | -10.3284 | 1.2997 | -0.021904 | 5.8048 | 26.64 | 63.46
2021-01-13 01:00 | 0.23009 | 0.017814 | 0.035707 | 0.065113 | 2.6895 | 3.1598 | 1.2923 | 0 | 9.4978 | 26.67 | 63.32
2021-01-13 01:05 |  |  |  |  | -7.5054 | 2.4234 |  |  | 9.4994 | 26.64 | 63.25
2021-01-13 01:10 |  |  |  |  | -3.9266 | 4.9287 |  |  | 6.3333 | 26.62 | 63.37
2021-01-13 01:15 |  |  |  |  | 4.775 | -6.7791 |  |  | 8.4457 | 26.59 | 63.3
2021-01-13 01:20 |  |  |  |  | 11.1136 | -4.2737 |  |  | 7.3916 | 26.55 | 63.23
2021-01-13 01:25 |  |  |  |  | -2.5968 | -4.8664 |  |  | 13.2013 | 26.52 | 63.19
2021-01-13 01:30 |  |  |  |  | -8.4855 | 5.3571 |  |  | 5.8095 | 26.47 | 63.37
2021-01-13 01:35 |  |  |  |  | -1.9324 | 4.4782 |  |  | 8.45 | 26.46 | 63.59
2021-01-13 01:40 |  |  |  |  | 8.8129 | 3.4045 |  |  | 7.394 | 26.46 | 63.48
2021-01-13 01:45 |  |  |  |  | 8.7503 | -10.2121 |  |  | 9.5105 | 26.38 | 63.37
2021-01-13 01:50 |  |  |  |  | -7.9532 | 0.87915 |  |  | 5.8122 | 26.36 | 63.54
2021-01-13 01:55 |  |  |  |  | -5.2032 | 8.4539 |  |  | 9.5111 | 26.36 | 63.47
2021-01-13 02:00 |  |  |  |  | 4.0483 | 2.8624 |  |  | 8.4539 | 26.36 | 63.6
2021-01-13 02:05 |  |  |  |  | 10.7233 | -5.2134 |  |  | 7.3985 | 26.32 | 63.61
2021-01-13 02:10 | 0.21723 | 0.024657 | 0.035696 | 0.071391 | 6.8288 | -4.8251 | 1.3868 | -0.058392 | 8.4551 | 26.32 | 63.71
2021-01-13 02:15 | 0.21723 | 0.021917 | 0.031496 | 0.065092 | -7.8612 | 2.341 | 1.3576 | -0.029196 | 7.9262 | 26.34 | 63.62
2021-01-13 02:20 | 0.19167 | 0.021917 | 0.035695 | 0.069291 | -3.5268 | 4.7535 | 1.343 | 0 | 5.813 | 26.32 | 63.67
2021-01-13 02:25 | 0.17891 | 0.021919 | 0.031498 | 0.065097 | 6.7372 | 10.0599 | 1.3285 | 0.014599 | 8.4534 | 26.36 | 63.76
2021-01-13 02:30 | 0.17892 | 0.02329 | 0.0336 | 0.067199 | 17.9531 | -1.8505 | 1.3286 | 0.021899 | 8.4525 | 26.38 | 63.8
2021-01-13 02:35 | 0.17892 | 0.02329 | 0.0336 | 0.069299 | 9.5081 | -3.2103 | 1.3286 | 0.0146 | 8.4523 | 26.39 | 63.75
2021-01-13 02:40 | 0.16613 | 0.023289 | 0.033598 | 0.067196 | -2.0447 | 0.89966 | 1.3285 | 0.021898 | 7.9254 | 26.35 | 63.78
2021-01-13 02:45 | 0.16614 | 0.02055 | 0.0357 | 0.0672 | -0.88948 | 7.4737 | 1.3286 | 0.0219 | 6.34 | 26.35 | 63.92
2021-01-13 02:50 | 0.16614 | 0.020551 | 0.033601 | 0.065102 | 8.1692 | 8.4861 | 1.3286 | 0.0219 | 9.5109 | 26.31 | 64.18
2021-01-13 02:55 | 0.15337 | 0.021921 | 0.031501 | 0.067203 | 11.6967 | -10.3062 | 1.3286 | 0.021901 | 6.8691 | 26.3 | 64.25
2021-01-13 03:00 | [9 empty] | 26.3 | 64.18
2021-01-13 03:05 | 0.23005 | 0.024662 | 0.033602 | 0.071404 | -3.0674 | 3.507 | 1.3287 | 0.0073003 | 8.982 | 26.32 | 64.22
2021-01-13 03:10 | 0.23005 | 0.024662 | 0.033602 | 0.071405 | 0.50101 | 13.2818 | 1.3214 | 0.0073004 | 7.3974 | 26.3 | 64.31
2021-01-13 03:15 | 0.21728 | 0.024662 | 0.033603 | 0.071407 | 6.2474 | 6.82 | 1.3141 | 0.014601 | 9.5116 | 26.27 | 64.51
2021-01-13 03:20 | 0.19171 | 0.026032 | 0.033602 | 0.073505 | 11.6254 | -8.7625 | 1.3141 | 0.021901 | 13.2139 | 26.2 | 64.71
2021-01-13 03:25 | 1.291 | 0.15895 | 0.073515 | 0.31506 | -16.5457 |  | 1.3216 | 0.021904 | 128.9378 | 26.23 | 64.98
2021-01-13 03:30 | 1.8159 | 0.41538 | 0.11767 | 0.75227 |  |  | 1.344 | 0.1607 | 344.7115 | 26.57 | 64.83
2021-01-13 03:35 | 0.38352 | 0.10827 | 0.063021 | 0.22898 |  |  | 1.3363 | 0.043814 | 344.7808 | 26.6 | 63.87
2021-01-13 03:40 | 0.20451 | 0.1014 | 0.056708 | 0.21213 |  | -12.1581 | 1.3434 | 0.029204 | 343.9961 | 26.42 | 64.03
2021-01-13 03:45 | 0.20452 | 0.12744 | 0.05041 | 0.24575 |  | -2.3724 | 1.3361 | 0.036507 | 344.6567 | 26.29 | 64.66
2021-01-13 03:50 | 0.9331 | 0.41244 | 0.075613 | 0.70782 | -1.5134 | 4.121 | 1.358 | 0.094915 | 343.1617 | 26.22 | 64.86
2021-01-13 03:55 | 0.94602 | 0.47007 | 0.10503 | 0.82767 | 17.9693 | 23.3693 | 1.3655 | 0.09493 | 345.0934 | 26.33 | 64.88
2021-01-13 04:00 | 0.43461 | 0.24391 | 0.10712 | 0.4789 | 26.3629 | 0.85899 | 1.3435 | 0.05111 | 344.6281 | 26.31 | 64.63
2021-01-13 04:05 | 0.44736 | 0.27952 | 0.10501 | 0.53347 | 21.1971 | 19.5917 | 1.3507 | 0.073009 | 344.1844 | 26.26 | 64.6
2021-01-13 04:10 | 0.57518 | 0.3357 | 0.11972 | 0.63429 | 21.8518 | 30.0219 | 1.3507 | 0.087612 | 344.6962 | 26.27 | 64.6
2021-01-13 04:15 | 1.2398 | 0.45626 | 0.14071 | 0.84008 | 44.5602 | 19.7034 | 1.3506 | 0.13141 | 344.1176 | 26.33 | 64.22
2021-01-13 04:20 | 1.4188 | 0.533 | 0.14912 | 0.96612 | 41.4123 | 45.1343 | 1.3507 | 0.12411 | 343.3584 | 26.36 | 64.27
2021-01-13 04:25 | 1.2269 | 0.55762 | 0.15961 | 1.0144 | 40.2435 | 21.7066 | 1.3433 | 0.094904 | 344.9123 | 26.41 | 63.86
2021-01-13 04:30 | 1.1758 | 0.52883 | 0.1554 | 0.96601 | 38.0439 | 17.8308 | 1.3505 | 0.1168 | 345.0738 | 26.44 | 63.58
2021-01-13 04:35 | 2.1216 | 0.85903 | 0.21421 | 1.531 | 38.3006 | 23.9558 | 1.3724 | 0.32851 | 344.2834 | 26.5 | 63.5
2021-01-13 04:40 | 2.3131 | 0.98363 | 0.20789 | 1.7156 | 41.8657 | 42.203 | 1.3942 | 0.29199 | 344.2297 | 26.57 | 63.02
2021-01-13 04:45 | 2.6326 | 1.1111 | 0.2415 | 1.9446 | 54.1144 | 17.3804 | 1.4162 | 0.40149 | 377.9499 | 26.62 | 62.88
2021-01-13 04:50 | 1.968 | 1.2795 | 0.28139 | 2.2427 |  |  | 1.4234 | 0.21899 | 510.3914 | 26.67 | 62.55
2021-01-13 04:55 | 1.7636 | 1.0837 | 0.3276 | 1.9887 |  | 37.0206 | 1.4162 | 0.1898 | 509.3004 | 26.68 | 62.62
2021-01-13 05:00 | 1.5336 | 1.1454 | 0.31711 | 2.0728 | 25.1007 | 51.8986 | 1.4162 | 0.2044 | 509.8207 | 26.66 | 62.88
2021-01-13 05:05 | 1.5721 | 1.7483 | 0.35913 | 3.0369 | 77.0542 | 53.5984 | 1.4382 | 0.37963 | 510.3065 | 26.67 | 62.98
2021-01-13 05:10 | 1.7768 | 2.2733 | 0.4684 | 3.9551 | 85.3874 | 85.9396 | 1.4384 | 0.36507 | 509.6327 | 26.72 | 63.13
2021-01-13 05:15 | 2.5817 | 2.7881 | 0.53133 | 4.8051 | 102.8595 | 79.5167 | 1.4309 | 0.30662 | 509.5853 | 26.79 | 62.48
2021-01-13 05:20 | 3.2976 | 2.4306 | 0.49145 | 4.2172 | 133.896 | 117.219 | 1.4309 | 0.33583 | 508.3594 | 26.88 | 62.25
2021-01-13 05:25 | 3.7832 | 2.6772 | 0.60905 | 4.7128 | 133.8638 | 122.8005 | 1.4528 | 0.32122 | 508.7907 | 26.94 | 62
2021-01-13 05:30 | 3.9624 | 2.191 | 0.6007 | 3.9592 | 142.1772 | 98.8103 | 1.4602 | 0.38696 | 509.0924 | 27.05 | 61.81
2021-01-13 05:35 | 4.6909 | 2.6376 | 0.55868 | 4.6017 | 129.1259 | 106.395 | 1.4748 | 0.35044 | 507.9162 | 27.13 | 61.45
2021-01-13 05:40 | 5.2917 | 3.0912 | 0.71201 | 5.4503 | 127.0109 | 98.2773 | 1.4821 | 0.43806 | 507.3154 | 27.17 | 61.34
2021-01-13 05:45 | 5.6871 | 3.5141 | 0.7161 | 6.1026 | 158.85 | 159.9031 | 1.4819 | 0.51829 | 506.1345 | 27.29 | 60.51
2021-01-13 05:50 | 5.4558 | 3.1476 | 0.66975 | 5.4945 | 191.1037 | 168.3095 | 1.4669 | 0.62765 | 506.6762 | 27.35 | 59.68
2021-01-13 05:55 | 5.1232 | 3.0652 | 0.58362 | 5.2799 | 202.659 | 141.2522 | 1.4741 | 0.6349 | 506.0705 | 27.42 | 59.23
2021-01-13 06:00 | 5.0715 | 3.1155 | 0.60245 | 5.3779 | 191.802 | 141.2251 | 1.4667 | 0.56915 | 507.6773 | 27.44 | 58.84
2021-01-13 06:05 | 3.9855 | 2.9332 | 0.60872 | 5.1049 | 168.3218 | 133.1777 | 1.4885 | 0.59102 | 506.6076 | 27.46 | 58.68
2021-01-13 06:10 | 3.7168 | 3.1985 | 0.60654 | 5.5093 | 163.6712 | 137.2067 | 1.5029 | 0.52528 | 508.2028 | 27.49 | 58.23
2021-01-13 06:15 | 4.1387 | 2.9647 | 0.60032 | 5.1426 | 171.7018 | 145.1321 | 1.4593 | 0.49616 | 507.9923 | 27.58 | 58.23
2021-01-13 06:20 | 4.7509 | 2.5246 | 0.53094 | 4.4007 | 163.9112 | 125.1173 | 1.459 | 0.54712 | 507.1128 | 27.54 | 57.81
2021-01-13 06:25 | 4.7753 | 2.3228 | 0.58326 | 4.1458 | 168.7125 | 110.3061 | 1.4513 | 0.56157 | 507.7476 | 27.55 | 57.12
2021-01-13 06:30 | 4.5195 | 2.5087 | 0.61887 | 4.4664 | 145.2882 | 119.9177 | 1.4439 | 0.52506 | 508.2851 | 27.57 | 56.82
2021-01-13 06:35 | 4.0086 | 2.6536 | 0.56849 | 4.636 | 138.0491 | 102.4364 | 1.4292 | 0.43752 | 507.6823 | 27.62 | 56.56
2021-01-13 06:40 | 4.0212 | 2.6029 | 0.61043 | 4.5981 | 131.6825 | 121.1839 | 1.4146 | 0.37918 | 507.5794 | 27.69 | 56.25
2021-01-13 06:45 | 4.1612 | 2.6628 | 0.59777 | 4.6794 | 141.8265 | 123.9156 | 1.4072 | 0.38642 | 507.0481 | 27.73 | 55.79
2021-01-13 06:50 | 3.9191 | 2.5673 | 0.53281 | 4.468 | 130.9869 | 71.5904 | 1.4073 | 0.37188 | 507.415 | 27.79 | 55.9
2021-01-13 06:55 | 6.0515 | 2.8659 | 0.55174 | 4.9447 | 126.0758 | 104.7703 | 1.4074 | 0.4813 | 507.7951 | 27.85 | 55.94
2021-01-13 07:00 | 5.0692 | 2.7978 | 0.5707 | 4.8593 | 129.6785 | 94.1101 | 1.4076 | 0.40843 | 507.6074 | 27.92 | 56.07
2021-01-13 07:05 | 4.5334 | 2.1835 | 0.45745 | 3.8044 | 132.0934 | 121.5198 | 1.4151 | 0.35012 | 507.9942 | 27.97 | 56.19
2021-01-13 07:10 | 6.0794 | 2.5631 | 0.43023 | 4.359 | 149.2173 | 118.0128 | 1.408 | 0.41583 | 505.7124 | 28.03 | 56.38
2021-01-13 07:15 | 6.1044 | 2.7627 | 0.44697 | 4.6796 | 147.3526 | 151.5618 | 1.4297 | 0.51062 | 507.7352 | 28.11 | 55.85
2021-01-13 07:20 | 5.3369 | 2.5252 | 0.50142 | 4.3722 | 178.8194 | 169.8105 | 1.4002 | 0.50321 | 506.1884 | 28.16 | 55.1
2021-01-13 07:25 | 6.4335 | 2.5904 | 0.57473 | 4.5454 | 188.0535 | 133.0416 | 1.3854 | 0.56143 | 506.23 | 28.2 | 54.42
2021-01-13 07:30 | 5.8987 | 2.3063 | 0.51191 | 4.045 | 168.9438 | 105.4929 | 1.3857 | 0.48863 | 507.5602 | 28.28 | 54.74
2021-01-13 07:35 | 5.5525 | 2.2783 | 0.48241 | 3.9746 | 131.7276 | 80.4457 | 1.3707 | 0.45933 | 505.5456 | 28.31 | 53.94
2021-01-13 07:40 | 6.2916 | 2.2122 | 0.46973 | 3.8606 | 123.5549 | 100.3692 | 1.3704 | 0.46653 | 507.1381 | 28.36 | 53.29
2021-01-13 07:45 | 6.4459 | 2.4 | 0.4048 | 4.0837 | 113.2649 | 72.9196 | 1.3707 | 0.45204 | 506.4483 | 28.4 | 53.65
2021-01-13 07:50 | 5.8578 | 2.5255 | 0.46136 | 4.3326 | 109.1215 | 87.1298 | 1.3705 | 0.38636 | 505.9722 | 28.42 | 53.17
2021-01-13 07:55 | 6.3957 | 2.4633 | 0.451 | 4.2268 | 119.4675 | 102.8515 | 1.3854 | 0.4448 | 506.8119 | 28.46 | 53.77
2021-01-13 08:00 | 6.3684 | 2.6254 | 0.44039 | 4.4668 | 136.2397 | 116.0652 | 1.3924 | 0.45197 | 505.3914 | 28.45 | 53.1
2021-01-13 08:05 | 6.1509 | 2.5582 | 0.32922 | 4.2505 | 159.4546 | 116.638 | 1.3922 | 0.75808 | 506.9584 | 28.48 | 52.81
2021-01-13 08:10 | 5.6657 | 2.1777 | 0.37533 | 3.7134 | 146.5417 | 100.2262 | 1.3703 | 0.95483 | 506.9885 | 28.48 | 52.66
2021-01-13 08:15 | 4.4149 | 2.1763 | 0.38789 | 3.7237 | 117.5944 | 67.2595 | 1.3411 | 0.51748 | 508.5775 | 28.49 | 52.49
2021-01-13 08:20 | 3.4829 | 1.7246 | 0.35219 | 2.9957 | 109.5944 | 52.7356 | 1.3336 | 0.39351 | 507.1644 | 28.44 | 52.24
2021-01-13 08:25 | 3.1894 | 1.8025 | 0.38363 | 3.1445 | 93.1824 | 52.7762 | 1.3408 | 0.33521 | 507.1664 | 28.44 | 52.23
2021-01-13 08:30 | 4.6054 | 1.663 | 0.35008 | 2.8992 | 89.8218 | 59.9492 | 1.3627 | 0.32063 | 507.7084 | 28.44 | 52.15
2021-01-13 08:35 | 5.0627 | 2.1381 | 0.44843 | 3.7258 | 91.0222 | 52.8871 | 1.3476 | 0.29137 | 509.5135 | 28.42 | 51.25
2021-01-13 08:40 | 4.0681 | 2.2776 | 0.49664 | 3.9857 | 105.4401 | 73.8948 | 1.3403 | 0.30594 | 507.8385 | 28.47 | 51.16
2021-01-13 08:45 | 3.5446 | 1.6593 | 0.41065 | 2.9541 | 89.3648 | 32.6205 | 1.3328 | 0.3423 | 507.9348 | 28.47 | 50.68
2021-01-13 08:50 | 4.1557 | 2.0143 | 0.47549 | 3.5631 | 86.5819 | 59.455 | 1.3398 | 0.3131 | 506.9404 | 28.5 | 50.05
2021-01-13 08:55 | 3.4669 | 1.887 | 0.44402 | 3.3364 | 76.4047 | 32.3749 | 1.3251 | 0.25482 | 508.5508 | 28.52 | 49.67
2021-01-13 09:00 | 3.7082 | 1.9043 | 0.49835 | 3.4173 | 81.657 | 62.8993 | 1.3175 | 0.32027 | 507.6021 | 28.53 | 49.04
2021-01-13 09:05 | 3.5951 | 1.8313 | 0.45039 | 3.2575 | 86.4859 | 70.7185 | 1.318 | 0.30584 | 507.2977 | 28.58 | 49.99
2021-01-13 09:10 | 4.5137 | 1.8466 | 0.45256 | 3.2853 | 102.0769 | 65.8139 | 1.3401 | 0.31318 | 507.1776 | 28.6 | 50.36
2021-01-13 09:15 | 3.1898 | 2.1966 | 0.47382 | 3.8388 | 102.1542 | 57.2831 | 1.341 | 0.23322 | 506.7266 | 28.67 | 51.8
2021-01-13 09:20 | 3.4937 | 1.8904 | 0.3939 | 3.2895 | 86.8483 | 49.4936 | 1.3328 | 0.24763 | 508.1403 | 28.65 | 50.24
2021-01-13 09:25 | 4.3451 | 1.7006 | 0.41248 | 3.0192 | 122.2936 | 106.5647 | 1.3319 | 0.32024 | 508.4709 | 28.66 | 48.5
2021-01-13 09:30 | 3.5682 | 1.5423 | 0.45231 | 2.8185 | 103.3955 | 54.8072 | 1.3248 | 0.313 | 507.8054 | 28.71 | 48.63
2021-01-13 09:35 | 4.4856 | 1.9084 | 0.5214 | 3.4467 | 89.7227 | 70.1185 | 1.332 | 0.34211 | 506.7283 | 28.73 | 48.53
2021-01-13 09:40 | 4.5127 | 1.9883 | 0.41894 | 3.4668 | 96.7301 | 61.1281 | 1.3398 | 0.37136 | 508.0593 | 28.77 | 49.3
2021-01-13 09:45 | 4.3205 | 1.9674 | 0.4356 | 3.4513 | 96.1467 | 57.1273 | 1.3322 | 0.28391 | 507.6352 | 28.78 | 48.69
2021-01-13 09:50 | 4.0292 | 1.9943 | 0.42951 | 3.4864 | 104.9228 | 51.7065 | 1.3255 | 0.28404 | 505.7735 | 28.81 | 49.75
2021-01-13 09:55 | 4.4239 | 1.994 | 0.4525 | 3.5069 | 92.3531 | 46.253 | 1.3326 | 0.33498 | 507.8965 | 28.84 | 49.32
2021-01-13 10:00 | 4.5462 | 1.847 | 0.42687 | 3.258 | 81.2757 | 50.6216 | 1.3384 | 0.39279 | 508.0011 | 28.81 | 46.57
2021-01-13 10:05 | 3.5684 | 2.0862 | 0.52773 | 3.7255 | 94.8594 | 52.5989 | 1.3322 | 0.32758 | 506.9554 | 28.88 | 48.34
2021-01-13 10:10 | 2.7408 | 1.7492 | 0.44617 | 3.1274 | 107.0403 | 88.6122 | 1.3325 | 0.23301 | 507.7913 | 28.93 | 48.84
2021-01-13 10:15 | 3.0345 | 1.6784 | 0.44625 | 3.019 | 94.4101 | 42.6355 | 1.3255 | 0.24033 | 506.6063 | 28.96 | 49.16
2021-01-13 10:20 | 3.7737 | 1.9448 | 0.39593 | 3.377 | 83.6018 | 61.9084 | 1.3326 | 0.25487 | 505.5451 | 28.99 | 48.88
2021-01-13 10:25 | 3.1616 | 1.9502 | 0.43573 | 3.4251 | 87.6077 | 48.2199 | 1.3253 | 0.23302 | 507.6103 | 29.02 | 48.73
2021-01-13 10:30 | 3.4294 | 1.7616 | 0.39175 | 3.0921 | 88.9361 | 43.234 | 1.3326 | 0.23303 | 504.8848 | 29.07 | 48.66
2021-01-13 10:35 | 3.7732 | 2.0894 | 0.45245 | 3.6573 | 82.899 | 48.1852 | 1.3252 | 0.29125 | 506.9769 | 29.11 | 48.27
2021-01-13 10:40 | 3.6705 | 2.0179 | 0.46491 | 3.5601 | 87.4182 | 52.508 | 1.3322 | 0.28391 | 506.5108 | 29.14 | 47.66
2021-01-13 10:45 | 3.9889 | 1.6148 | 0.41673 | 2.892 | 84.2545 | 60.224 | 1.3321 | 0.2475 | 505.9533 | 29.17 | 47.49
2021-01-13 10:50 | 4.4227 | 1.4865 | 0.45237 | 2.731 | 87.0766 | 18.751 | 1.3396 | 0.32761 | 505.9055 | 29.17 | 47.72
2021-01-13 10:55 | 3.7603 | 1.6616 | 0.47965 | 3.0287 | 75.4199 | 39.8106 | 1.3324 | 0.31308 | 505.3149 | 29.19 | 47.87
2021-01-13 11:00 | 3.6966 | 1.8898 | 0.50898 | 3.4058 | 69.4658 | 60.1248 | 1.3324 | 0.29852 | 504.715 | 29.23 | 47.8
2021-01-13 11:05 | 3.3397 | 1.771 | 0.44405 | 3.1565 | 94.379 | 48.6427 | 1.3252 | 0.29853 | 504.0871 | 29.29 | 47.65
2021-01-13 11:10 | 3.5433 | 1.7749 | 0.44401 | 3.1667 | 71.7326 | 36.8911 | 1.3177 | 0.33489 | 505.6648 | 29.32 | 47.31
2021-01-13 11:15 | 3.849 | 1.7174 | 0.37488 | 3.0074 | 77.5413 | 37.2259 | 1.3177 | 0.24752 | 506.652 | 29.37 | 47.07
2021-01-13 11:20 | 3.6578 | 2.1409 | 0.40838 | 3.6922 | 72.84 | 49.1955 | 1.3104 | 0.28392 | 505.5589 | 29.4 | 46.96
2021-01-13 11:25 | 4.3334 | 2.4839 | 0.59269 | 4.4002 | 90.0335 | 41.2543 | 1.3177 | 0.34217 | 506.4899 | 29.46 | 46.88
2021-01-13 11:30 | 4.4731 | 2.6244 | 0.53399 | 4.5547 | 92.4704 | 67.6145 | 1.3176 | 0.39309 | 506.529 | 29.47 | 46.59
2021-01-13 11:35 | 3.8739 | 1.7649 | 0.40203 | 3.1074 | 80.4234 | 38.8609 | 1.3175 | 0.38578 | 506.0791 | 29.45 | 46.45
2021-01-13 11:40 | 2.676 | 1.7471 | 0.45228 | 3.1324 | 83.4593 | 62.6939 | 1.3174 | 0.24019 | 505.5834 | 29.44 | 46.42
2021-01-13 11:45 | 2.7143 | 1.7131 | 0.46696 | 3.0928 | 115.598 | 84.2186 | 1.3029 | 0.22565 | 506.0279 | 29.47 | 46.48
2021-01-13 11:50 | 2.9052 | 1.8153 | 0.47319 | 3.2558 | 126.3091 | 85.9526 | 1.3101 | 0.27657 | 506.0329 | 29.5 | 46.14
2021-01-13 11:55 | 3.6063 | 2.1597 | 0.44182 | 3.7544 | 114.1983 | 37.6175 | 1.3175 | 0.34211 | 505.9744 | 29.51 | 46.31
2021-01-13 12:00 | 2.778 | 2.045 | 0.48371 | 3.6184 | 92.6488 | 64.0325 | 1.3175 | 0.33483 | 505.9659 | 29.51 | 46.35
2021-01-13 12:05 | 2.7271 | 2.1079 | 0.50884 | 3.742 | 87.7057 | 57.0092 | 1.303 | 0.25477 | 504.8929 | 29.52 | 46.36
2021-01-13 12:10 | 2.0644 | 1.5478 | 0.37692 | 2.7494 | 88.1528 | 37.4754 | 1.2957 | 0.24021 | 505.3756 | 29.55 | 46.24
2021-01-13 12:15 | 3.4663 | 1.8456 | 0.40625 | 3.2395 | 84.0072 | 55.5018 | 1.3103 | 0.28389 | 505.3042 | 29.58 | 46.26
2021-01-13 12:20 | 3.9889 | 1.9359 | 0.39788 | 3.3652 | 92.8078 | 23.2045 | 1.3103 | 0.29118 | 504.7173 | 29.61 | 46.24
2021-01-13 12:25 | 3.5557 | 1.4359 | 0.34554 | 2.5465 | 82.7372 | 22.7464 | 1.3103 | 0.26207 | 504.6863 | 29.62 | 46.28
2021-01-13 12:30 | 3.2247 | 1.7025 | 0.40421 | 3.0159 | 71.8346 | 51.0846 | 1.3177 | 0.28393 | 505.6875 | 29.62 | 46.5
2021-01-13 12:35 | 2.97 | 1.8406 | 0.43776 | 3.2591 | 66.9249 | 40.6158 | 1.3106 | 0.28395 | 505.633 | 29.63 | 46.65
2021-01-13 12:40 | 2.8041 | 1.5645 | 0.4147 | 2.8107 | 62.3025 | 50.7903 | 1.3251 | 0.29122 | 505.6405 | 29.64 | 46.51
2021-01-13 12:45 | 3.6328 | 1.4307 | 0.35817 | 2.5511 | 67.9551 | 39.2802 | 1.3324 | 0.32036 | 504.5328 | 29.66 | 46.58
2021-01-13 12:50 | 3.5315 | 1.8833 | 0.43784 | 3.3267 | 82.9702 | 91.4457 | 1.3181 | 0.29857 | 504.9527 | 29.68 | 46.9
2021-01-13 12:55 | 3.3917 | 1.941 | 0.56571 | 3.5409 | 119.2969 | 89.6742 | 1.311 | 0.27676 | 503.7148 | 29.75 | 47.06
2021-01-13 13:00 | 2.7795 | 1.595 | 0.47977 | 2.9247 | 113.0656 | 56.0687 | 1.3036 | 0.24033 | 504.3108 | 29.73 | 46.93
2021-01-13 13:05 | 3.2258 | 1.3942 | 0.3855 | 2.5225 | 112.0487 | 37.7406 | 1.3036 | 0.19664 | 505.3602 | 29.72 | 47.02
2021-01-13 13:10 | 3.1111 | 1.1495 | 0.36665 | 2.1286 | 91.7611 | 56.703 | 1.2964 | 0.19664 | 506.487 | 29.67 | 47.17
2021-01-13 13:15 | 3.0092 | 1.2316 | 0.38972 | 2.2775 | 88.3696 | 26.1651 | 1.311 | 0.22578 | 504.4144 | 29.64 | 47.39
2021-01-13 13:20 | 2.9075 | 1.2905 | 0.39604 | 2.3741 | 77.6453 | 35.6856 | 1.3111 | 0.24037 | 505.4159 | 29.64 | 47.6
2021-01-13 13:25 | 2.8824 | 1.6106 | 0.394 | 2.8628 | 90.0023 | 43.1186 | 1.3186 | 0.25498 | 504.2807 | 29.65 | 47.91
2021-01-13 13:30 | 3.699 | 1.8678 | 0.3605 | 3.2257 | 80.1032 | 55.6437 | 1.3187 | 0.24043 | 506.7939 | 29.68 | 48.07
2021-01-13 13:35 | 3.955 | 2.2471 | 0.44863 | 3.893 | 91.6331 | 52.9202 | 1.3117 | 0.24777 | 505.5733 | 29.72 | 48.46
2021-01-13 13:40 | 2.7936 | 1.7299 | 0.46324 | 3.1148 | 91.8255 | 28.707 | 1.3116 | 0.21859 | 505.0481 | 29.76 | 48.05
2021-01-13 13:45 | 2.4617 | 1.2866 | 0.3563 | 2.3264 | 86.1307 | 55.5804 | 1.3041 | 0.21857 | 505.6497 | 29.75 | 47.79
2021-01-13 13:50 | 2.8446 | 1.6956 | 0.39825 | 2.9974 | 83.4144 | 55.3511 | 1.3115 | 0.24045 | 505.6508 | 29.72 | 48.1
2021-01-13 13:55 | 2.9725 | 1.5946 | 0.44861 | 2.8929 | 96.7639 | 47.3256 | 1.3408 | 0.2842 | 504.9662 | 29.78 | 48.22
2021-01-13 14:00 | 3.674 | 1.8927 | 0.51777 | 3.419 | 100.4239 | 58.999 | 1.3481 | 0.3352 | 503.3851 | 29.8 | 48.07
2021-01-13 14:05 | 3.0232 | 1.883 | 0.4842 | 3.3706 | 86.0591 | 47.9637 | 1.3261 | 0.22588 | 502.3376 | 29.82 | 47.87
2021-01-13 14:10 | 2.819 | 1.8077 | 0.4674 | 3.2383 | 95.0332 | 52.5014 | 1.3115 | 0.26229 | 504.4791 | 29.81 | 47.74
2021-01-13 14:15 | 3.3676 | 1.7148 | 0.47791 | 3.1064 | 88.9358 | 64.2093 | 1.3625 | 0.35703 | 505.4805 | 29.82 | 47.84
2021-01-13 14:20 | 3.9157 | 1.6504 | 0.44433 | 2.9741 | 107.1614 | 75.2742 | 1.3915 | 0.29142 | 505.5303 | 29.82 | 47.61
2021-01-13 14:25 | 3.5333 | 1.7243 | 0.44435 | 3.0874 | 122.7181 | 88.4109 | 1.3625 | 0.23315 | 504.477 | 29.81 | 47.75
2021-01-13 14:30 | 3.6867 | 2.1785 | 0.46955 | 3.8088 | 124.098 | 49.6392 | 1.3335 | 0.23317 | 503.3476 | 29.83 | 47.93
2021-01-13 14:35 | 3.6868 | 2.3262 | 0.52197 | 4.0856 | 103.2825 | 34.7201 | 1.3262 | 0.29876 | 503.2997 | 29.86 | 47.88
2021-01-13 14:40 | 3.1633 | 1.9129 | 0.44015 | 3.3703 | 103.7561 | 73.0823 | 1.3114 | 0.28415 | 503.3455 | 29.88 | 47.46
2021-01-13 14:45 | 3.7887 | 1.8721 | 0.44019 | 3.3098 | 107.2367 | 80.8867 | 1.3699 | 0.30603 | 503.8316 | 29.87 | 47.73
2021-01-13 14:50 | 3.8018 | 1.9626 | 0.50523 | 3.5135 | 105.176 | 58.5944 | 1.37 | 0.35708 | 503.7292 | 29.9 | 47.89
2021-01-13 14:55 | 3.9172 | 2.2665 | 0.52416 | 3.9983 | 125.1757 | 113.0797 | 1.3337 | 0.33526 | 503.0275 | 29.97 | 47.99
2021-01-13 15:00 | 3.7764 | 1.994 | 0.41928 | 3.4758 | 126.4372 | 62.9328 | 1.3263 | 0.36437 | 503.052 | 29.99 | 47.67
2021-01-13 15:05 | 3.5342 | 1.7234 | 0.41511 | 3.0568 | 130.2427 | 99.2335 | 1.3337 | 0.36439 | 503.5068 | 30.01 | 47.77
2021-01-13 15:10 | 3.1643 | 1.8492 | 0.47383 | 3.3105 | 128.2032 | 79.831 | 1.341 | 0.31338 | 502.9443 | 30.03 | 47.75
2021-01-13 15:15 | 3.5846 | 2.0704 | 0.46744 | 3.6389 | 112.2468 | 72.3445 | 1.3334 | 0.30603 | 503.5687 | 30.03 | 47.28
2021-01-13 15:20 | 5.4471 | 1.8667 | 0.4947 | 3.356 | 110.2485 | 47.9142 | 1.3262 | 0.36433 | 502.5824 | 29.99 | 47.43
2021-01-13 15:25 | 7.3492 | 1.9983 | 0.52833 | 3.5914 | 107.9311 | 75.1864 | 1.3264 | 0.45914 | 503.601 | 29.95 | 47.96
2021-01-13 15:30 | 4.7846 | 1.7822 | 0.4256 | 3.1595 | 96.9478 | 45.6567 | 1.3118 | 0.41541 | 504.663 | 29.94 | 47.98
2021-01-13 15:35 | [9 empty] | 29.94 | 48.04
2021-01-13 15:40 | 4.211 | 1.6005 | 0.3984 | 2.8538 | 98.4713 | 59.0052 | 1.312 | 0.25511 | 504.0758 | 29.94 | 48.28
2021-01-13 15:45 | 4.3904 | 1.8032 | 0.40056 | 3.1646 | 99.6815 | 54.1137 | 1.3122 | 0.29889 | 504.5008 | 29.95 | 48.62
2021-01-13 15:50 | 3.5995 | 1.6871 | 0.36705 | 2.9532 | 96.9572 | 63.0247 | 1.3197 | 0.29164 | 502.8404 | 29.97 | 48.85
2021-01-13 15:55 | 3.8683 | 1.6847 | 0.39649 | 2.9789 | 101.9497 | 73.7915 | 1.3199 | 0.30628 | 503.199 | 30.01 | 49.18
2021-01-13 16:00 | 4.4691 | 1.8466 | 0.38817 | 3.2186 | 124.5227 | 89.4643 | 1.3201 | 0.31363 | 502.5395 | 30.04 | 49.5
2021-01-13 16:05 | 3.9839 | 1.8082 | 0.37138 | 3.1431 | 126.9952 | 72.3542 | 1.3129 | 0.29904 | 503.0424 | 30.05 | 49.48
2021-01-13 16:10 | 4.6733 | 1.5864 | 0.32521 | 2.7548 | 119.9827 | 73.9651 | 1.3128 | 0.29903 | 502.6078 | 30.01 | 49.5
2021-01-13 16:15 | 4.4571 | 1.4978 | 0.37144 | 2.6673 | 99.8601 | 42.2163 | 1.3131 | 0.31368 | 503.6119 | 29.98 | 50.02
2021-01-13 16:20 | 4.394 | 1.7664 | 0.43867 | 3.1463 | 84.5284 | 82.4745 | 1.3279 | 0.32832 | 503.9489 | 30.03 | 50.31
2021-01-13 16:25 | 4.3684 | 1.7568 | 0.3715 | 3.0644 | 89.9847 | 69.333 | 1.3279 | 0.30643 | 501.8502 | 30.04 | 50.27
2021-01-13 16:30 | 4.3947 | 1.8858 | 0.44714 | 3.3399 | 102.5289 | 92.5949 | 1.3427 | 0.37216 | 502.8956 | 29.99 | 50.78
2021-01-13 16:35 | 5.0337 | 2.1845 | 0.39888 | 3.7473 | 116.9772 | 81.511 | 1.3793 | 0.40137 | 501.3046 | 30 | 50.84
2021-01-13 16:40 | 4.7779 | 2.0912 | 0.54999 | 3.7555 | 103.5194 | 67.933 | 1.3646 | 0.40134 | 503.4218 | 30 | 50.68
2021-01-13 16:45 | 4.1394 | 1.6531 | 0.41147 | 2.9432 | 86.2417 | 64.6149 | 1.3282 | 0.35758 | 502.8914 | 29.99 | 50.83
2021-01-13 16:50 | 3.4623 | 1.4997 | 0.39678 | 2.6956 | 73.8566 | 35.3338 | 1.3136 | 0.27731 | 501.8513 | 29.98 | 50.93
2021-01-13 16:55 | 3.8332 | 1.6451 | 0.39262 | 2.9142 | 70.0407 | 66.1972 | 1.3283 | 0.35033 | 504.4556 | 29.95 | 51.24
2021-01-13 17:00 | 3.7312 | 1.5369 | 0.34645 | 2.7023 | 80.3277 | 85.9194 | 1.3065 | 0.32845 | 503.3411 | 29.98 | 51.26
2021-01-13 17:05 | 3.9356 | 1.4314 | 0.30235 | 2.4965 | 78.7941 | 43.302 | 1.3065 | 0.48902 | 501.8474 | 29.94 | 51.37
2021-01-13 17:10 | 4.4341 | 1.3767 | 0.28556 | 2.3958 | 76.5373 | 63.4114 | 1.3065 | 0.59852 | 502.3857 | 29.92 | 51.5
2021-01-13 17:15 | 4.7275 | 1.2218 | 0.27084 | 2.1436 | 65.7663 | 44.311 | 1.3137 | 0.48169 | 503.5596 | 29.87 | 51.42
2021-01-13 17:20 | 4.1395 | 0.97106 | 0.27502 | 1.7635 | 60.9171 | 42.7646 | 1.3063 | 0.3211 | 502.1308 | 29.81 | 51.44
2021-01-13 17:25 | 3.2452 | 1.0724 | 0.28132 | 1.9252 | 50.9726 | 10.1495 | 1.3063 | 0.24813 | 504.8636 | 29.73 | 51.7
2021-01-13 17:30 | 2.2866 | 0.92985 | 0.2393 | 1.6646 | 43.5971 | 58.4463 | 1.2988 | 0.18972 | 505.5888 | 29.65 | 51.61
2021-01-13 17:35 | 2.6188 | 0.86138 | 0.2372 | 1.5575 | 36.3616 | 41.7882 | 1.2988 | 0.19701 | 505.2173 | 29.56 | 51.88
2021-01-13 17:40 | 2.8233 | 0.96411 | 0.21202 | 1.6919 | 56.6389 | 29.0144 | 1.3062 | 0.18972 | 505.338 | 29.48 | 52.18
2021-01-13 17:45 | 2.4527 | 1.023 | 0.20362 | 1.7696 | 52.7135 | 53.5924 | 1.2988 | 0.17513 | 503.3438 | 29.43 | 52.29
2021-01-13 17:50 | 2.21 | 0.89285 | 0.21411 | 1.5827 | 52.763 | 30.0554 | 1.2988 | 0.16782 | 504.9569 | 29.41 | 52.28
2021-01-13 17:55 | 2.1462 | 0.84222 | 0.21621 | 1.5072 | 45.9279 | 30.3223 | 1.2989 | 0.19702 | 504.4831 | 29.37 | 52.49
2021-01-13 18:00 | 2.2738 | 0.69156 | 0.17422 | 1.2343 | 45.109 | 41.2051 | 1.2988 | 0.2189 | 504.5983 | 29.31 | 52.6
2021-01-13 18:05 | 2.0183 | 0.75728 | 0.20361 | 1.3644 | 35.8499 | 33.0293 | 1.2915 | 0.18971 | 505.7461 | 29.24 | 52.85
2021-01-13 18:10 | 1.5967 | 0.70382 | 0.21829 | 1.2971 | 27.3554 | 24.2081 | 1.2841 | 0.1897 | 504.317 | 29.18 | 52.85
2021-01-13 18:15 | 1.8394 | 0.6874 | 0.21829 | 1.272 | 20.1719 | 20.1923 | 1.2914 | 0.13863 | 506.5363 | 29.1 | 53.12
2021-01-13 18:20 | 1.6096 | 0.72856 | 0.23511 | 1.3519 | 20.348 | 24.344 | 1.2916 | 0.12405 | 506.5605 | 29.05 | 53.56
2021-01-13 18:25 | 1.6608 | 0.5971 | 0.21412 | 1.1294 | 32.4895 | 26.8787 | 1.2916 | 0.13135 | 504.4842 | 29.04 | 53.6
2021-01-13 18:30 | 1.5455 | 0.62165 | 0.21828 | 1.1712 | 27.4366 | 17.402 | 1.2987 | 0.16781 | 506.248 | 28.97 | 53.44
2021-01-13 18:35 | 2.2098 | 0.94621 | 0.23928 | 1.6897 | 62.3353 | 142.38 | 1.2987 | 0.16781 | 448.7448 | 28.94 | 53.64
2021-01-13 18:40 | 2.5419 | 1.1448 | 0.21409 | 1.9688 | 220.011 | 333.8996 | 1.2987 | 0.197 | 342.0759 | 28.92 | 53.68
2021-01-13 18:45 | 2.6443 | 1.1544 | 0.2246 | 1.9941 | 156.2653 | 76.0734 | 1.2988 | 0.23349 | 341.0204 | 28.91 | 53.86
2021-01-13 18:50 | 2.6314 | 1.0421 | 0.23929 | 1.8366 | 93.8218 | 76.3676 | 1.2988 | 0.2116 | 342.0992 | 28.89 | 53.85
2021-01-13 18:55 | 2.0565 | 0.71068 | 0.21829 | 1.3077 | 64.6753 | 37.4726 | 1.2914 | 0.16781 | 341.0728 | 28.88 | 53.82
2021-01-13 19:00 | 1.5455 | 0.52715 | 0.19099 | 0.99693 | 32.136 | 28.1509 | 1.2913 | 0.13132 | 341.7113 | 28.8 | 53.89
2021-01-13 19:05 | 1.4818 | 0.58608 | 0.17841 | 1.0747 | 15.1242 | 28.317 | 1.2915 | 0.11674 | 342.7606 | 28.77 | 54.21
2021-01-13 19:10 | 1.3924 | 0.72713 | 0.18261 | 1.2972 | 9.9637 | 27.0705 | 1.2915 | 0.10215 | 342.7925 | 28.74 | 54.32
2021-01-13 19:15 | 1.4819 | 0.91889 | 0.15324 | 1.5617 | 16.4435 | 47.2864 | 1.2915 | 0.13134 | 341.1931 | 28.75 | 54.42
2021-01-13 19:20 | 1.3158 | 0.79288 | 0.15323 | 1.3665 | 14.1744 | 19.6213 | 1.2988 | 0.10945 | 341.2575 | 28.7 | 54.52
2021-01-13 19:25 | 1.6096 | 0.77238 | 0.15534 | 1.3393 | 7.0824 | 46.1632 | 1.3135 | 0.13135 | 340.7868 | 28.64 | 54.82
2021-01-13 19:30 | 1.7887 | 0.76151 | 0.17845 | 1.3457 | 24.2749 | 47.9468 | 1.3063 | 0.15325 | 341.8186 | 28.62 | 55.16
2021-01-13 19:35 | 1.5204 | 0.71083 | 0.18895 | 1.2785 | 21.1269 | 36.1621 | 1.3063 | 0.13136 | 341.3054 | 28.61 | 55.2
2021-01-13 19:40 | 1.2776 | 0.55056 | 0.14485 | 0.98876 | 20.0321 | 27.8406 | 1.2989 | 0.10216 | 341.9498 | 28.52 | 55.35
2021-01-13 19:45 | 1.7889 | 0.71912 | 0.17847 | 1.2808 | 5.2439 | 20.0965 | 1.3064 | 0.10218 | 341.4532 | 28.45 | 55.96
2021-01-13 19:50 | 1.3801 | 0.61231 | 0.14908 | 1.0877 | -1.7992 | 1.3801 | 1.2992 | 0.094886 | 343.5629 | 28.42 | 56.2
2021-01-13 19:55 | 1.4568 | 0.54247 | 0.17848 | 1.01 | -5.5408 | 19.0658 | 1.2993 | 0.094889 | 342.584 | 28.35 | 56.51
2021-01-13 20:00 | 1.2012 | 0.41919 | 0.14909 | 0.79164 | -2.3513 | 25.0265 | 1.3066 | 0.080293 | 342.1185 | 28.29 | 56.78
2021-01-13 20:05 | 1.0096 | 0.38906 | 0.13229 | 0.72655 | -6.5122 | 0.34759 | 1.2993 | 0.080294 | 342.2413 | 28.18 | 57.16
2021-01-13 20:10 | 1.3676 | 0.5412 | 0.17221 | 0.99969 | -6.1451 | 11.7381 | 1.2995 | 0.12411 | 341.6888 | 28.16 | 57.61
2021-01-13 20:15 | 1.0992 | 0.4453 | 0.13441 | 0.81698 | -6.6156 | 24.0083 | 1.2995 | 0.087608 | 342.1733 | 28.19 | 57.55
2021-01-13 20:20 | 1.176 | 0.5125 | 0.15543 | 0.941 | 5.0006 | 18.6628 | 1.307 | 0.080316 | 342.6348 | 28.21 | 57.78
2021-01-13 20:25 | 1.2911 | 0.5961 | 0.17224 | 1.0881 | 4.2951 | 22.9277 | 1.2997 | 0.065715 | 342.0568 | 28.25 | 57.71
2021-01-13 20:30 | 1.1888 | 0.80161 | 0.15123 | 1.38 | 10.8599 | 14.8992 | 1.2996 | 0.05841 | 342.0743 | 28.25 | 57.58
2021-01-13 20:35 | 1.4315 | 0.67411 | 0.11551 | 1.1467 | 8.5787 | 11.0327 | 1.2995 | 0.073006 | 342.176 | 28.19 | 57.53
2021-01-13 20:40 | 1.5337 | 0.6823 | 0.13231 | 1.1761 | 2.5357 | 17.31 | 1.2994 | 0.1168 | 342.305 | 28.09 | 57.75
2021-01-13 20:45 | 2.1474 | 0.91534 | 0.13653 | 1.5396 | -4.7039 | 22.006 | 1.3069 | 0.16063 | 341.7567 | 28.07 | 58.17
2021-01-13 20:50 | 1.9302 | 0.99074 | 0.15123 | 1.6678 | 4.3564 | 11.5659 | 1.3143 | 0.17524 | 342.7679 | 28.09 | 58.21
2021-01-13 20:55 | 1.8407 | 0.7701 | 0.17854 | 1.359 | -1.4112 | 3.4462 | 1.307 | 0.17523 | 342.2623 | 28.08 | 58.19
2021-01-13 21:00 | 1.4316 | 0.74816 | 0.17223 | 1.319 | 5.1845 | 21.3924 | 1.3069 | 0.17523 | 342.3615 | 28 | 58.4
2021-01-13 21:05 | 0.93309 | 0.55494 | 0.15543 | 1.0061 | 8.385 | 4.8367 | 1.3069 | 0.13872 | 343.5083 | 27.92 | 58.62
2021-01-13 21:10 | 0.95858 | 0.41515 | 0.11551 | 0.75187 | -9.7955 | 1.9836 | 1.3068 | 0.10951 | 342.6424 | 27.78 | 58.92
2021-01-13 21:15 | 0.74133 | 0.32747 | 0.10291 | 0.60488 | 16.5956 | 139.1759 | 1.3068 | 0.080309 | 249.8331 | 27.69 | 59.32
2021-01-13 21:20 | 0.51117 | 0.20138 | 0.081896 | 0.39268 | 339.2563 | 481.6388 | 1.2993 | 0.058397 | 2.6258 | 27.57 | 59.28
2021-01-13 21:25 | 0.53666 | 0.18355 | 0.073487 | 0.35484 | 229.916 | 60.8625 | 1.3064 | 0.05109 | 5.7798 | 27.45 | 59.34
2021-01-13 21:30 | 0.37052 | 0.16025 | 0.067181 | 0.31281 | 95.5266 | 16.7115 | 1.299 | 0.043787 | 10.5123 | 27.38 | 59.32
2021-01-13 21:35 | 0.39602 | 0.13695 | 0.07347 | 0.28338 | 28.8403 | 9.5862 | 1.3062 | 0.036485 | 7.8878 | 27.28 | 59.32
2021-01-13 21:40 | 0.42158 | 0.13695 | 0.067175 | 0.2771 | 4.3435 | 5.1918 | 1.3062 | 0.029189 | 7.3625 | 27.25 | 59.5
2021-01-13 21:45 | 0.31936 | 0.098597 | 0.062972 | 0.21201 | 0.90953 | -14.5729 | 1.2988 | 0.029187 | 8.416 | 27.21 | 59.46
2021-01-13 21:50 | 0.37045 | 0.10544 | 0.062972 | 0.2246 | 0.39856 | -2.9125 | 1.2988 | 0.029187 | 6.3132 | 27.15 | 59.68
2021-01-13 21:55 | 0.26828 | 0.089018 | 0.058778 | 0.19523 | -10.4757 | 7.8491 | 1.2989 | 0.021892 | 7.3649 | 27.15 | 59.88
2021-01-13 22:00 | 0.30663 | 0.076699 | 0.058783 | 0.17845 | -13.6655 | 7.5431 | 1.3063 | 0.029191 | 8.942 | 27.16 | 60.07
2021-01-13 22:05 | 0.33218 | 0.07396 | 0.054585 | 0.17005 | -6.6948 | -17.1101 | 1.299 | 0.029191 | 7.3643 | 27.15 | 60.11
2021-01-13 22:10 | 0.24278 | 0.076707 | 0.062989 | 0.18057 | -1.0222 | -13.2786 | 1.2992 | 0.021896 | 8.4145 | 27.18 | 60.3
2021-01-13 22:15 | 0.26834 | 0.067121 | 0.056692 | 0.15958 | -5.0397 | 1.7889 | 1.3065 | 0.021897 | 7.3618 | 27.21 | 60.27
2021-01-13 22:20 | 0.28112 | 0.063012 | 0.054593 | 0.15328 | -18.1656 | 7.1456 | 1.2992 | 0.021897 | 10.5163 | 27.22 | 60.27
2021-01-13 22:25 | 0.25556 | 0.057531 | 0.052492 | 0.14068 | -9.9668 | 2.1058 | 1.2992 | 0.021896 | 10.5173 | 27.2 | 60.27
2021-01-13 22:30 | 0.25554 | 0.04931 | 0.04829 | 0.12387 | 1.1448 | -6.2762 | 1.2991 | 0.021895 | 9.4673 | 27.16 | 60.27
2021-01-13 22:35 | 0.24276 | 0.050678 | 0.058786 | 0.13647 | 7.891 | -0.38842 | 1.2991 | 0.014596 | 7.3651 | 27.1 | 60.42
2021-01-13 22:40 | 0.23 | 0.052052 | 0.048293 | 0.12808 | -11.398 | 0.66446 | 1.2992 | 0.0072988 | 6.8383 | 27.11 | 60.61
2021-01-13 22:45 | 0.23001 | 0.043834 | 0.048293 | 0.11548 | -12.5431 | 13.504 | 1.2919 | 0.021897 | 6.3115 | 27.14 | 60.54
2021-01-13 22:50 | 0.21723 | 0.042464 | 0.052492 | 0.11758 | -9.3535 |  | 1.2919 | 0.021896 | 7.8901 | 27.12 | 60.56
2021-01-13 22:55 | 0.19167 | 0.036984 | 0.054591 | 0.10918 | -0.53156 | -9.6703 | 1.2919 | 0.014597 | 4.7339 | 27.13 | 60.51
2021-01-13 23:00 | 0.19166 | 0.038352 | 0.050389 | 0.10918 | -3.0154 | -1.4413 | 1.2918 | 0.021895 | 8.4176 | 27.08 | 60.56
2021-01-13 23:05 | 0.19166 | 0.043831 | 0.04829 | 0.11548 | -16.4265 | -3.1074 | 1.2918 | 0.014597 | 9.4698 | 27.08 | 60.57
2021-01-13 23:10 | 0.17887 | 0.041089 | 0.046188 | 0.10917 | -14.0236 | -5.9794 | 1.2917 | 0.021894 | 8.4192 | 27.04 | 60.55
2021-01-13 23:15 | 0.20443 | 0.03698 | 0.046188 | 0.10287 | -1.5025 | -7.1549 | 1.2917 | 0.014596 | 8.9454 | 27.04 | 60.55
2021-01-13 23:20 | 0.20443 | 0.032872 | 0.048289 | 0.098677 | 4.0068 | -10.3033 | 1.2991 | 0.021895 | 8.4111 | 27.02 | 60.64
2021-01-13 23:25 | 0.30665 | 0.036982 | 0.04409 | 0.10078 | -10.14 | -3.782 | 1.2918 | 0.021895 | 9.463 | 27 | 60.76
2021-01-13 23:30 | 0.3322 | 0.035612 | 0.046189 | 0.10078 | -16.2728 | -0.40886 | 1.2845 | 0.021895 | 8.4117 | 27 | 60.72
2021-01-13 23:35 | 0.22999 | 0.036982 | 0.04619 | 0.10288 | -8.9133 | -11.2541 | 1.2845 | -0.029193 | 6.8349 | 26.98 | 60.82
2021-01-13 23:40 | 0.24277 | 0.038352 | 0.044091 | 0.10288 | -0.27599 | -12.716 | 1.2553 | -0.029194 | 8.412 | 26.98 | 60.87
2021-01-13 23:45 | 0.30667 | 0.039724 | 0.044093 | 0.10498 | 2.944 | -3.5165 | 1.2408 | 0 | 10.5138 | 27 | 60.91
2021-01-13 23:50 |  | 0.036982 | 0.039891 | 0.094479 | -7.2983 | 10.4875 | 1.2334 | 0.014597 | 9.9904 | 26.95 | 60.94
2021-01-13 23:55 | 0.17888 | 0.032874 | 0.039892 | 0.088183 | -6.3172 | 3.2199 | 1.2334 | 0.021895 | 7.3614 | 26.94 | 61.03
2021-01-14 | 0.12777 | 0.027394 | 0.035691 | 0.077681 | -2.6474 | -14.1874 | 1.2334 | 0.014596 | 12.6231 | 26.87 | 61.16
2021-01-14 00:05 | 0.10222 | 0.030133 | 0.04199 | 0.088179 | 4.4975 | -9.7105 | 1.2334 | 0.014596 | 7.891 | 26.81 | 61.39
2021-01-14 00:10 | 0.10223 | 0.027398 | 0.044096 | 0.086092 | 2.2286 | 4.5595 | 1.2336 | 0.021898 | 8.4155 | 26.82 | 61.76
2021-01-14 00:15 | 0.089457 | 0.028769 | 0.044099 | 0.088197 | -9.876 | 2.8115 | 1.2336 | 0.021899 | 9.4663 | 26.84 | 61.85
2021-01-14 00:20 | 0.051114 | 0.028767 | 0.039896 | 0.081892 | -10.4478 | -1.4108 | 1.2336 | 0.014598 | 6.313 | 26.76 | 61.94
2021-01-14 00:25 | 0.07668 | 0.03288 | 0.0399 | 0.0882 | -5.9401 |  | 1.2337 | 0.0146 | 7.8907 | 26.75 | 62.27
2021-01-14 00:30 | 0.10225 | 0.031514 | 0.037805 | 0.086111 | 0.83848 | -6.1352 | 1.2338 | 0.021903 | 11.0344 | 26.75 | 62.57
2021-01-14 00:35 | 0.11504 | 0.027404 | 0.033605 | 0.075612 | -7.5976 | -2.9654 | 1.2412 | 0.07301 | 16.2896 | 26.73 | 62.71
2021-01-14 00:40 | 0.11503 | 0.024663 | 0.035704 | 0.073509 | -14.0085 | 8.1392 | 1.263 | 0.13871 | 9.986 | 26.68 | 62.79
2021-01-14 00:45 | 0.10225 | 0.024662 | 0.035702 | 0.073504 | -2.9038 | -1.7382 | 1.2922 | 0.065703 | 12.6185 | 26.59 | 62.95
2021-01-14 00:50 | 0.089468 | 0.027403 | 0.035704 | 0.075607 | 1.4315 | -14.315 | 1.2995 | 0.043804 | 9.4644 | 26.56 | 63.18
2021-01-14 00:55 | 0.11504 | 0.030146 | 0.037807 | 0.084017 | 8.3137 | 1.0124 | 1.2996 | 0.029205 | 5.2571 | 26.58 | 63.38
2021-01-14 01:00 | 0.076698 | 0.028777 | 0.037809 | 0.081919 | -2.6895 | 12.5989 | 1.2997 | 0.029207 | 8.4094 | 26.64 | 63.27
2021-01-14 01:05 |  |  |  |  | -8.7023 | -0.86921 |  |  | 8.41 | 26.63 | 63.21
2021-01-14 01:10 |  |  |  |  | -3.8959 | -4.9491 |  |  | 5.7832 | 26.58 | 63.21
2021-01-14 01:15 |  |  |  |  | 1.9531 | -16.6781 |  |  | 7.8864 | 26.56 | 63.38
2021-01-14 01:20 |  |  |  |  | 4.0292 | -1.8305 |  |  | 8.9368 | 26.58 | 63.48
2021-01-14 01:25 |  |  |  |  | -6.0022 | 1.2577 |  |  | 8.4137 | 26.52 | 63.4
2021-01-14 01:30 |  |  |  |  | -14.4179 | -6.0535 |  |  | 7.8887 | 26.48 | 63.61
2021-01-14 01:35 |  |  |  |  | -12.8232 | -19.2246 |  |  | 7.8887 | 26.47 | 63.76
2021-01-14 01:40 |  |  |  |  | -5.9108 | -17.5279 |  |  | 13.6722 | 26.49 | 63.81
2021-01-14 01:45 |  |  |  |  | -0.020453 | -0.71585 |  |  | 11.5687 | 26.49 | 63.83
2021-01-14 01:50 |  |  |  |  | -10.3681 | 4.3967 |  |  | 13.6795 | 26.37 | 63.89
2021-01-14 01:55 |  |  |  |  | -14.0287 | 0.10225 |  |  | 8.4204 | 26.29 | 64.2
2021-01-14 02:00 |  |  |  |  | -7.2501 | -20.3597 |  |  | 11.5638 | 26.33 | 64.23
2021-01-14 02:05 |  |  |  |  | 0.55218 | -5.5013 |  |  | 9.462 | 26.32 | 64.17
2021-01-14 02:10 | 0.16617 | 0.036996 | 0.035706 | 0.092416 | 0.97144 | -5.8082 | 1.358 | -0.014602 | 6.3081 | 26.31 | 64.25
2021-01-14 02:15 | 0.26845 | 0.038371 | 0.03571 | 0.092425 | -9.8381 | 4.5816 | 1.3362 | 0.0073019 | 4.2037 | 26.4 | 64.19
2021-01-14 02:20 | 0.294 | 0.039739 | 0.031507 | 0.092419 | -7.598 | -0.29656 | 1.3362 | 0.021904 | 10.5092 | 26.42 | 63.95
2021-01-14 02:25 | 0.29397 | 0.041105 | 0.035704 | 0.098712 | -2.5461 | -17.0658 | 1.336 | 0.029203 | 12.6143 | 26.37 | 63.88
2021-01-14 02:30 | 0.16616 | 0.045217 | 0.033605 | 0.10292 | 0.49082 | -8.6303 | 1.3288 | 0.029204 | 5.256 | 26.36 | 64
2021-01-14 02:35 | 0.33231 | 0.042474 | 0.035703 | 0.098709 | 5.4192 | 7.0654 | 1.3287 | 0.036503 | 10.514 | 26.32 | 63.98
2021-01-14 02:40 | 0.2556 | 0.045211 | 0.0336 | 0.1029 | -1.9528 | 5.5517 | 1.3286 | 0.0438 | 10.5169 | 26.26 | 64
2021-01-14 02:45 | 0.20447 | 0.045209 | 0.035699 | 0.105 | -3.3227 | 9.9578 | 1.3285 | 0.051098 | 15.7792 | 26.2 | 64.09
2021-01-14 02:50 | 0.25558 | 0.042468 | 0.033598 | 0.10079 | 1.2677 | -12.1863 | 1.3358 | 0.043797 | 16.3077 | 26.16 | 64.18
2021-01-14 02:55 | 0.19166 | 0.034243 | 0.035693 | 0.088182 | 3.363 | -7.9833 | 1.3429 | 0.036492 | 21.053 | 26.05 | 64.18
2021-01-14 03:00 | [9 empty] | 25.91 | 64.57
2021-01-14 03:05 | 0.25555 | 0.046572 | 0.031494 | 0.10078 | -10.631 | -0.30666 | 1.3429 | 0.043791 | 10.5312 | 25.91 | 64.77
2021-01-14 03:10 | 0.19169 | 0.053428 | 0.031499 | 0.1134 | -13.5666 | -3.1897 | 1.3431 | 0.051097 | 7.3694 | 25.97 | 64.94
2021-01-14 03:15 | 0.31948 | 0.050688 | 0.037798 | 0.11339 | -5.6638 | -14.7934 | 1.3431 | 0.043797 | 12.632 | 26 | 64.82
2021-01-14 03:20 | 0.25561 | 0.058912 | 0.039901 | 0.1302 | 4.9997 | 1.2065 | 1.3578 | 0.051101 | 8.4195 | 26.04 | 64.89
2021-01-14 03:25 | 0.20447 | 0.049319 | 0.035699 | 0.1113 | 12.2071 | 9.3342 | 1.3577 | 0.043798 | 6.8404 | 26.08 | 64.57
2021-01-14 03:30 | 0.43436 | 0.039716 | 0.035687 | 0.096566 | -0.13286 | 3.1581 | 1.3646 | 0.043784 | 7.8998 | 25.91 | 64.26
2021-01-14 03:35 | 1.1884 | 0.36576 | 0.067195 | 0.62785 |  |  | 1.3577 | 0.14599 | 229.4961 | 25.99 | 64.76
2021-01-14 03:40 | 1.1247 | 0.55627 | 0.10921 | 0.95978 |  |  | 1.3798 | 0.14601 | 316.6912 | 26.61 | 62.89
2021-01-14 03:45 | 0.72827 | 0.16025 | 0.079779 | 0.32541 |  | -8.2588 | 1.4012 | 0.10217 | 316.6106 | 26.79 | 61.27
2021-01-14 03:50 | 0.48556 | 0.11643 | 0.060891 | 0.23936 |  | 12.4816 | 1.3941 | 0.043793 | 317.1114 | 26.78 | 61.61
2021-01-14 03:55 | 0.56216 | 0.36843 | 0.090275 | 0.65712 | -3.9658 | 4.0884 | 1.3793 | 0.051085 | 317.7397 | 26.72 | 61.48
2021-01-14 04:00 | 1.6099 | 0.49994 | 0.12807 | 0.8944 | 6.3681 | -8.6884 | 1.3794 | 0.094877 | 317.6504 | 26.79 | 61.36
2021-01-14 04:05 | 1.917 | 0.51512 | 0.1176 | 0.90929 | 11.4814 | 33.5548 | 1.3943 | 0.1095 | 317.5058 | 26.86 | 61.72
2021-01-14 04:10 | 1.8782 | 0.6013 | 0.13647 | 1.0582 | 22.8455 | 23.745 | 1.4013 | 0.12407 | 318.0356 | 26.92 | 60.91
2021-01-14 04:15 | 1.2138 | 0.64236 | 0.13646 | 1.119 | 34.4249 | 5.315 | 1.3939 | 0.087575 | 316.456 | 26.94 | 60.7
2021-01-14 04:20 | 1.3546 | 0.6603 | 0.15119 | 1.1633 | 22.3889 | 28.9318 | 1.3796 | 0.12409 | 315.888 | 26.92 | 61.33
2021-01-14 04:25 | 1.2905 | 0.89857 | 0.15327 | 1.5306 | 29.6034 | 38.9055 | 1.3867 | 0.11678 | 316.3936 | 26.97 | 60.86
2021-01-14 04:30 | 0.94558 | 0.91914 | 0.15328 | 1.5622 |  |  | 1.3795 | 0.12408 | 441.7087 | 27.02 | 60.77
2021-01-14 04:35 | 0.67718 | 0.7999 | 0.20155 | 1.4277 |  |  | 1.3721 | 0.10217 | 453.8624 | 26.99 | 60.62
2021-01-14 04:40 | 0.61328 | 0.75331 | 0.20365 | 1.3583 |  | 6.5212 | 1.3793 | 0.13136 | 455.0973 | 26.92 | 60.74
2021-01-14 04:45 | 1.3671 | 0.86973 | 0.23514 | 1.5704 | -14.5857 | 38.851 | 1.3939 | 0.14596 | 453.4711 | 26.91 | 60.83
2021-01-14 04:50 | 1.5586 | 1.2271 | 0.30859 | 2.1895 | 46.6863 | 50.0692 | 1.4084 | 0.17513 | 455.0276 | 26.95 | 60.43
2021-01-14 04:55 | 1.4055 | 1.5491 | 0.32333 | 2.6958 | 58.7332 | 66.287 | 1.4013 | 0.29923 | 453.3894 | 27 | 60.54
2021-01-14 05:00 | 2.1847 | 1.8421 | 0.35479 | 3.1784 | 53.6387 | 29.6505 | 1.4011 | 0.37948 | 452.8555 | 27.03 | 60.22
2021-01-14 05:05 | 3.0021 | 1.8447 | 0.37366 | 3.2034 | 63.6505 | 76.8447 | 1.4083 | 0.32837 | 452.7821 | 27.1 | 59.78
2021-01-14 05:10 | 2.8744 | 1.9118 | 0.43663 | 3.3671 | 71.8266 | 68.2189 | 1.4083 | 0.2554 | 452.1977 | 27.14 | 59.64
2021-01-14 05:15 | 3.2966 | 2.2121 | 0.506 | 3.8947 | 98.3148 | 84.9444 | 1.4159 | 0.35033 | 453.0109 | 27.24 | 59.79
2021-01-14 05:20 | 3.4757 | 2.6205 | 0.49764 | 4.5166 | 112.2256 | 103.618 | 1.416 | 0.39415 | 452.2554 | 27.37 | 59.55
2021-01-14 05:25 | 3.2716 | 3.0071 | 0.62368 | 5.2331 | 126.0172 | 114.4235 | 1.4161 | 0.46718 | 449.4484 | 27.47 | 59.44
2021-01-14 05:30 | 4.2943 | 3.1964 | 0.66573 | 5.5653 | 118.3991 | 100.0667 | 1.4309 | 0.51102 | 449.8184 | 27.55 | 59.36
2021-01-14 05:35 | 6.4027 | 3.6223 | 0.7287 | 6.2811 | 151.9478 | 155.015 | 1.46 | 0.55479 | 449.0051 | 27.76 | 58.5
2021-01-14 05:40 | 6.7481 | 3.8581 | 0.81063 | 6.7245 | 156.2484 | 109.7276 | 1.4527 | 0.57671 | 449.136 | 28.01 | 57.76
2021-01-14 05:45 | 7.745 | 4.1869 | 0.92404 | 7.3419 | 157.9053 | 145.4213 | 1.4454 | 0.63512 | 448.3591 | 28.18 | 57.2
2021-01-14 05:50 | 9.7773 | 4.2062 | 0.89886 | 7.3463 | 216.588 | 222.6921 | 1.4674 | 0.63513 | 448.5878 | 28.37 | 56.63
2021-01-14 05:55 | 7.3098 | 3.9249 | 0.84837 | 6.8646 | 258.2473 | 211.0758 | 1.4745 | 0.64237 | 448.9767 | 28.49 | 55.98
2021-01-14 06:00 | 5.0479 | 3.281 | 0.81897 | 5.8483 | 235.1206 | 186.2215 | 1.438 | 0.61317 | 448.3976 | 28.53 | 55.84
2021-01-14 06:05 | 5.7374 | 3.6423 | 0.76009 | 6.3432 | 209.8875 | 175.2539 | 1.4233 | 0.57661 | 447.9229 | 28.53 | 55.58
2021-01-14 06:10 | 6.5171 | 4.1096 | 0.73702 | 7.0385 | 203.2108 | 176.9379 | 1.416 | 0.60583 | 448.3805 | 28.56 | 55.59
2021-01-14 06:15 | 7.0027 | 3.8165 | 0.81262 | 6.6626 | 210.02 | 183.9515 | 1.4306 | 0.67882 | 448.7663 | 28.65 | 55.31
2021-01-14 06:20 | 4.6639 | 2.719 | 0.70548 | 4.8733 | 184.6639 | 113.7832 | 1.4743 | 0.50361 | 447.6823 | 28.7 | 54.97
2021-01-14 06:25 | 5.9028 | 2.7612 | 0.64244 | 4.875 | 144.489 | 120.2849 | 1.4961 | 0.40869 | 447.6597 | 28.74 | 54.64
2021-01-14 06:30 | 6.0172 | 2.6281 | 0.55001 | 4.5806 | 156.9845 | 118.0961 | 1.4741 | 0.51811 | 448.6869 | 28.78 | 54.27
2021-01-14 06:35 | 4.5863 | 2.5884 | 0.5479 | 4.5175 | 149.7865 | 124.4712 | 1.4594 | 0.44513 | 449.2911 | 28.73 | 54.38
2021-01-14 06:40 | 3.8323 | 2.7813 | 0.59824 | 4.8615 | 148.7455 | 137.0748 | 1.4521 | 0.43051 | 447.7981 | 28.7 | 54.33
2021-01-14 06:45 | 4.1391 | 2.2528 | 0.47441 | 3.9276 | 161.434 | 123.9064 | 1.4448 | 0.32107 | 447.6629 | 28.78 | 54.17
2021-01-14 06:50 | 6.004 | 2.2472 | 0.49749 | 3.9421 | 140.8158 | 121.9504 | 1.5104 | 0.48888 | 448.0949 | 28.85 | 53.87
2021-01-14 06:55 | 6.209 | 2.7843 | 0.52483 | 4.7948 | 144.304 | 110.1776 | 1.5471 | 0.49623 | 447.9192 | 28.94 | 53.82
2021-01-14 07:00 | 7.6779 | 3.169 | 0.51641 | 5.374 | 142.7146 | 107.7616 | 1.4667 | 0.5327 | 448.8138 | 29.05 | 53.39
2021-01-14 07:05 | 8.8277 | 2.7541 | 0.5605 | 4.7821 | 136.0005 | 129.9399 | 1.4522 | 0.61297 | 447.7707 | 29.05 | 53.4
2021-01-14 07:10 | 6.5403 | 2.8442 | 0.56884 | 4.9286 | 127.7412 | 75.9089 | 1.4374 | 0.51806 | 448.8527 | 29.05 | 53.18
2021-01-14 07:15 | 5.7613 | 2.7813 | 0.55836 | 4.8217 | 125.3745 | 111.2816 | 1.4375 | 0.47429 | 448.3022 | 29.06 | 53.23
2021-01-14 07:20 | 5.0714 | 2.3074 | 0.48488 | 4.0218 | 139.7496 | 132.4836 | 1.4155 | 0.4232 | 448.2852 | 29.08 | 53.1
2021-01-14 07:25 | 6.1951 | 2.3621 | 0.44917 | 4.0698 | 133.5796 | 75.813 | 1.4009 | 0.44507 | 447.2698 | 29.08 | 52.96
2021-01-14 07:30 | 6.9747 | 2.7114 | 0.57933 | 4.7354 | 135.6915 | 129.0694 | 1.4009 | 0.51076 | 447.2029 | 29.11 | 52.99
2021-01-14 07:35 | 7.3065 | 2.7345 | 0.51634 | 4.708 | 139.8757 | 116.5256 | 1.4082 | 0.62748 | 448.7085 | 29.16 | 52.74
2021-01-14 07:40 | 6.0423 | 2.4595 | 0.4597 | 4.2296 | 131.831 | 106.1904 | 1.401 | 0.47428 | 447.6266 | 29.17 | 52.85
2021-01-14 07:45 | 5.2123 | 2.6007 | 0.50591 | 4.4924 | 134.3243 | 115.3964 | 1.3865 | 0.45243 | 447.623 | 29.15 | 53.09
2021-01-14 07:50 | 5.2637 | 2.7556 | 0.58782 | 4.8138 | 150.6438 | 122.7003 | 1.4011 | 0.48164 | 448.1192 | 29.15 | 53.22
2021-01-14 07:55 | 6.3374 | 3.0722 | 0.58366 | 5.295 | 163.7498 | 146.2095 | 1.4159 | 0.53277 | 449.0648 | 29.19 | 53.29
2021-01-14 08:00 | 5.2391 | 2.6903 | 0.47874 | 4.6026 | 157.9394 | 93.4552 | 1.3941 | 0.48903 | 447.9344 | 29.22 | 53.44
2021-01-14 08:05 | 4.4973 | 2.7598 | 0.46607 | 4.6964 | 129.5624 | 87.0632 | 1.4085 | 0.42328 | 446.9758 | 29.21 | 53.11
2021-01-14 08:10 | 9.008 | 2.2409 | 0.43041 | 3.8632 | 122.1618 | 76.5313 | 1.5181 | 0.4817 | 447.981 | 29.21 | 53.3
2021-01-14 08:15 | 7.3599 | 2.2587 | 0.45562 | 3.9179 | 124.8121 | 112.5967 | 1.467 | 0.47441 | 448.5802 | 29.15 | 53.54
2021-01-14 08:20 | 5.073 | 2.5712 | 0.46614 | 4.4073 | 114.9534 | 80.3192 | 1.3722 | 0.35765 | 447.5321 | 29.14 | 53.69
2021-01-14 08:25 | 4.9456 | 2.5166 | 0.47038 | 4.3279 | 126.854 | 100.0376 | 1.3358 | 0.40878 | 446.4356 | 29.15 | 53.88
2021-01-14 08:30 | 4.7537 | 1.9644 | 0.49345 | 3.5045 | 124.5255 | 104.5703 | 1.3284 | 0.37956 | 448.0244 | 29.15 | 53.73
2021-01-14 08:35 | 4.8685 | 2.2671 | 0.48083 | 3.9559 | 118.0399 | 67.6631 | 1.3357 | 0.37954 | 448.5015 | 29.19 | 53.52
2021-01-14 08:40 | 5.5709 | 2.471 | 0.4766 | 4.2642 | 120.6595 | 116.9591 | 1.3283 | 0.42331 | 447.5338 | 29.16 | 53.46
2021-01-14 08:45 | 5.6616 | 2.7099 | 0.58171 | 4.7355 | 136.2049 | 83.868 | 1.3213 | 0.4964 | 447.8859 | 29.21 | 53.81
2021-01-14 08:50 | 5.4824 | 2.4057 | 0.51238 | 4.1999 | 125.147 | 75.2763 | 1.3212 | 0.51098 | 446.8661 | 29.21 | 53.7
2021-01-14 08:55 | 5.3929 | 2.0138 | 0.40318 | 3.49 | 107.5408 | 71.7075 | 1.3285 | 0.50367 | 449.5405 | 29.21 | 53.62
2021-01-14 09:00 | 4.0134 | 1.8662 | 0.42845 | 3.289 | 100.0126 | 102.2519 | 1.336 | 0.37234 | 447.357 | 29.23 | 53.96
2021-01-14 09:05 | 4.2316 | 1.9433 | 0.41174 | 3.3905 | 108.9323 | 91.3718 | 1.329 | 0.33591 | 447.2449 | 29.24 | 54.45
2021-01-14 09:10 | 5.5619 | 1.9299 | 0.39498 | 3.3532 | 123.5526 | 76.5414 | 1.3365 | 0.40898 | 448.2125 | 29.25 | 54.72
2021-01-14 09:15 | 5.1268 | 1.7749 | 0.42647 | 3.1471 | 107.9466 | 90.068 | 1.3364 | 0.45277 | 447.1886 | 29.26 | 54.53
2021-01-14 09:20 | 4.6664 | 1.6652 | 0.38864 | 2.9411 | 93.3988 | 57.3975 | 1.3364 | 0.41624 | 446.1967 | 29.24 | 54.5
2021-01-14 09:25 | 4.4635 | 1.7412 | 0.39509 | 3.0662 | 81.8932 | 56.1506 | 1.3369 | 0.38718 | 446.5312 | 29.25 | 55.38
2021-01-14 09:30 | 4.489 | 1.9742 | 0.44763 | 3.4738 | 74.638 | 68.581 | 1.3442 | 0.43831 | 444.9357 | 29.28 | 55.25
2021-01-14 09:35 | 5.2169 | 2.3371 | 0.47484 | 4.0572 | 86.3443 | 83.0608 | 1.4169 | 0.51125 | 444.9295 | 29.35 | 54.51
2021-01-14 09:40 | 4.8464 | 2.1056 | 0.42865 | 3.654 | 106.2271 | 60.786 | 1.4681 | 0.37982 | 445.2259 | 29.48 | 54.27
2021-01-14 09:45 | 3.6572 | 2.1248 | 0.39083 | 3.6477 | 94.8932 | 50.5872 | 1.3732 | 0.31408 | 444.5708 | 29.57 | 54.01
2021-01-14 09:50 | 3.4397 | 2.0383 | 0.42653 | 3.5509 | 83.4323 | 74.0211 | 1.3293 | 0.27024 | 444.5005 | 29.63 | 53.73
2021-01-14 09:55 | 3.3769 | 1.9101 | 0.47292 | 3.4008 | 98.2876 | 71.0167 | 1.3078 | 0.28495 | 445.835 | 29.68 | 54.35
2021-01-14 10:00 | 3.6725 | 1.6489 | 0.4731 | 2.9984 | 103.5579 | 75.8565 | 1.3084 | 0.43125 | 444.5326 | 29.74 | 55.09
2021-01-14 10:05 | 4.1582 | 1.4456 | 0.40366 | 2.6175 | 104.3004 | 64.9344 | 1.3374 | 0.38733 | 444.5528 | 29.77 | 54.66
2021-01-14 10:10 | 6.1775 | 1.8139 | 0.47707 | 3.2575 | 119.8966 | 89.2113 | 1.3515 | 0.42372 | 444.1528 | 29.8 | 53.72
2021-01-14 10:15 | 5.4591 | 2.0969 | 0.5399 | 3.7541 | 130.0661 | 79.0501 | 1.3437 | 0.37974 | 444.2426 | 29.86 | 52.61
2021-01-14 10:20 | 4.118 | 1.9317 | 0.53587 | 3.4947 | 119.8769 | 92.5089 | 1.3368 | 0.32872 | 446.0693 | 29.93 | 53.14
2021-01-14 10:25 | 4.026 | 1.9812 | 0.51035 | 3.5472 | 124.2222 | 99.57 | 1.336 | 0.32853 | 445.7747 | 29.96 | 51.67
2021-01-14 10:30 | 3.2484 | 1.7891 | 0.50646 | 3.2489 | 123.7969 | -6.1694 | 1.3295 | 0.32873 | 443.4139 | 30.02 | 52.84
2021-01-14 10:35 | 3.7977 | 2.026 | 0.66397 | 3.7695 | 118.2545 | 72.702 | 1.3293 | 0.35059 | 442.8163 | 30.12 | 52.2
2021-01-14 10:40 | 4.8829 | 1.8417 | 0.5314 | 3.3544 | 111.5346 | 83.0553 | 1.3288 | 0.38697 | 444.4248 | 30.19 | 51.18
2021-01-14 10:45 | 4.5928 | 1.8981 | 0.54026 | 3.4497 | 118.6601 | 82.5728 | 1.33 | 0.40922 | 443.3862 | 30.29 | 52.79
2021-01-14 10:50 | 3.426 | 2.0967 | 0.58606 | 3.8 | 109.243 | 63.8563 | 1.3217 | 0.33589 | 442.6456 | 30.32 | 50.99
2021-01-14 10:55 | 3.9344 | 1.6829 | 0.51636 | 3.096 | 105.4205 | 74.5996 | 1.3353 | 0.33564 | 443.9705 | 30.35 | 49.21
2021-01-14 11:00 | 4.6146 | 1.7335 | 0.56503 | 3.2222 | 107.1823 | 66.8189 | 1.3216 | 0.40159 | 442.033 | 30.4 | 50.65
2021-01-14 11:05 | 4.869 | 2.0481 | 0.59008 | 3.7316 | 98.6882 | 80.1119 | 1.3139 | 0.37228 | 443.6456 | 30.44 | 49.93
2021-01-14 11:10 | 4.8469 | 2.1469 | 0.61992 | 3.9107 | 110.1043 | 76.0152 | 1.3149 | 0.41637 | 442.2241 | 30.49 | 51.37
2021-01-14 11:15 | 4.0137 | 2.1952 | 0.62382 | 3.9887 | 110.2864 | 69.9145 | 1.3069 | 0.37967 | 442.3937 | 30.52 | 50.21
2021-01-14 11:20 | 3.3469 | 2.3745 | 0.63812 | 4.2779 | 113.2621 | 48.0109 | 1.2988 | 0.29916 | 444.1812 | 30.55 | 48.72
2021-01-14 11:25 | 2.8605 | 2.1657 | 0.62323 | 3.9429 | 105.1144 | 29.1672 | 1.2984 | 0.32825 | 444.7518 | 30.61 | 47.85
2021-01-14 11:30 | 3.0514 | 2.1105 | 0.66085 | 3.8917 | 106.4906 | 66.7788 | 1.2981 | 0.51779 | 443.7277 | 30.67 | 47.2
2021-01-14 11:35 | 2.911 | 1.8888 | 0.53078 | 3.4259 | 110.0142 | 57.7904 | 1.2908 | 0.53966 | 443.6966 | 30.74 | 46.96
2021-01-14 11:40 | 3.118 | 1.7082 | 0.56064 | 3.1791 | 112.9528 | 71.8465 | 1.2992 | 0.36496 | 443.7355 | 30.8 | 48.72
2021-01-14 11:45 | 3.9662 | 1.7144 | 0.58024 | 3.2081 | 123.826 | 50.644 | 1.33 | 0.28501 | 442.6121 | 30.85 | 51.21
2021-01-14 11:50 | 4.3264 | 2.0445 | 0.57841 | 3.7144 | 116.6642 | 73.3593 | 1.3526 | 0.30708 | 442.3488 | 30.89 | 52.1
2021-01-14 11:55 | 3.6869 | 2.1656 | 0.53642 | 3.8559 | 113.1686 | 67.3891 | 1.3747 | 0.351 | 441.7832 | 30.88 | 52.45
2021-01-14 12:00 | 3.2395 | 2.1372 | 0.63963 | 3.9156 | 99.0354 | 53.0927 | 1.3677 | 0.3657 | 442.6775 | 30.91 | 52.81
2021-01-14 12:05 | 2.8046 | 1.9659 | 0.76809 | 3.7815 | 102.8105 | 81.1829 | 1.3533 | 0.27066 | 439.9497 | 30.97 | 52.96
2021-01-14 12:10 | 2.4464 | 1.9593 | 0.69032 | 3.6958 | 97.8958 | 44.1422 | 1.3535 | 0.31459 | 441.8756 | 31.02 | 53.1
2021-01-14 12:15 | 2.2929 | 1.6753 | 0.62303 | 3.1909 | 80.7915 | 49.7723 | 1.3609 | 0.32194 | 443.3337 | 31.05 | 53.21
2021-01-14 12:20 | 3.9581 | 1.4294 | 0.54936 | 2.7405 | 85.7297 | 59.0864 | 1.3609 | 0.37315 | 442.8109 | 31.06 | 53.15
2021-01-14 12:25 | 3.9068 | 1.5036 | 0.49673 | 2.8015 | 87.3479 | 66.3819 | 1.3682 | 0.37314 | 442.8735 | 31.02 | 53.25
2021-01-14 12:30 | 3.8045 | 1.5147 | 0.48623 | 2.8079 | 89.761 | 59.0687 | 1.3756 | 0.3878 | 442.8635 | 31.01 | 53.4
2021-01-14 12:35 | 3.4587 | 1.6699 | 0.46099 | 3.0206 | 85.3158 | 58.6091 | 1.3756 | 0.37318 | 442.8219 | 31.03 | 53.4
2021-01-14 12:40 | 4.0992 | 1.9088 | 0.48414 | 3.4037 | 93.391 | 62.4007 |  |  | 441.7369 | 31.07 | 53.27
2021-01-14 12:45 | 4.0869 | 1.8788 | 0.49261 | 3.3725 | 100.7288 | 89.9365 | 1.4124 | 0.4098 | 442.1036 | 31.14 | 53.28
2021-01-14 12:50 | 3.9591 | 1.6152 | 0.49265 | 2.9686 | 102.0596 | 67.312 | 1.4271 | 0.37324 | 441.5669 | 31.13 | 53.49
2021-01-14 12:55 | 3.2297 | 1.6418 | 0.51174 | 3.0262 | 118.9847 | 72.0162 | 1.4202 | 0.37335 | 440.4862 | 31.13 | 54.03
2021-01-14 13:00 | 3.4236 | 1.4639 | 0.46985 | 2.7138 | 121.5146 | 75.5697 | 1.4209 | 0.33691 | 441.2115 | 31.19 | 54.88
2021-01-14 13:05 | 3.7441 | 1.6714 | 0.55834 | 3.1204 | 123.4005 | 59.0537 | 1.4282 | 0.3955 | 439.1363 | 31.21 | 54.79
2021-01-14 13:10 | 3.309 | 1.7984 | 0.54795 | 3.3024 | 125.0852 | 64.4664 | 1.4432 | 0.35165 | 439.4892 | 31.24 | 55.26
2021-01-14 13:15 | 3.7331 | 1.8098 | 0.51013 | 3.2842 | 127.6073 | 84.8731 | 1.4435 | 0.43233 | 439.3898 | 31.24 | 55.74
2021-01-14 13:20 | 4.3491 | 1.8511 | 0.56497 | 3.4003 | 135.4761 | 73.1674 | 1.4509 | 0.43968 | 440.3331 | 31.28 | 55.73
2021-01-14 13:25 | 4.6572 | 1.7728 | 0.56711 | 3.2867 | 137.3923 | 93.2371 | 1.4364 | 0.38841 | 440.808 | 31.29 | 55.81
2021-01-14 13:30 | 4.3752 | 1.9875 | 0.50599 | 3.5525 | 116.665 | 59.5642 | 1.3998 | 0.42507 | 440.2449 | 31.31 | 55.85
2021-01-14 13:35 | 4.0799 | 2.0988 | 0.52916 | 3.7463 | 120.744 | 70.5538 | 1.3851 | 0.48367 | 441.278 | 31.32 | 55.71
2021-01-14 13:40 | 3.3229 | 1.7563 | 0.55867 | 3.2487 | 131.0689 | 71.3335 | 1.3997 | 0.40306 | 441.2801 | 31.32 | 55.7
2021-01-14 13:45 | 3.7588 | 1.4729 | 0.51014 | 2.7678 | 113.7348 | 71.0817 | 1.4143 | 0.40303 | 441.3284 | 31.31 | 55.57
2021-01-14 13:50 | 4.1179 | 1.4962 | 0.53542 | 2.8268 | 117.7241 | 59.5137 | 1.4069 | 0.38836 | 439.8454 | 31.28 | 55.61
2021-01-14 13:55 | 4.3232 | 1.6269 | 0.5818 | 3.0734 | 104.0845 | 70.9462 | 1.4069 | 0.35172 | 440.3454 | 31.29 | 55.57
2021-01-14 14:00 | 4.4639 | 1.6749 | 0.5143 | 3.0816 | 104.3421 | 89.7395 | 1.3775 | 0.33704 | 439.8427 | 31.31 | 55.32
2021-01-14 14:05 | 5.2468 | 1.9679 | 0.54385 | 3.5603 | 139.1308 | 85.8779 | 1.3629 | 0.40301 | 440.2756 | 31.34 | 55.4
2021-01-14 14:10 | 4.9505 | 1.8932 | 0.52685 | 3.4288 | 117.4572 | 80.9108 | 1.3626 | 0.39559 | 439.2896 | 31.39 | 54.71
2021-01-14 14:15 | 4.385 | 1.7978 | 0.53935 | 3.2951 | 104.7674 | 95.4641 | 1.3622 | 0.35886 | 440.4362 | 31.39 | 54.13
2021-01-14 14:20 | 3.9235 | 1.8789 | 0.53936 | 3.4174 | 132.7516 | 80.1618 | 1.3329 | 0.39549 | 440.9553 | 31.38 | 54.2
2021-01-14 14:25 | 4.7441 | 2.015 | 0.55201 | 3.6407 | 123.9722 | 81.6395 | 1.3256 | 0.4907 | 439.4395 | 31.41 | 54.07
2021-01-14 14:30 | 4.7698 | 2.3559 | 0.6405 | 4.2539 | 112.4234 | 68.0695 | 1.3037 | 0.53465 | 440.4158 | 31.44 | 54
2021-01-14 14:35 | 4.5519 | 2.2776 | 0.64473 | 4.1339 | 111.4825 | 66.5736 | 1.311 | 0.47607 | 440.3469 | 31.48 | 53.93
2021-01-14 14:40 | 3.7314 | 2.1306 | 0.6637 | 3.9274 | 109.3711 | 83.5209 | 1.3989 | 0.56397 | 440.2823 | 31.52 | 53.84
2021-01-14 14:45 | 3.8082 | 2.0343 | 0.69109 | 3.8094 | 117.7811 | 79.7448 | 1.4795 | 0.40283 | 439.7185 | 31.56 | 53.69
2021-01-14 14:50 | 4.257 | 2.1498 | 0.64262 | 3.9379 | 124.6829 | 82.0107 | 1.4502 | 0.38085 | 439.7103 | 31.57 | 53.63
2021-01-14 14:55 | 6.1287 | 1.8088 | 0.55199 | 3.3246 | 110.2137 | 78.8779 | 1.3549 | 0.51998 | 438.6952 | 31.58 | 53.49
2021-01-14 15:00 | 6.2824 | 1.6644 | 0.50142 | 3.0527 | 120.8993 | 56.1161 | 1.3548 | 0.51997 | 440.7804 | 31.56 | 53.51
2021-01-14 15:05 | 5.8592 | 1.7318 | 0.55407 | 3.2086 | 101.3988 | 72.7925 | 1.3621 | 0.51264 | 440.3059 | 31.54 | 53.53
2021-01-14 15:10 | 4.1285 | 1.7909 | 0.52459 | 3.2698 | 118.0074 | 82.9796 | 1.3549 | 0.44674 | 440.2373 | 31.58 | 53.46
2021-01-14 15:15 | 4.2558 | 1.7177 | 0.47604 | 3.109 | 130.4838 | 79.8244 | 1.3619 | 0.44664 | 439.8597 | 31.55 | 53.12
2021-01-14 15:20 | 3.8713 | 1.6312 | 0.48026 | 2.9806 | 114.8586 | 67.4487 | 1.3912 | 0.50523 | 439.8326 | 31.56 | 53.15
2021-01-14 15:25 | 3.8198 | 1.899 | 0.50972 | 3.4227 | 107.868 | 77.0735 | 1.4424 | 0.43198 | 440.8696 | 31.57 | 52.99
2021-01-14 15:30 | 4.1142 | 1.9304 | 0.48861 | 3.4476 | 126.4257 | 91.2357 | 1.4203 | 0.43926 | 438.8391 | 31.59 | 52.71
2021-01-14 15:35 | [9 empty] | 31.6 | 52.46
2021-01-14 15:40 | 3.5877 | 1.6716 | 0.50531 | 3.0677 | 127.2403 | 89.3132 | 1.3613 | 0.57819 | 441.1094 | 31.57 | 52.12
2021-01-14 15:45 | 3.6132 | 1.8103 | 0.51371 | 3.2865 | 106.7658 | 68.4506 | 1.3539 | 0.63672 | 439.5768 | 31.58 | 52.01
2021-01-14 15:50 | 3.8565 | 1.7608 | 0.55791 | 3.2569 | 104.0049 | 88.5994 | 1.3466 | 0.42447 | 439.037 | 31.61 | 51.85
2021-01-14 15:55 | 4.139 | 2.7419 | 0.62538 | 4.8304 | 129.0862 | 105.6411 | 1.3468 | 0.45381 | 439.4502 | 31.63 | 52.12
2021-01-14 16:00 | 5.0237 | 2.7215 | 0.60648 | 4.7782 | 158.0514 | 123.0906 | 1.3396 | 0.49778 | 439.8906 | 31.65 | 52.26
2021-01-14 16:05 | 4.6912 | 1.9855 | 0.49916 | 3.5426 | 165.581 | 127.4977 | 1.3471 | 0.50517 | 440.3073 | 31.67 | 52.51
2021-01-14 16:10 | 4.1273 | 1.6516 | 0.46547 | 2.9971 | 135.6324 | 120.7843 | 1.3764 | 0.49786 | 439.3026 | 31.65 | 52.62
2021-01-14 16:15 | 5.6015 | 1.5775 | 0.47601 | 2.8919 | 138.1576 | 92.1359 | 1.4424 | 0.41001 | 438.7684 | 31.66 | 52.63
2021-01-14 16:20 | 4.3448 | 1.5017 | 0.52018 | 2.822 | 106.8072 | 44.4065 | 1.4056 | 0.58566 | 438.8071 | 31.67 | 52.35
2021-01-14 16:25 | 4.9478 | 1.7451 | 0.60661 | 3.2837 | 106.6674 | 64.3163 | 1.3765 | 0.65163 | 439.2899 | 31.65 | 52.68
2021-01-14 16:30 | 4.8082 | 2.4177 | 0.55411 | 4.2601 | 122.6789 | 73.8125 | 1.4501 | 0.65182 | 439.6182 | 31.69 | 53.15
2021-01-14 16:35 | 4.8589 | 2.1728 | 0.50559 | 3.8362 | 145.0232 | 74.4603 | 1.4939 | 0.49796 | 440.094 | 31.75 | 52.73
2021-01-14 16:40 | 4.0634 | 1.7369 | 0.52026 | 3.1848 | 130.748 | 73.424 | 1.4424 | 0.35877 | 439.1357 | 31.75 | 52.43
2021-01-14 16:45 | 5.0227 | 1.7911 | 0.48425 | 3.2276 | 96.7426 | 79.1735 | 1.3832 | 0.45376 | 439.8941 | 31.71 | 51.66
2021-01-14 16:50 | 4.8416 | 1.8481 | 0.48197 | 3.3149 | 87.4246 | 65.9476 | 1.3462 | 0.39507 | 439.5969 | 31.67 | 51.04
2021-01-14 16:55 | 3.8953 | 1.7953 | 0.55796 | 3.3099 | 86.1476 | 54.647 | 1.3467 | 0.33668 | 440.4436 | 31.67 | 51.87
2021-01-14 17:00 | 3.6119 | 1.5831 | 0.48196 | 2.9086 | 84.4101 | 83.0473 | 1.3461 | 0.33653 | 439.6075 | 31.67 | 50.99
2021-01-14 17:05 | 5.0965 | 1.5498 | 0.39769 | 2.7733 | 81.4212 | 48.7831 | 1.3532 | 0.33646 | 439.6868 | 31.68 | 50.52
2021-01-14 17:10 | 4.7855 | 1.4416 | 0.34902 | 2.5588 | 76.6702 | 70.8048 | 1.3375 | 0.38006 | 440.5672 | 31.66 | 48.98
2021-01-14 17:15 | 4.6164 | 1.3517 | 0.42446 | 2.4964 | 74.7631 | 45.3817 | 1.3294 | 0.36522 | 441.4266 | 31.6 | 47.92
2021-01-14 17:20 | 3.6312 | 1.1843 | 0.39289 | 2.2081 | 75.7546 | 56.238 | 1.3292 | 0.33596 | 441.5201 | 31.58 | 47.67
2021-01-14 17:25 | 4.0646 | 1.2236 | 0.38645 | 2.262 | 79.8189 | 67.8349 | 1.3288 | 0.33584 | 441.201 | 31.55 | 47.04
2021-01-14 17:30 | 4.4462 | 1.723 | 0.48496 | 3.1281 | 99.5531 | 85.397 | 1.3282 | 0.3503 | 441.9276 | 31.53 | 46.22
2021-01-14 17:35 | 3.9239 | 1.658 | 0.40613 | 2.9476 | 121.4581 | 127.6446 | 1.3244 | 0.33475 | 442.7311 | 31.49 | 40.35
2021-01-14 17:40 | 2.7445 | 1.1713 | 0.3356 | 2.1311 | 111.8206 | 59.9849 | 1.3197 | 0.26249 | 441.2123 | 31.54 | 44.37
2021-01-14 17:45 | 2.7212 | 1.1271 | 0.3044 | 2.0321 | 108.2157 | 72.2392 | 1.3281 | 0.26271 | 442.4811 | 31.47 | 46.33
2021-01-14 17:50 | 1.9696 | 0.85006 | 0.26901 | 1.5699 | 75.1729 | 55.8451 | 1.3296 | 0.263 | 443.6393 | 31.4 | 48.82
2021-01-14 17:55 | 2.5996 | 0.8937 | 0.2925 | 1.6624 | 2.5715 | 60.1991 | 1.3386 | 0.25602 | 443.2313 | 31.29 | 51.84
2021-01-14 18:00 | 2.8961 | 0.96161 | 0.27374 | 1.7477 | 40.9966 | 54.129 | 1.3322 | 0.25619 | 442.6136 | 31.16 | 53.64
2021-01-14 18:05 | 2.2666 | 0.85934 | 0.26723 | 1.5845 | 173.9807 | 424.866 | 1.3239 | 0.19018 | 353.6538 | 31 | 52.65
2021-01-14 18:10 | 2.4983 | 0.97375 | 0.33052 | 1.8231 | 296.9135 | 219.6949 | 1.3246 | 0.23418 | 310.4579 | 30.87 | 54.09
2021-01-14 18:15 | 2.3058 | 0.94616 | 0.27154 | 1.7218 | 183.6451 | 100.3695 | 1.3244 | 0.23415 | 310.5585 | 30.81 | 54
2021-01-14 18:20 | 1.5882 | 0.76205 | 0.28203 | 1.4501 | 99.5978 | 66.1936 | 1.3169 | 0.16095 | 311.2472 | 30.68 | 54.11
2021-01-14 18:25 | 1.8705 | 0.78148 | 0.24631 | 1.4442 | 47.486 | 55.4396 | 1.3173 | 0.17564 | 311.5468 | 30.61 | 54.99
2021-01-14 18:30 | 1.9214 | 0.81428 | 0.25889 | 1.5049 | 27.7499 | 67.3048 | 1.3024 | 0.15365 | 311.1682 | 30.54 | 54.75
2021-01-14 18:35 | 2.4471 | 1.074 | 0.32421 | 1.9705 | 30.4928 | 54.1901 | 1.2953 | 0.20491 | 311.6956 | 30.46 | 55.5
2021-01-14 18:40 | 3.2404 | 1.2412 | 0.30306 | 2.2056 | 25.7899 | 78.8554 | 1.3022 | 0.22679 | 310.8298 | 30.4 | 54.95
2021-01-14 18:45 | 2.7799 | 1.0931 | 0.25681 | 1.9345 | 35.6028 | 68.1209 | 1.2952 | 0.19757 | 311.3231 | 30.36 | 55.53
2021-01-14 18:50 | 2.6633 | 0.82906 | 0.23354 | 1.5044 | 10.9195 | 45.5935 | 1.2872 | 0.23404 | 312.1224 | 30.23 | 54.86
2021-01-14 18:55 | 2.2919 | 0.68491 | 0.20197 | 1.2518 | 11.2365 | 47.0766 | 1.2872 | 0.24134 | 312.3017 | 30.07 | 55.26
2021-01-14 19:00 | 2.2264 | 0.61451 | 0.18082 | 1.1228 | 7.2371 | 22.0287 | 1.2717 | 0.20465 | 312.6562 | 29.92 | 54.27
2021-01-14 19:05 | 2.3288 | 0.43483 | 0.19764 | 0.86626 | -7.5341 | 23.9125 | 1.2352 | 0.23388 | 311.7532 | 29.79 | 54.7
2021-01-14 19:10 | 4.4424 | 0.90715 | 0.29872 | 1.6892 | -7.8144 | 24.7645 | 1.2505 | 0.54113 | 312.1519 | 29.75 | 56.01
2021-01-14 19:15 | 5.1209 | 1.29 | 0.31765 | 2.2972 | 27.6526 | 85.846 | 1.2505 | 0.69469 | 311.5743 | 29.81 | 55.81
2021-01-14 19:20 | 3.8421 | 1.0681 | 0.2357 | 1.8729 | 36.0847 | 65.8582 | 1.2582 | 0.84858 | 311.7822 | 29.8 | 56.76
2021-01-14 19:25 | 2.8818 | 0.8801 | 0.19152 | 1.5406 | 20.0727 | 46.5596 | 1.2876 | 0.68038 | 311.9102 | 29.65 | 57.45
2021-01-14 19:30 | 2.1771 | 0.7894 | 0.21254 | 1.4226 | 14.1282 | 19.9783 | 1.2801 | 0.47548 | 312.0574 | 29.54 | 57.56
2021-01-14 19:35 | 1.9719 | 0.94027 | 0.31771 | 1.759 | 6.5969 | 26.2546 | 1.2799 | 0.28525 | 312.6752 | 29.49 | 57.36
2021-01-14 19:40 | 2.0221 | 1.0413 | 0.31965 | 1.9158 | 17.8661 | 50.6291 | 1.272 | 0.22662 | 312.8253 | 29.5 | 56.12
2021-01-14 19:45 | 1.5103 | 0.71624 | 0.22084 | 1.3187 | 37.2823 | 46.3546 | 1.2721 | 0.15353 | 314.3644 | 29.48 | 56.45
2021-01-14 19:50 | 1.6636 | 0.57615 | 0.19976 | 1.0829 | 24.7946 | 50.5516 | 1.2791 | 0.12426 | 313.4724 | 29.41 | 56.14
2021-01-14 19:55 | 1.2281 | 0.38537 | 0.17869 | 0.7694 | 37.3869 | 58.8692 | 1.2715 | 0.036537 | 311.5436 | 29.35 | 55.71
2021-01-14 20:00 | 1.4076 | 0.45818 | 0.16822 | 0.87054 | 51.0842 | 52.9678 | 1.2426 | 0.073094 | 313.1079 | 29.26 | 56.64
2021-01-14 20:05 | 1.3304 | 0.3593 | 0.14925 | 0.7 | 50.1063 | 48.2437 | 1.2349 | 0.073072 | 312.261 | 29.17 | 56.19
2021-01-14 20:10 | 1.5093 | 0.48951 | 0.15974 | 0.91008 | 59.1451 | 71.5471 | 1.2274 | 0.087674 | 313.3936 | 29.12 | 56.02
2021-01-14 20:15 | 1.4713 | 0.64051 | 0.1766 | 1.1584 | 66.6628 |  | 1.2351 | 0.10231 | 313.8007 | 29.15 | 56.54
2021-01-14 20:20 | 1.2022 | 0.67045 | 0.17443 | 1.2021 | 49.6651 | -3.1514 | 1.2273 | 0.11689 | 313.4222 | 29.12 | 55.8
2021-01-14 20:25 | 0.88246 | 0.53469 | 0.16182 | 0.98141 | 47.4634 | 45.7753 | 1.2273 | 0.080357 | 312.9669 | 29.07 | 55.87
2021-01-14 20:30 | 0.78031 | 0.50189 | 0.14504 | 0.91225 | 41.1387 | 27.9784 | 1.2275 | 0.080374 | 314.3806 | 28.95 | 56.82
2021-01-14 20:35 | 1.3684 | 0.71838 | 0.16391 | 1.2651 | 24.094 | 28.3296 | 1.2345 | 0.10957 | 313.5326 | 28.84 | 56.58
2021-01-14 20:40 | 1.2277 | 0.67726 | 0.1471 | 1.1852 | 24.872 | 23.3578 | 1.2346 | 0.12419 | 314.0879 | 28.8 | 56.76
2021-01-14 20:45 | 1.2663 | 0.74044 | 0.16814 | 1.3031 | 24.927 | 20.0562 | 1.2347 | 0.10229 | 314.1028 | 28.74 | 57.33
2021-01-14 20:50 | 1.087 | 0.4565 | 0.12608 | 0.82582 | 11.3762 | 29.9034 | 1.2272 | 0.094958 | 315.247 | 28.71 | 56.86
2021-01-14 20:55 | 1.33 | 0.42773 | 0.13239 | 0.79013 | 17.7402 | 23.183 | 1.2345 | 0.18992 | 314.2453 | 28.66 | 57.13
2021-01-14 21:00 | 1.0615 | 0.27969 | 0.11769 | 0.54641 | 11.6128 | 14.58 | 1.2711 | 0.12419 | 314.8161 | 28.59 | 57.54
2021-01-14 21:05 | 1.2787 | 0.33859 | 0.14499 | 0.66399 | 14.6903 | 3.3145 | 1.2855 | 0.094955 | 313.8749 | 28.54 | 57.33
2021-01-14 21:10 | 0.83128 | 0.18645 | 0.10507 | 0.39087 | 11.6021 | 12.2569 | 1.2857 | 0.065745 | 315.0281 | 28.4 | 58.07
2021-01-14 21:15 | 0.56258 | 0.11513 | 0.088241 | 0.26682 | 201.6483 | 491.8975 | 1.2854 | 0.036516 | 25.5359 | 28.22 | 58.08
2021-01-14 21:20 | 0.39623 | 0.06714 | 0.067209 | 0.16802 | 234.4376 | 118.3078 | 1.285 | 0.029204 | 8.8752 | 27.78 | 58.75
2021-01-14 21:25 | 0.28126 | 0.05345 | 0.058822 | 0.14075 | 112.791 | 7.4049 | 1.2853 | 0.021908 | 10.9709 | 27.51 | 60.28
2021-01-14 21:30 | 0.26848 | 0.042487 | 0.065126 | 0.13025 | 49.5341 | 6.1572 | 1.2853 | 0.021908 | 10.9775 | 27.32 | 61.03
2021-01-14 21:35 | 0.24286 | 0.034256 | 0.063011 | 0.11552 | 11.6676 | 14.0502 | 1.285 | 0.014602 | 8.3709 | 27.13 | 61.12
2021-01-14 21:40 | 0.19175 | 0.030148 | 0.056714 | 0.10293 | 6.6166 | 12.7014 | 1.2851 | 0.021905 | 10.9867 | 27.11 | 61.41
2021-01-14 21:45 | 0.15341 | 0.021928 | 0.05672 | 0.090332 | 12.447 | -2.3421 | 1.2852 | 0.014605 | 9.4156 | 27.13 | 61.61
2021-01-14 21:50 | 0.21737 | 0.017819 | 0.054629 | 0.081943 | 17.4921 | -11.3545 | 1.2855 | 0 | 6.7988 | 27.14 | 62.03
2021-01-14 21:55 | 0.30688 | 0.016449 | 0.054629 | 0.079842 | 3.2018 | 7.2219 | 1.2855 | 0.0073037 | 7.845 | 27.13 | 62.06
2021-01-14 22:00 | 0.23011 | 0.012334 | 0.050415 | 0.06932 | -3.4976 | 5.4816 | 1.2852 | 0.014604 | 12.0299 | 27.18 | 61.25
2021-01-14 22:05 | 0.2173 | 0.010962 | 0.044109 | 0.058812 | 3.0065 | 2.6894 | 1.285 | 0.0073014 | 7.846 | 27.19 | 60.98
2021-01-14 22:10 | 0.23007 | 0.0095912 | 0.044105 | 0.058807 | 12.0452 | -5.1023 | 1.2849 | 0.0073007 | 12.0356 | 27.09 | 61.1
2021-01-14 22:15 | 0.14062 | 0.0095925 | 0.050413 | 0.065117 | 12.9161 | -8.8357 | 1.2851 | 0.014604 | 7.8482 | 27.09 | 61.48
2021-01-14 22:20 | 0.17896 | 0.0095923 | 0.048311 | 0.063015 | -0.56245 | 7.0255 | 1.2778 | 0.014603 | 12.5531 | 27.19 | 61.07
2021-01-14 22:25 | 0.16614 | 0.0095903 | 0.048301 | 0.063002 | -6.0425 | 2.3516 | 1.2775 | -0.0146 | 10.9852 | 27.22 | 60.4
2021-01-14 22:30 | 0.19169 | 0.0082197 | 0.041998 | 0.054597 | 1.0939 | 3.2715 | 1.2701 | 0 | 8.8958 | 27.14 | 60.48
2021-01-14 22:35 | 0.12779 | 0.0082195 | 0.044097 | 0.054596 | 11.9305 | -11.9918 | 1.2701 | 0.0072994 | 13.085 | 27.08 | 60.63
2021-01-14 22:40 | 0.11502 | 0.0068501 | 0.0378 | 0.0483 | 13.465 | -1.8608 | 1.2702 | 0.0072999 | 12.5615 | 27.06 | 60.9
2021-01-14 22:45 | 0.17887 | 0.006848 | 0.037789 | 0.046186 | -2.7903 | 3.0152 | 1.2698 | -0.0072977 | 5.761 | 26.96 | 60.43
2021-01-14 22:50 | 0.24273 | 0.005478 | 0.035687 | 0.044084 | -1.7374 | 5.0079 | 1.2551 | -0.029189 | 12.0535 | 26.79 | 60.84
2021-01-14 22:55 | 0.1661 | 0.0054788 | 0.039891 | 0.048289 | 8.0955 | 9.0564 | 1.248 | 0.04379 | 11.0041 | 26.78 | 61.28
2021-01-14 23:00 | 0.19168 | 0.0054796 | 0.039897 | 0.048296 | 20.109 | -4.1302 | 1.2482 | 0.0072994 | 10.4729 | 26.94 | 61.12
2021-01-14 23:05 | 0.10224 | 0.00548 | 0.042 | 0.0504 | 17.0432 | -2.6787 | 1.241 | 0.0072998 | 8.8975 | 27.07 | 60.84
2021-01-14 23:10 | 0.21721 | 0.0068484 | 0.04199 | 0.050388 | -1.8399 | 5.1619 | 1.2407 | 0.014596 | 11.5144 | 27.14 | 59.96
2021-01-14 23:15 | 0.1533 | 0.0068474 | 0.039884 | 0.05038 | -3.2295 | 4.1289 | 1.2405 | 0.058376 | 10.9953 | 27.07 | 59.8
2021-01-14 23:20 | 0.20442 | 0.006848 | 0.039888 | 0.050385 | 7.3897 | 11.0896 | 1.2406 | 0.0072977 | 9.4225 | 27.11 | 59.89
2021-01-14 23:25 | 0.22998 | 0.0068484 | 0.04199 | 0.050388 | 20.7291 | -7.9932 | 1.2334 | 0.0072981 | 14.1319 | 27.13 | 59.98
2021-01-14 23:30 | 0.20445 | 0.0068489 | 0.039894 | 0.050392 | 18.1446 | -1.5231 | 1.2335 | 0.051091 | 13.6092 | 27.09 | 60.35
2021-01-14 23:35 | 0.16609 | 0.0068481 | 0.037789 | 0.048287 | -0.82791 | 7.4614 | 1.2479 | 0.051085 | 10.9966 | 27 | 60.35
2021-01-14 23:40 | 0.16606 | 0.0068469 | 0.035683 | 0.046178 | 0.55184 | 5.1913 | 1.255 | 0 | 12.0478 | 26.96 | 59.98
2021-01-14 23:45 | 0.1916 | 0.0068466 | 0.035682 | 0.046177 | 13.121 | 10.1575 | 1.2477 | -0.021889 | 13.0959 | 26.96 | 59.88
2021-01-14 23:50 |  | 0.0068469 | 0.033585 | 0.04408 | 24.1482 | -6.7754 | 1.2331 | 0.014593 | 12.5744 | 26.89 | 60.26
2021-01-14 23:55 | 0.14055 | 0.0068485 | 0.035692 | 0.04619 | 14.7908 | -8.3818 | 1.2334 | 0.080281 | 8.9051 | 26.88 | 60.94
2021-01-15 | 0.29386 | 0.0068481 | 0.037789 | 0.046187 | -8.8923 | -5.7136 | 1.2552 | 0.029191 | 9.9514 | 26.94 | 60.55
2021-01-15 00:05 | 0.2427 | 0.0068467 | 0.037781 | 0.048276 | -6.3153 | 2.5036 | 1.2623 | 0.0072963 | 9.4293 | 26.95 | 59.94
2021-01-15 00:10 | 0.2427 | 0.0068467 | 0.037782 | 0.050375 | 3.9241 | 4.3942 | 1.255 | 0.014593 | 13.0966 | 26.94 | 59.99
2021-01-15 00:15 | 0.31937 | 0.0082168 | 0.041983 | 0.054578 | 11.9777 | -17.5782 | 1.2551 | 0.014594 | 7.8567 | 26.96 | 60.17
2021-01-15 00:20 | 0.28109 | 0.0082179 | 0.044089 | 0.056685 | 6.5825 | 1.8705 | 1.2626 | 0.021894 | 8.3788 | 26.98 | 60.47
2021-01-15 00:25 | 0.21715 | 0.0082158 | 0.039879 | 0.054572 | -4.4962 | 6.3049 | 1.2695 | 0.014592 | 7.8577 | 26.96 | 59.83
2021-01-15 00:30 | 0.26822 | 0.0082151 | 0.039876 | 0.052468 | -2.3399 | -0.1124 | 1.2694 | 0.021886 | 7.3342 | 26.97 | 59.56
2021-01-15 00:35 | 0.2299 | 0.0095842 | 0.039876 | 0.054567 | 9.4207 | -0.20435 | 1.2767 | 0.014591 | 11.5252 | 26.97 | 59.55
2021-01-15 00:40 | 0.38318 | 0.0095847 | 0.039878 | 0.054569 | 14.4894 | -10.8006 | 1.2768 | 0.0072958 | 8.906 | 26.95 | 59.75
2021-01-15 00:45 | 0.21714 | 0.0095848 | 0.039878 | 0.056669 | 7.3163 | 8.1133 | 1.2768 | 0.0072959 | 7.3353 | 26.91 | 59.92
2021-01-15 00:50 | 0.28094 | 0.010952 | 0.044066 | 0.060853 | -0.48015 | 4.2703 | 1.2765 | 0.0072943 | 12.0547 | 26.88 | 59.42
2021-01-15 00:55 | 0.25541 | 0.010952 | 0.044067 | 0.060855 | 0.58233 | -4.2092 | 1.2765 | 0.0072945 | 9.4249 | 26.86 | 59.52
2021-01-15 01:00 | 0.22989 | 0.012322 | 0.044071 | 0.062959 | 5.9976 | -5.3845 | 1.2767 | 0.01459 | 9.4234 | 26.88 | 59.7
2021-01-15 01:05 |  |  |  |  | 15.4295 | -5.7835 |  |  | 11.515 | 26.92 | 59.79
2021-01-15 01:10 |  |  |  |  | 1.4203 | -5.5178 |  |  | 9.4204 | 26.95 | 59.69
2021-01-15 01:15 |  |  |  |  | -8.7849 | -3.279 |  |  | 7.3303 | 26.91 | 58.97
2021-01-15 01:20 |  |  |  |  | -2.901 | -0.91934 |  |  | 10.473 | 26.88 | 59.03
2021-01-15 01:25 |  |  |  |  | 5.6383 | -4.3104 |  |  | 9.4281 | 26.82 | 59.09
2021-01-15 01:30 |  |  |  |  | 9.7861 |  |  |  | 11.5284 | 26.66 | 59.89
2021-01-15 01:35 |  |  |  |  | 1.3383 | 7.0694 |  |  | 5.2416 | 26.56 | 60.44
2021-01-15 01:40 |  |  |  |  | -1.7159 | 11.4601 |  |  | 8.3906 | 26.47 | 60.23
2021-01-15 01:45 |  |  |  |  | 4.6882 | 2.4411 |  |  | 7.866 | 26.48 | 60.19
2021-01-15 01:50 |  |  |  |  | 11.5625 | -0.20428 |  |  | 8.9124 | 26.55 | 60.02
2021-01-15 01:55 |  |  |  |  | 16.4455 | -9.949 |  |  | 7.8618 | 26.62 | 59.87
2021-01-15 02:00 |  |  |  |  | 4.4232 | 1.6957 |  |  | 15.1954 | 26.68 | 59.84
2021-01-15 02:05 |  |  |  |  | -6.0666 | -0.040852 |  |  | 8.3854 | 26.68 | 59.26
2021-01-15 02:10 | 0.34467 | 0.023264 | 0.037758 | 0.075516 | 1.4298 | 10.6925 | 1.3198 | -0.021875 | 10.482 | 26.69 | 59.07
2021-01-15 02:15 | 0.34467 | 0.021896 | 0.041953 | 0.075515 | 13.8686 | 6.1275 | 1.2979 | -0.014583 | 9.4345 | 26.67 | 59.13
2021-01-15 02:20 | 0.35749 | 0.023268 | 0.044057 | 0.077625 | 16.0259 | -12.9004 | 1.2908 | 0.0072928 | 13.0993 | 26.72 | 59.38
2021-01-15 02:25 | 0.33198 | 0.0219 | 0.041962 | 0.07763 | 0.94997 | -3.0031 | 1.2836 | 0.014587 | 9.4305 | 26.73 | 59.53
2021-01-15 02:30 | 0.33188 | 0.021894 | 0.039852 | 0.073411 | -8.6594 | 1.4296 | 1.2832 | 0.014582 | 13.106 | 26.64 | 58.97
2021-01-15 02:35 | 0.3191 | 0.024629 | 0.037753 | 0.075505 | 1.7359 | 6.0859 | 1.2832 | 0.014582 | 14.6837 | 26.55 | 59.18
2021-01-15 02:40 | 0.45953 | 0.023262 | 0.04195 | 0.077607 | 11.1818 | -3.2269 | 1.2832 | 0.0072911 | 10.4871 | 26.57 | 59.25
2021-01-15 02:45 | 0.48505 | 0.023262 | 0.041949 | 0.077606 | 19.3407 | -4.4114 | 1.2759 | 0.014582 | 10.4862 | 26.6 | 59.12
2021-01-15 02:50 | 0.31918 | 0.023267 | 0.041958 | 0.077623 | 3.3093 | -3.1254 | 1.2762 | 0.014585 | 10.4716 | 26.65 | 59.49
2021-01-15 02:55 | 0.35743 | 0.021895 | 0.041952 | 0.075514 | -7.7614 | 1.1642 | 1.2687 | 0.014583 | 8.9033 | 26.61 | 59.24
2021-01-15 03:00 | [9 empty] | 26.62 | 58.98
2021-01-15 03:05 | 0.39572 | 0.023263 | 0.039854 | 0.075513 | 7.6796 | -1.0825 | 1.2687 | 0.014583 | 15.7109 | 26.63 | 59.12
2021-01-15 03:10 | 0.80443 | 0.43391 | 0.081828 | 0.74904 |  |  | 1.2836 | 0.094815 | 343.1559 | 26.89 | 58.96
2021-01-15 03:15 | 0.65117 | 0.39967 | 0.065039 | 0.67767 |  |  | 1.2836 | 0.051052 | 353.1415 | 27.31 | 57.39
2021-01-15 03:20 | 0.5871 | 0.26817 | 0.06082 | 0.47188 |  | -5.6872 | 1.2831 | 0.021871 | 351.7338 | 27.29 | 56.42
2021-01-15 03:25 | 0.45951 | 0.12041 | 0.054533 | 0.23701 |  | -1.9912 | 1.2759 | 0.021873 | 350.7838 | 27.18 | 57.04
2021-01-15 03:30 | 0.48508 | 0.11769 | 0.054537 | 0.23493 | -5.7699 | 4.2177 | 1.2833 | 0.014583 | 351.9419 | 27.06 | 57.66
2021-01-15 03:35 | 0.49771 | 0.16554 | 0.050329 | 0.30617 | 3.0629 | 15.5185 | 1.2903 | 0.014579 | 352.0704 | 27.03 | 57.04
2021-01-15 03:40 | 0.57437 | 0.20387 | 0.07131 | 0.38381 | 10.0987 | 11.2015 | 1.2904 | 0.021872 | 351.4725 | 27.05 | 57.37
2021-01-15 03:45 | 0.93177 | 0.33386 | 0.11745 | 0.62921 | 13.3664 | -0.93943 | 1.2905 | 0.043745 | 352.9547 | 27.12 | 57.17
2021-01-15 03:50 | 0.75296 | 0.37349 | 0.11953 | 0.68993 | 19.3677 | 7.8206 | 1.2903 | 0.036449 | 351.8664 | 27.2 | 56.51
2021-01-15 03:55 | 0.81688 | 0.36259 | 0.12794 | 0.68373 | 18.7679 | 22.2294 | 1.2977 | 0.051035 | 352.3421 | 27.2 | 56.87
2021-01-15 04:00 | 0.77843 | 0.28454 | 0.11743 | 0.55358 | 13.8841 | 29.5548 | 1.3048 | 0.036446 | 352.9261 | 27.21 | 56.28
2021-01-15 04:05 | 1.1103 | 0.34065 | 0.13421 | 0.65637 | 24.5945 | 11.4856 | 1.3194 | 0.058316 | 352.4213 | 27.18 | 56.51
2021-01-15 04:10 | 0.76572 | 0.47883 | 0.14679 | 0.88076 | 25.2585 | 10.3015 | 1.3194 | 0.051027 | 351.8932 | 27.18 | 56.55
2021-01-15 04:15 | 0.79113 | 0.53621 | 0.16564 | 0.98547 | 25.1528 | 22.9683 | 1.3265 | 0.05102 | 352.4428 | 27.2 | 56.1
2021-01-15 04:20 | 0.9061 | 0.86736 | 0.22019 | 1.5497 | 29.4852 | 13.6298 | 1.3194 | 0.065607 | 352.8565 | 27.25 | 56.32
2021-01-15 04:25 | 1.276 | 0.87407 | 0.17612 | 1.518 | -16.6697 |  | 1.3192 | 0.10204 | 425.5416 | 27.28 | 55.81
2021-01-15 04:30 | 1.5696 | 0.65252 | 0.15517 | 1.1554 |  |  | 1.3193 | 0.10205 | 512.2552 | 27.3 | 55.92
2021-01-15 04:35 | 2.0034 | 0.66892 | 0.19081 | 1.2141 |  | 8.4935 | 1.3266 | 0.1312 | 510.2751 | 27.24 | 56.07
2021-01-15 04:40 | 1.8628 | 0.79329 | 0.29142 | 1.5074 | 9.5028 | 27.5896 | 1.3482 | 0.15304 | 512.9285 | 27.26 | 55.62
2021-01-15 04:45 | 2.9351 | 1 | 0.24534 | 1.7803 | 46.5629 | 56.047 | 1.3558 | 0.2041 | 511.2314 | 27.28 | 56.05
2021-01-15 04:50 | 2.7305 | 0.98481 | 0.29143 | 1.801 | 65.2354 | 51.9964 | 1.341 | 0.19678 | 510.2291 | 27.3 | 55.58
2021-01-15 04:55 | 1.9013 | 1.1846 | 0.35645 | 2.1723 | 79.8486 | 60.6674 | 1.3338 | 0.1312 | 509.0234 | 27.37 | 55.57
2021-01-15 05:00 | 1.7734 | 1.354 | 0.34591 | 2.4214 | 69.1185 | 61.0757 | 1.3336 | 0.12389 | 509.5296 | 27.43 | 54.93
2021-01-15 05:05 | 3.0114 | 1.5238 | 0.33548 | 2.6713 | 75.9082 | 61.0043 | 1.3411 | 0.21866 | 508.8205 | 27.49 | 55.18
2021-01-15 05:10 | 3.1134 | 1.8261 | 0.42562 | 3.2226 | 78.2524 | 63.8595 | 1.3411 | 0.2478 | 508.2036 | 27.56 | 54.83
2021-01-15 05:15 | 2.6285 | 1.7166 | 0.39627 | 3.0276 | 83.1214 | 65.3906 | 1.341 | 0.24051 | 506.587 | 27.59 | 54.73
2021-01-15 05:20 | 2.8455 | 1.9506 | 0.44451 | 3.4344 | 88.0238 | 63.2081 | 1.3557 | 0.29883 | 508.5587 | 27.65 | 54.62
2021-01-15 05:25 | 3.6872 | 1.9504 | 0.48009 | 3.4697 | 100.2919 | 95.6784 | 1.3555 | 0.35709 | 510.6077 | 27.71 | 54.11
2021-01-15 05:30 | 4.4149 | 2.4813 | 0.59547 | 4.3968 | 134.4593 | 119.8517 | 1.3629 | 0.32798 | 507.2986 | 27.78 | 54.19
2021-01-15 05:35 | 4.3126 | 2.5605 | 0.66881 | 4.5936 | 158.9377 | 145.9642 | 1.3701 | 0.34254 | 507.6518 | 27.9 | 53.64
2021-01-15 05:40 | 3.6877 | 3.0381 | 0.63741 | 5.2964 | 161.3185 | 121.7417 | 1.363 | 0.31341 | 507.8696 | 28.05 | 53.43
2021-01-15 05:45 | 4.2486 | 2.8667 | 0.64571 | 5.0378 | 159.3582 | 131.7489 | 1.3701 | 0.34981 | 506.7739 | 28.12 | 52.88
2021-01-15 05:50 | 3.93 | 3.276 | 0.66466 | 5.6842 | 160.9277 | 140.2873 | 1.3702 | 0.39358 | 506.0777 | 28.19 | 52.95
2021-01-15 05:55 | 4.7592 | 3.5604 | 0.79462 | 6.2521 | 173.9154 | 154.3578 | 1.3702 | 0.40814 | 505.8966 | 28.31 | 52.48
2021-01-15 06:00 | 4.3001 | 3.4689 | 0.72965 | 6.0469 | 202.6374 | 178.659 | 1.3702 | 0.34985 | 507.8102 | 28.4 | 52.31
2021-01-15 06:05 | 4.4909 | 2.8694 | 0.66666 | 5.0649 | 176.1437 | 145.4324 | 1.3992 | 0.31336 | 509.496 | 28.37 | 52.05
2021-01-15 06:10 | 3.8784 | 2.4303 | 0.5828 | 4.3081 | 183.3275 | 193.7278 | 1.421 | 0.30607 | 508.0371 | 28.31 | 52.21
2021-01-15 06:15 | 4.0064 | 2.7411 | 0.60592 | 4.8075 | 204.2105 | 175.8542 | 1.4066 | 0.34983 | 507.9509 | 28.33 | 52.41
2021-01-15 06:20 | 4.7972 | 2.3319 | 0.51783 | 4.0902 | 191.8875 | 151.5095 | 1.4065 | 0.40082 | 509.4649 | 28.38 | 52.09
2021-01-15 06:25 | 4.1977 | 2.4086 | 0.55349 | 4.2455 | 160.0283 | 98.9485 | 1.3701 | 0.3644 | 509.4278 | 28.39 | 52.16
2021-01-15 06:30 | 4.0573 | 2.094 | 0.48849 | 3.6983 | 121.5142 | 117.1558 | 1.3701 | 0.31337 | 508.8826 | 28.41 | 52.05
2021-01-15 06:35 | 5.4994 | 2.1872 | 0.5619 | 3.9145 | 95.799 | 90.0725 | 1.3775 | 0.34984 | 508.3777 | 28.38 | 52.31
2021-01-15 06:40 | 4.5289 | 2.3701 | 0.54714 | 4.1821 | 105.7849 | 80.9027 | 1.37 | 0.29877 | 507.4025 | 28.39 | 51.86
2021-01-15 06:45 | 4.2997 | 2.5632 | 0.74008 | 4.6669 | 126.905 | 114.3197 | 1.3628 | 0.32795 | 508.2706 | 28.46 | 51.93
2021-01-15 06:50 | 4.1974 | 2.5069 | 0.50314 | 4.3458 | 146.3091 | 119.9255 | 1.3627 | 0.37166 | 508.7758 | 28.49 | 51.67
2021-01-15 06:55 | 4.9118 | 3.0963 | 0.60166 | 5.3499 | 134.7027 | 81.385 | 1.3919 | 0.36436 | 508.7482 | 28.51 | 51.58
2021-01-15 07:00 | 4.3631 | 3.2754 | 0.56391 | 5.5846 | 130.7691 | 116.7665 | 1.37 | 0.32063 | 509.2183 | 28.55 | 51.38
2021-01-15 07:05 | 4.7205 | 2.8024 | 0.48847 | 4.7841 | 142.9228 | 100.7798 | 1.3555 | 0.37166 | 509.6153 | 28.61 | 51.3
2021-01-15 07:10 | 4.5169 | 2.3485 | 0.40675 | 4.0088 | 129.4218 | 105.7811 | 1.3629 | 0.31339 | 508.9949 | 28.64 | 51.45
2021-01-15 07:15 | 5.1031 | 2.072 | 0.4025 | 3.5785 | 118.4338 | 95.0002 | 1.3773 | 0.32064 | 507.4637 | 28.66 | 51.08
2021-01-15 07:20 | 4.5803 | 2.1692 | 0.41091 | 3.736 | 117.5835 | 79.0423 | 1.3337 | 0.2988 | 507.8695 | 28.71 | 51.08
2021-01-15 07:25 | 5.7668 | 2.7286 | 0.52831 | 4.7128 | 106.6497 | 82.2047 | 1.3482 | 0.36438 | 507.854 | 28.72 | 51.05
2021-01-15 07:30 | 6.5325 | 2.4387 | 0.50107 | 4.2392 | 108.4194 | 80.299 | 1.3483 | 0.44456 | 508.8772 | 28.72 | 51.14
2021-01-15 07:35 | 4.8485 | 1.9929 | 0.44658 | 3.5034 | 113.4561 | 100.7273 | 1.3337 | 0.41542 | 508.3022 | 28.74 | 51.18
2021-01-15 07:40 | 4.287 | 2.198 | 0.44866 | 3.8178 | 119.7104 | 109.6358 | 1.341 | 0.33525 | 508.3648 | 28.71 | 51.21
2021-01-15 07:45 | 4.4523 | 2.541 | 0.57229 | 4.4672 | 138.8212 | 111.1121 | 1.3481 | 0.34249 | 508.9161 | 28.73 | 50.84
2021-01-15 07:50 | 3.8913 | 2.2471 | 0.46122 | 3.9057 | 139.2917 | 100.7611 | 1.3482 | 0.34252 | 507.2287 | 28.78 | 50.89
2021-01-15 07:55 | 4.5419 | 2.5904 | 0.47588 | 4.4465 | 121.7219 | 88.9797 | 1.3773 | 0.39352 | 510.3867 | 28.77 | 50.84
2021-01-15 08:00 | 5.1665 | 2.3973 | 0.44859 | 4.1232 | 80.2355 | 76.3574 | 1.4136 | 0.40077 | 508.351 | 28.77 | 50.61
2021-01-15 08:05 | 5.511 | 2.6353 | 0.40667 | 4.4461 | 85.278 | 76.7257 | 1.4792 | 0.47364 | 509.9241 | 28.76 | 50.67
2021-01-15 08:10 | 5.1539 | 2.3016 | 0.47375 | 3.9997 | 94.1376 | 70.5216 | 1.4501 | 0.41535 | 507.2802 | 28.78 | 50.64
2021-01-15 08:15 | 4.0699 | 1.8956 | 0.46122 | 3.3669 | 95.1059 | 41.8576 | 1.4138 | 0.27693 | 507.7628 | 28.78 | 50.82
2021-01-15 08:20 | 3.9543 | 1.9828 | 0.49676 | 3.536 | 93.5457 | 65.4524 | 1.3698 | 0.24773 | 509.4438 | 28.77 | 50.35
2021-01-15 08:25 | 3.674 | 2.1347 | 0.39409 | 3.6663 | 93.1859 | 54.5379 | 1.3262 | 0.32061 | 508.9155 | 28.75 | 50.61
2021-01-15 08:30 | 3.5209 | 1.9802 | 0.37941 | 3.4168 | 95.7978 | 59.3646 | 1.3189 | 0.30604 | 507.3752 | 28.74 | 50.62
2021-01-15 08:35 | 3.8273 | 1.9667 | 0.38573 | 3.4003 | 103.1642 | 83.7928 | 1.319 | 0.32064 | 509.4154 | 28.74 | 50.82
2021-01-15 08:40 | 3.8527 | 2.1566 | 0.46746 | 3.7733 | 89.055 | 38.0367 | 1.3189 | 0.29147 | 507.9126 | 28.72 | 50.76
2021-01-15 08:45 | 3.4698 | 2.0923 | 0.45278 | 3.66 | 80.7861 | 57.9974 | 1.3262 | 0.29147 | 507.9436 | 28.71 | 50.72
2021-01-15 08:50 | 3.5465 | 1.9693 | 0.43602 | 3.4546 | 81.4211 | 56.2538 | 1.3408 | 0.29876 | 507.8791 | 28.74 | 50.7
2021-01-15 08:55 | 4.9116 | 1.8298 | 0.40039 | 3.2052 | 76.758 | 52.162 | 1.3408 | 0.38621 | 507.8729 | 28.74 | 50.73
2021-01-15 09:00 | 4.6696 | 1.7712 | 0.44026 | 3.1552 | 92.4125 | 82.1546 | 1.3409 | 0.34981 | 506.7495 | 28.76 | 50.91
2021-01-15 09:05 | 4.4265 | 1.9337 | 0.39827 | 3.3602 | 90.4596 | 60.7316 | 1.3334 | 0.3279 | 506.8423 | 28.75 | 50.57
2021-01-15 09:10 | 3.7501 | 1.8419 | 0.42968 | 3.253 | 98.5651 | 81.2379 | 1.3261 | 0.32787 | 509.9537 | 28.78 | 50.29
2021-01-15 09:15 | 3.7882 | 1.7283 | 0.42127 | 3.0705 | 105.8348 | 81.6719 | 1.326 | 0.32785 | 507.8513 | 28.81 | 50.06
2021-01-15 09:20 | 3.0616 | 1.5494 | 0.40246 | 2.7774 | 98.9601 | 45.699 | 1.3261 | 0.25503 | 508.8423 | 28.8 | 50.41
2021-01-15 09:25 | 3.4186 | 1.6218 | 0.43598 | 2.9219 | 87.6182 | 49.5442 | 1.3334 | 0.26959 | 509.4188 | 28.78 | 50.36
2021-01-15 09:30 | 3.8773 | 1.8444 | 0.50508 | 3.3323 | 82.729 | 52.5576 | 1.3332 | 0.28412 | 506.4097 | 28.76 | 50.03
2021-01-15 09:35 | 3.9543 | 2.1441 | 0.5261 | 3.8127 | 106.8217 | 88.4636 | 1.3406 | 0.39345 | 507.2714 | 28.83 | 50.12
2021-01-15 09:40 | 3.4684 | 1.8495 | 0.48192 | 3.3169 | 125.494 | 91.4325 | 1.3475 | 0.28406 | 507.8972 | 28.87 | 49.17
2021-01-15 09:45 | 4.0293 | 2.09 | 0.46933 | 3.6729 | 106.6074 | 52.8396 | 1.3328 | 0.26948 | 507.2808 | 28.94 | 48.87
2021-01-15 09:50 | 3.455 | 1.9038 | 0.43155 | 3.3498 | 88.7536 | 67.0089 | 1.3181 | 0.28401 | 507.7895 | 28.99 | 48.38
2021-01-15 09:55 | 3.1114 | 1.8591 | 0.41279 | 3.2625 | 93.4443 | 70.3791 | 1.3111 | 0.25493 | 507.6335 | 29.02 | 48.8
2021-01-15 10:00 | 3.1747 | 1.8725 | 0.54891 | 3.4171 | 106.7325 | 68.5744 | 1.3036 | 0.2549 | 507.048 | 29.1 | 48.25
2021-01-15 10:05 | 3.9274 | 1.7032 | 0.47982 | 3.0905 | 100.1325 | 72.5287 | 1.3037 | 0.26221 | 506.3291 | 29.19 | 48.23
2021-01-15 10:10 | 3.9786 | 1.5474 | 0.44632 | 2.8183 | 92.8237 | 57.761 | 1.2965 | 0.29136 | 506.2669 | 29.21 | 48.31
2021-01-15 10:15 | 2.8817 | 1.6649 | 0.45047 | 3.0025 | 112.2999 | 83.8908 | 1.3037 | 0.22578 | 506.8589 | 29.19 | 48.18
2021-01-15 10:20 | 3.2132 | 1.6867 | 0.38971 | 2.9752 | 114.1251 | 79.4836 | 1.3037 | 0.29861 | 507.867 | 29.21 | 48.11
2021-01-15 10:25 | 4.0431 | 1.7706 | 0.39191 | 3.1059 | 106.7168 | 76.4639 | 1.304 | 0.29141 | 505.9924 | 29.32 | 48.43
2021-01-15 10:30 | 3.7734 | 1.6591 | 0.36449 | 2.9075 | 118.3843 | 76.1421 | 1.318 | 0.29855 | 507.6725 | 29.39 | 47.11
2021-01-15 10:35 | 2.9057 | 2.0985 | 0.43349 | 3.6501 | 105.6872 | 75.5287 | 1.3103 | 0.26207 | 506.7473 | 29.41 | 46.37
2021-01-15 10:40 | 3.1232 | 1.8694 | 0.41475 | 3.2803 | 102.2871 | 49.624 | 1.3107 | 0.29126 | 506.5869 | 29.43 | 46.91
2021-01-15 10:45 | 3.6093 | 1.75 | 0.41285 | 3.0953 | 104.295 | 75.8491 | 1.3113 | 0.27683 | 506.7536 | 29.5 | 47.8
2021-01-15 10:50 | 4.0957 | 2.0831 | 0.51366 | 3.7067 | 121.2011 | 87.2926 | 1.2973 | 0.29152 | 504.353 | 29.57 | 48.59
2021-01-15 10:55 | 3.4961 | 2.0175 | 0.52206 | 3.6146 | 95.9406 | 37.3289 | 1.29 | 0.29882 | 506.3277 | 29.62 | 48.51
2021-01-15 11:00 | 4.7616 | 2.3592 | 0.5307 | 4.147 | 102.5027 | 85.1211 | 1.3052 | 0.34271 | 504.463 | 29.66 | 49.53
2021-01-15 11:05 | 4.5717 | 2.1219 | 0.5267 | 3.7792 | 104.4699 | 72.1462 | 1.3057 | 0.34283 | 506.3027 | 29.69 | 50.27
2021-01-15 11:10 | 3.9971 | 1.703 | 0.44066 | 3.0511 | 104.1334 | 40.4867 | 1.2984 | 0.32095 | 505.8493 | 29.65 | 50.4
2021-01-15 11:15 | 4.0096 | 1.5948 | 0.41546 | 2.86 | 103.5249 | 53.4276 | 1.2983 | 0.32093 | 506.3947 | 29.65 | 50.27
2021-01-15 11:20 | 3.2054 | 1.458 | 0.38191 | 2.6167 | 96.3703 | 72.0248 | 1.2911 | 0.24072 | 505.7933 | 29.68 | 50.34
2021-01-15 11:25 | 3.6654 | 1.9592 | 0.52465 | 3.5298 | 80.8682 | 40.2859 | 1.2839 | 0.2845 | 506.2714 | 29.68 | 50.52
2021-01-15 11:30 | 5.7851 | 1.844 | 0.49733 | 3.324 | 80.6691 | 56.1394 | 1.2911 | 0.34284 | 506.2358 | 29.72 | 50.26
2021-01-15 11:35 | 4.8143 | 1.7317 | 0.41967 | 3.0741 | 98.237 | 44.2352 | 1.2911 | 0.35742 | 504.14 | 29.75 | 50.07
2021-01-15 11:40 | 4.7891 | 1.8017 | 0.44279 | 3.2024 | 97.7238 | 74.9301 | 1.2839 | 0.35015 | 504.0244 | 29.8 | 50.06
2021-01-15 11:45 | 4.8834 | 1.8939 | 0.50835 | 3.4135 | 103.1086 | 82.5114 | 1.2706 | 0.3359 | 503.4227 | 29.86 | 52.18
2021-01-15 11:50 | 3.7602 | 2.1156 | 0.56324 | 3.806 | 113.4816 | 74.4675 | 1.2712 | 0.27761 | 503.1003 | 29.91 | 53.12
2021-01-15 11:55 | 3.402 | 1.626 | 0.48125 | 2.9737 | 108.8423 | 95.6232 | 1.2784 | 0.25568 | 503.0867 | 29.93 | 52.97
2021-01-15 12:00 | 3.5798 | 1.3075 | 0.41807 | 2.4202 | 122.3072 | 97.2382 | 1.278 | 0.2483 | 503.8358 | 29.89 | 52.33
2021-01-15 12:05 | 3.745 | 1.4099 | 0.40956 | 2.5708 | 118.9622 | 84.0936 | 1.2704 | 0.27013 | 502.4036 | 29.9 | 51.7
2021-01-15 12:10 | 3.987 | 1.4466 | 0.43466 | 2.6521 | 82.3979 | 57.423 | 1.2701 | 0.30657 | 503.5494 | 29.9 | 51.18
2021-01-15 12:15 | 3.5912 | 1.9481 | 0.4641 | 3.4503 | 66.5679 | 41.3046 | 1.2556 | 0.30659 | 502.4594 | 29.91 | 51.34
2021-01-15 12:20 | 3.693 | 1.5384 | 0.41366 | 2.7738 | 68.1665 | 50.2661 | 1.2482 | 0.32846 | 504.5383 | 29.93 | 51.06
2021-01-15 12:25 | 4.0908 | 1.5294 | 0.40332 | 2.7476 | 76.8869 | 50.2761 | 1.2414 | 0.32129 | 502.772 | 29.94 | 51.95
2021-01-15 12:30 | 4.0386 | 1.5824 | 0.43261 | 2.8603 | 77.7859 | 54.945 | 1.2556 | 0.3066 | 504.4579 | 29.94 | 51.32
2021-01-15 12:35 | 3.2969 | 1.5849 | 0.43046 | 2.8599 | 75.8545 | 50.6957 | 1.2482 | 0.31387 | 504.0096 | 29.94 | 50.99
2021-01-15 12:40 | 3.0928 | 1.5139 | 0.42211 | 2.7427 | 77.8169 | 51.2849 | 1.2556 | 0.2774 | 503.414 | 29.95 | 51.25
2021-01-15 12:45 | 4.3969 | 1.5469 | 0.41585 | 2.785 | 75.6566 | 43.2733 | 1.2557 | 0.37234 | 503.3325 | 29.97 | 51.41
2021-01-15 12:50 | 3.7455 | 1.7691 | 0.41591 | 3.1298 | 82.7028 | 53.8126 | 1.2632 | 0.34319 | 503.2642 | 29.97 | 51.72
2021-01-15 12:55 | 2.659 | 2.1104 | 0.47054 | 3.7034 | 88.34 | 53.7935 | 1.2486 | 0.32859 | 502.7358 | 29.97 | 51.78
2021-01-15 13:00 | 2.7484 | 2.1392 | 0.57135 | 3.8503 | 93.6256 | 61.5751 | 1.2486 | 0.31398 | 503.1606 | 30.03 | 51.56
2021-01-15 13:05 | 3.5169 | 1.8096 | 0.57159 | 3.3455 | 105.3374 | 56.8736 | 1.2418 | 0.28489 | 502.3571 | 30.08 | 52.34
2021-01-15 13:10 | 4.4656 | 1.5061 | 0.46677 | 2.7754 | 101.8832 | 47.6608 | 1.2498 | 0.27773 | 502.0032 | 30.13 | 53.41
2021-01-15 13:15 | 4.1976 | 1.6051 | 0.42899 | 2.8894 | 95.9711 | 57.2305 | 1.2573 | 0.33626 | 501.4613 | 30.1 | 53.85
2021-01-15 13:20 | 2.8794 | 1.4652 | 0.38272 | 2.6286 | 89.3571 | 47.1971 | 1.2646 | 0.35088 | 501.4861 | 30.09 | 53.82
2021-01-15 13:25 | 3.8271 | 1.5999 | 0.37648 | 2.8288 | 112.6568 | 91.9932 | 1.2721 | 0.38749 | 500.3263 | 30.12 | 54.1
2021-01-15 13:30 | 3.7251 | 1.6385 | 0.43541 | 2.949 | 146.8618 | 105.5304 | 1.2576 | 0.35097 | 501.2042 | 30.18 | 54.14
2021-01-15 13:35 | 4.4765 | 1.3779 | 0.41613 | 2.5283 | 154.1956 | 97.4185 | 1.2566 | 0.33606 | 503.7045 | 30.17 | 52.25
2021-01-15 13:40 | 4.848 | 1.5893 | 0.42249 | 2.8586 | 135.1106 | 68.5837 | 1.264 | 0.32149 | 503.14 | 30.16 | 52.58
2021-01-15 13:45 | 5.0687 | 1.5931 | 0.37438 | 2.8163 | 118.6489 | 45.0143 | 1.2648 | 0.32169 | 500.2194 | 30.18 | 53.95
2021-01-15 13:50 | 4.4534 | 1.6846 | 0.39954 | 2.9818 | 101.2717 | 49.6735 | 1.2573 | 0.2997 | 500.8353 | 30.18 | 53.49
2021-01-15 13:55 | 3.7878 | 1.5707 | 0.46261 | 2.8703 | 100.3672 | 39.9258 | 1.2645 | 0.28507 | 502.3776 | 30.19 | 53.38
2021-01-15 14:00 | 4.3143 | 1.4767 | 0.41652 | 2.6822 | 91.9092 | -6.0221 | 1.2724 | 0.351 | 502.0981 | 30.23 | 54.21
2021-01-15 14:05 | 3.9179 | 1.6512 | 0.45023 | 2.9812 | 86.9917 | 49.0525 | 1.3091 | 0.35104 | 500.9551 | 30.27 | 54.31
2021-01-15 14:10 | 3.0728 | 1.7623 | 0.49229 | 3.1936 | 112.4836 | 109.0421 | 1.2871 | 0.25596 | 502.9354 | 30.32 | 54.11
2021-01-15 14:15 | 3.6489 | 1.6745 | 0.46705 | 3.0316 | 110.3131 | 53.2514 | 1.2725 | 0.3291 | 500.8948 | 30.31 | 54.16
2021-01-15 14:20 | 4.7246 | 1.599 | 0.47759 | 2.9287 | 111.4031 | 78.2362 | 1.2726 | 0.38762 | 501.3064 | 30.36 | 54.09
2021-01-15 14:25 | 5.1852 | 1.8172 | 0.5028 | 3.2903 | 100.2524 | 69.7711 | 1.2725 | 0.40953 | 501.3212 | 30.37 | 53.92
2021-01-15 14:30 | 4.7496 | 1.9735 | 0.52171 | 3.5468 | 87.5881 | 50.738 | 1.2651 | 0.42413 | 501.3315 | 30.38 | 53.77
2021-01-15 14:35 | 5.5692 | 1.8967 | 0.51542 | 3.4228 | 82.8186 | 60.2755 | 1.2725 | 0.4534 | 501.3009 | 30.39 | 53.77
2021-01-15 14:40 | 5.3255 | 1.6413 | 0.4712 | 2.9892 | 48.9539 | 32.7008 | 1.2724 | 0.4168 | 499.7705 | 30.41 | 53.53
2021-01-15 14:45 | 4.6085 | 1.9144 | 0.49853 | 3.4329 | 38.4756 | 90.1109 | 1.2723 | 0.37292 | 499.7387 | 30.44 | 53.36
2021-01-15 14:50 | 5.6322 | 2.0501 | 0.52374 | 3.6662 | 79.66 | 68.7847 | 1.2795 | 0.43139 | 500.2829 | 30.44 | 53.22
2021-01-15 14:55 | 5.6445 | 2.4231 | 0.51107 | 4.2232 | 108.4862 | 91.54 | 1.2721 | 0.48983 | 501.2916 | 30.48 | 52.88
2021-01-15 15:00 | 5.5543 | 1.8384 | 0.46896 | 3.2848 | 126.2805 | 80.0029 | 1.2793 | 0.41668 | 500.8101 | 30.49 | 52.64
2021-01-15 15:05 | 5.3108 | 1.8918 | 0.51729 | 3.4171 | 135.6593 | 84.0922 | 1.2719 | 0.42396 | 501.8717 | 30.49 | 52.48
2021-01-15 15:10 | 4.21 | 1.6736 | 0.45839 | 3.0237 | 134.8854 | 82.9418 | 1.2499 | 0.39471 | 498.8184 | 30.49 | 52.38
2021-01-15 15:15 | 3.1988 | 1.3483 | 0.41209 | 2.4789 | 122.5066 | 87.0894 | 1.2717 | 0.29235 | 501.4317 | 30.49 | 52.16
2021-01-15 15:20 | 3.0705 | 1.3317 | 0.38681 | 2.4302 | 105.5217 | 47.6229 | 1.3008 | 0.30692 | 501.6269 | 30.41 | 52.12
2021-01-15 15:25 | 3.6466 | 1.6912 | 0.43101 | 3.0234 | 109.1884 | 60.3929 | 1.2936 | 0.29965 | 501.6343 | 30.37 | 52.5
2021-01-15 15:30 | 3.6602 | 1.5544 | 0.43951 | 2.8221 | 116.9613 | 79.2847 | 1.2793 | 0.28509 | 500.968 | 30.4 | 52.87
2021-01-15 15:35 | [9 empty] | 30.42 | 53.04
2021-01-15 15:40 | 3.9678 | 1.3213 | 0.35544 | 2.3829 | 112.6025 | 79.5293 | 1.2429 | 0.38748 | 499.3954 | 30.39 | 53.1
2021-01-15 15:45 | 5.5428 | 1.3942 | 0.3702 | 2.5052 | 118.7098 | 63.0211 | 1.2503 | 0.43871 | 502.9674 | 30.36 | 53.47
2021-01-15 15:50 | 5.5682 | 1.4587 | 0.38492 | 2.6208 | 119.3518 | 89.1939 | 1.2795 | 0.40214 | 499.858 | 30.39 | 53.32
2021-01-15 15:55 | 5.2228 | 1.4779 | 0.37441 | 2.6419 | 112.29 | 72.5558 | 1.3381 | 0.38753 | 500.8809 | 30.38 | 53.43
2021-01-15 16:00 | 3.6355 | 1.375 | 0.36811 | 2.4779 | 99.1413 | 53.6106 | 1.3015 | 0.28517 | 500.3665 | 30.38 | 53.44
2021-01-15 16:05 | 3.7507 | 1.4121 | 0.35969 | 2.5263 | 93.8877 | 60.1955 | 1.2577 | 0.29248 | 500.3831 | 30.37 | 53.47
2021-01-15 16:10 | 7.0285 | 1.2667 | 0.36814 | 2.3098 | 94.7578 | 57.4159 | 1.287 | 0.45339 | 500.8267 | 30.38 | 53.67
2021-01-15 16:15 | 6.5803 | 1.4053 | 0.37655 | 2.5307 | 92.0318 | 50.5939 | 1.287 | 0.38025 | 499.8282 | 30.37 | 53.66
2021-01-15 16:20 | 4.9806 | 1.4618 | 0.37028 | 2.6109 | 101.8754 | 60.6479 | 1.2433 | 0.3291 | 499.1767 | 30.42 | 53.76
2021-01-15 16:25 | 4.584 | 1.5497 | 0.4692 | 2.8447 | 89.5298 | 60.1099 | 1.2434 | 0.32913 | 500.6885 | 30.41 | 53.97
2021-01-15 16:30 | 5.0594 | 1.8097 | 0.46725 | 3.2434 | 96.2393 | 70.2736 | 1.2511 | 0.4463 | 499.9516 | 30.45 | 54.55
2021-01-15 16:35 | 4.7652 | 1.7357 | 0.43782 | 3.0984 | 100.6745 | 92.6505 | 1.2585 | 0.41707 | 500.3387 | 30.5 | 54.58
2021-01-15 16:40 | 4.9439 | 1.5666 | 0.37883 | 2.7781 | 122.0349 | 100.7428 | 1.3022 | 0.5048 | 499.3668 | 30.51 | 54.25
2021-01-15 16:45 | 5.6743 | 1.3278 | 0.38938 | 2.4247 | 124.3993 | 90.4098 | 1.3096 | 0.43898 | 499.3852 | 30.48 | 54.48
2021-01-15 16:50 | 5.9046 | 1.1987 | 0.39357 | 2.2309 | 100.6004 | 59.3889 | 1.3023 | 0.38775 | 499.4769 | 30.44 | 54.49
2021-01-15 16:55 | 7.083 | 1.3483 | 0.35358 | 2.4204 | 63.1088 | 87.3831 | 1.3023 | 0.43896 | 500.5294 | 30.42 | 54.57
2021-01-15 17:00 | 7.1598 | 1.5639 | 0.41462 | 2.8118 | 72.1364 | 71.788 | 1.2876 | 0.51213 | 500.0154 | 30.42 | 54.58
2021-01-15 17:05 | 6.1089 | 1.5212 | 0.36617 | 2.6979 | 94.4633 | 67.9685 | 1.2509 | 0.45355 | 500.1388 | 30.38 | 54.45
2021-01-15 17:10 | 6.5318 | 1.3949 | 0.40407 | 2.5402 | 100.4413 | 78.1153 | 1.2437 | 0.38773 | 500.6426 | 30.37 | 54.59
2021-01-15 17:15 | 6.2358 | 1.4152 | 0.364 | 2.5332 | 108.3359 | 80.8832 | 1.2507 | 0.39495 | 500.8101 | 30.34 | 54.16
2021-01-15 17:20 | 4.8788 | 1.1792 | 0.34929 | 2.1567 | 103.1786 | 86.6856 | 1.2507 | 0.32914 | 500.3045 | 30.32 | 54.34
2021-01-15 17:25 | 4.8026 | 1.0791 | 0.34723 | 2.0034 | 117.4864 | 86.1144 | 1.2509 | 0.31456 | 500.7759 | 30.3 | 54.73
2021-01-15 17:30 | 3.701 | 0.87586 | 0.32196 | 1.6645 | 96.9995 | 57.1158 | 1.2728 | 0.25602 | 500.377 | 30.25 | 54.75
2021-01-15 17:35 | 2.984 | 0.81687 | 0.27357 | 1.5257 | 92.6291 | 59.4031 | 1.2582 | 0.18288 | 500.4365 | 30.2 | 55.01
2021-01-15 17:40 | 3.1888 | 0.79624 | 0.27987 | 1.5004 | 78.8148 | 51.8602 | 1.2435 | 0.21945 | 501.5823 | 30.14 | 55.1
2021-01-15 17:45 | 3.6753 | 0.78524 | 0.2967 | 1.4982 | 75.0731 | 48.693 | 1.2508 | 0.27796 | 501.1509 | 30.1 | 55.16
2021-01-15 17:50 | 3.752 | 0.66167 | 0.2483 | 1.2604 | 63.8232 | 23.1116 | 1.2508 | 0.2487 | 502.2354 | 30.07 | 55.21
2021-01-15 17:55 | 3.0994 | 0.7414 | 0.28832 | 1.4248 | 52.9821 | 39.8262 | 1.2583 | 0.20484 | 501.6983 | 30.04 | 55.64
2021-01-15 18:00 | 3.1634 | 0.62469 | 0.24833 | 1.208 | 58.8518 | 51.3929 | 1.2509 | 0.26336 | 501.2795 | 29.99 | 55.75
2021-01-15 18:05 | 4.6873 | 0.79765 | 0.27778 | 1.5004 | 50.4689 | 40.9919 | 1.2655 | 0.35845 | 501.9096 | 29.93 | 55.86
2021-01-15 18:10 | 3.663 | 0.82516 | 0.29464 | 1.5616 | 56.8659 | 40.4107 | 1.2583 | 0.29263 | 503.4464 | 29.91 | 56.08
2021-01-15 18:15 | 3.2533 | 0.80461 | 0.28413 | 1.5154 | 69.8717 | 64.4103 | 1.2511 | 0.35117 | 501.9332 | 29.88 | 56.29
2021-01-15 18:20 | 2.6638 | 0.72763 | 0.21675 | 1.3321 | 71.2877 | 51.2886 | 1.2436 | 0.32919 | 502.5544 | 29.85 | 56.12
2021-01-15 18:25 | 3.3033 | 0.7398 | 0.22511 | 1.3591 | 53.3958 | 18.7546 | 1.2506 | 0.33642 | 500.7296 | 29.79 | 55.73
2021-01-15 18:30 | 3.342 | 0.65887 | 0.23145 | 1.2414 | 38.9976 | 56.9855 | 1.2653 | 0.24136 | 502.2442 | 29.78 | 55.95
2021-01-15 18:35 | 2.9576 | 0.61488 | 0.21459 | 1.1571 | 114.9632 | 303.9497 | 1.2725 | 0.28522 | 427.9848 | 29.72 | 55.91
2021-01-15 18:40 | 4.7388 | 0.65765 | 0.21256 | 1.2206 | 280.8235 | 294.7171 | 1.2876 | 0.54868 | 344.7814 | 29.68 | 56.81
2021-01-15 18:45 | 4.7401 | 0.81302 | 0.25051 | 1.4967 | 204.199 | 136.3001 | 1.266 | 0.49029 | 344.1611 | 29.69 | 57.42
2021-01-15 18:50 | 5.035 | 0.85976 | 0.25263 | 1.5726 | 130.547 | 78.1827 | 1.266 | 0.57081 | 346.7419 | 29.66 | 57.64
2021-01-15 18:55 | 3.5994 | 0.70443 | 0.23995 | 1.3218 | 88.2096 | 74.4576 | 1.2658 | 0.54875 | 347.1624 | 29.66 | 57.24
2021-01-15 19:00 | 3.3416 | 0.60801 | 0.25877 | 1.1907 | 54.8582 | 35.2133 | 1.2578 | 0.35103 | 346.8417 | 29.64 | 56.17
2021-01-15 19:05 | 4.0205 | 0.60669 | 0.24406 | 1.174 | 34.0997 | 35.5133 | 1.2653 | 0.29255 | 345.2939 | 29.62 | 56.43
2021-01-15 19:10 | 2.2797 | 0.64939 | 0.21676 | 1.2122 | 24.1388 | 23.5548 | 1.2436 | 0.19752 | 346.3077 | 29.56 | 57.18
2021-01-15 19:15 | 2.7026 | 0.72499 | 0.18521 | 1.2986 | 21.2111 | 43.2317 | 1.2365 | 0.30728 | 346.3122 | 29.52 | 57.59
2021-01-15 19:20 | 3.4459 | 0.67427 | 0.18103 | 1.2146 | 24.6877 | 45.0508 | 1.2439 | 0.33659 | 346.305 | 29.49 | 57.97
2021-01-15 19:25 | 3.2279 | 0.63987 | 0.19153 | 1.1724 | 23.2713 | 35.8036 | 1.2438 | 0.24144 | 346.4062 | 29.43 | 57.95
2021-01-15 19:30 | 3.0229 | 0.66047 | 0.20627 | 1.2187 | 19.0699 | 27.5033 | 1.2365 | 0.25608 | 346.9561 | 29.4 | 58.04
2021-01-15 19:35 | 2.626 | 0.63031 | 0.19997 | 1.1661 | 17.1551 | 41.2174 | 1.2366 | 0.24146 | 345.4191 | 29.37 | 58.34
2021-01-15 19:40 | 2.2033 | 0.59047 | 0.20628 | 1.1114 | 21.3254 | 32.4544 | 1.2439 | 0.21219 | 346.4919 | 29.34 | 58.37
2021-01-15 19:45 | 2.1781 | 0.63867 | 0.19369 | 1.1727 | 20.8381 | 34.3065 | 1.2441 | 0.18296 | 345.4221 | 29.31 | 58.99
2021-01-15 19:50 | 1.7682 | 0.72797 | 0.20633 | 1.3222 | 25.8305 | 37.6387 | 1.2442 | 0.15369 | 346.9901 | 29.28 | 59.15
2021-01-15 19:55 | 1.2942 | 0.51374 | 0.16423 | 0.95381 | 28.4054 |  | 1.2443 | 0.13175 | 346.9985 | 29.25 | 59.43
2021-01-15 20:00 | 1.4221 | 0.47521 | 0.17263 | 0.90316 | 13.9189 | 31.6405 | 1.2441 | 0.13173 | 346.1077 | 29.17 | 59.39
2021-01-15 20:05 | 1.7296 | 0.42165 | 0.1579 | 0.80422 | 16.543 | 23.2155 | 1.2514 | 0.14637 | 346.6767 | 29.12 | 59.58
2021-01-15 20:10 | 2.0116 | 0.39695 | 0.13475 | 0.74321 | 8.2002 | 9.3893 | 1.2588 | 0.17565 | 347.2271 | 29.07 | 59.9
2021-01-15 20:15 | 2.6653 | 0.5742 | 0.17056 | 1.0507 | 12.3631 | 20.7179 | 1.2663 | 0.25618 | 347.2152 | 29.05 | 60.21
2021-01-15 20:20 | 5.1899 | 0.73768 | 0.17056 | 1.2992 | 11.6868 | 38.1461 | 1.3029 | 0.51237 | 345.6755 | 29.04 | 60.3
2021-01-15 20:25 | 6.0226 | 0.70744 | 0.1874 | 1.2718 | 25.1873 | 37.9399 | 1.2882 | 0.85637 | 345.6977 | 29.03 | 60.26
2021-01-15 20:30 | 5.5101 | 0.6264 | 0.17687 | 1.137 | 30.3646 | 39.9804 | 1.2955 | 0.84906 | 348.2885 | 29.01 | 60.36
2021-01-15 20:35 | 3.6645 | 0.48487 | 0.13685 | 0.88218 | 24.0886 | 44.364 | 1.2881 | 0.63674 | 345.8272 | 28.94 | 60.39
2021-01-15 20:40 | 3.4599 | 0.52614 | 0.16424 | 0.97072 | 18.7195 | 9.5955 | 1.2883 | 0.49042 | 346.3705 | 28.88 | 60.88
2021-01-15 20:45 | 2.1527 | 0.36676 | 0.13054 | 0.69272 | 9.6973 | 14.5563 | 1.2808 | 0.27081 | 348.0329 | 28.8 | 60.98
2021-01-15 20:50 | 2.1782 | 0.30905 | 0.12843 | 0.60216 | 15.9702 | 26.4461 | 1.2881 | 0.30007 | 346.6071 | 28.71 | 61.19
2021-01-15 20:55 | 1.8963 | 0.27195 | 0.11579 | 0.53266 | 12.4333 | 16.1541 | 1.2881 | 0.1976 | 346.242 | 28.59 | 61.53
2021-01-15 21:00 | 1.9473 | 0.28565 | 0.11789 | 0.55575 | 9.2034 | 24.0641 | 1.2952 | 0.18294 | 347.3967 | 28.52 | 61.47
2021-01-15 21:05 | 1.4595 | 0.3088 | 0.14305 | 0.61639 | 15.0251 | 31.1051 | 1.2944 | 0.16088 | 347.6704 | 28.48 | 59.99
2021-01-15 21:10 | 1.367 | 0.22323 | 0.12176 | 0.46394 | 15.7496 | 15.3101 | 1.2916 | 0.13865 | 347.8424 | 28.38 | 55.1
2021-01-15 21:15 | 1.4932 | 0.28046 | 0.11534 | 0.54524 | 14.3446 | 32.8547 | 1.2976 | 0.11664 | 348.7367 | 28.37 | 52.51
2021-01-15 21:20 | 1.1489 | 0.28738 | 0.11957 | 0.56007 | 7.3938 | 24.898 | 1.276 | 0.12396 | 348.1109 | 28.38 | 53.17
2021-01-15 21:25 | 1.1871 | 0.26 | 0.10488 | 0.50551 | 17.585 | 3.7069 | 1.2833 | 0.15312 | 347.6329 | 28.36 | 53.11
2021-01-15 21:30 | 1.5951 | 0.26539 | 0.11113 | 0.51793 | 6.0436 | 17.4672 | 1.2975 | 0.18223 | 347.246 | 28.34 | 52.39
2021-01-15 21:35 | 1.3526 | 0.27905 | 0.10903 | 0.53677 | 10.3306 | 24.7036 | 1.3119 | 0.14577 | 348.8012 | 28.36 | 52.16
2021-01-15 21:40 | 1.2121 | 0.21611 | 0.11531 | 0.44657 | 14.4126 | 7.9412 | 1.3191 | 0.13118 | 347.7952 | 28.36 | 51.94
2021-01-15 21:45 | 1.544 | 0.20928 | 0.10064 | 0.42144 | 11.7391 | 15.0669 | 1.3265 | 0.14577 | 348.8184 | 28.35 | 52.15
2021-01-15 21:50 | 1.4679 | 0.23399 | 0.11536 | 0.47403 | 24.7634 | 34.0458 | 1.327 | 0.13853 | 349.1852 | 28.37 | 53.01
2021-01-15 21:55 | 1.4689 | 0.22456 | 0.13013 | 0.47433 | 26.1689 | 6.6623 | 1.3205 | 0.13132 | 348.4207 | 28.39 | 54.55
2021-01-15 22:00 | 1.3669 | 0.24924 | 0.11755 | 0.4996 | 33.6745 | 27.8083 | 1.3281 | 0.16053 | 350.3295 | 28.34 | 55.17
2021-01-15 22:05 | 1.1855 | 0.20907 | 0.11939 | 0.43986 | 37.568 | 32.9383 | 1.3252 | 0.13106 | 350.1376 | 28.27 | 49.89
2021-01-15 22:10 | 0.97778 | 0.18513 | 0.12102 | 0.4048 | 20.6222 | 9.4984 | 1.3201 | 0.1088 | 351.0608 | 28.18 | 40.44
2021-01-15 22:15 | 1.0251 | 0.21571 | 0.12893 | 0.46166 | -2.5817 | 10.6003 | 1.3156 | 0.1012 | 352.8207 | 28.14 | 31.88
2021-01-15 22:20 | 0.9982 | 0.18963 | 0.11627 | 0.40695 | -7.7127 | 4.7712 | 1.3063 | 0.093826 | 352.8555 | 28.14 | 27.82
2021-01-15 22:25 | 0.70697 | 0.19623 | 0.12032 | 0.42111 | -12.7861 | -16.0785 | 1.2908 | 0.072111 | 353.2103 | 28.1 | 25.64
2021-01-15 22:30 | 0.87036 | 0.28396 | 0.11193 | 0.5472 | -5.762 | 2.8558 | 1.2897 | 0.064846 | 354.0428 | 28.09 | 23.5
2021-01-15 22:35 | 0.9836 | 0.30821 | 0.10361 | 0.57812 | 0.020176 | -3.1677 | 1.2821 | 0.064827 | 353.6325 | 28.08 | 22.76
2021-01-15 22:40 | 0.66822 | 0.27978 | 0.11602 | 0.54487 | 3.621 | -16.6627 | 1.2675 | 0.064815 | 353.7549 | 28.03 | 22.36
2021-01-15 22:45 | 0.63036 | 0.24732 | 0.10358 | 0.48269 | -1.1699 | -8.7948 | 1.2674 | 0.05761 | 353.3806 | 27.92 | 22.34
2021-01-15 22:50 | 0.75643 | 0.3676 | 0.10772 | 0.6712 | 14.594 | 2.6122 | 1.2674 | 0.31685 | 353.4292 | 27.88 | 22.38
2021-01-15 22:55 | 0.81941 | 0.57299 | 0.10772 | 0.98602 | 17.5883 | -11.265 | 1.2385 | 0.12241 | 354.0133 | 27.85 | 22.25
2021-01-15 23:00 | 0.40339 | 0.38378 | 0.091141 | 0.67942 | 16.9523 | -4.3969 | 1.2097 | 0.10801 | 354.6002 | 27.81 | 22.2
2021-01-15 23:05 | 0.49162 | 0.44459 | 0.084926 | 0.7664 | 14.8746 | -6.202 | 1.2025 | 0.086404 | 354.7234 | 27.71 | 22.29
2021-01-15 23:10 | 0.63027 | 0.57025 | 0.080782 | 0.95488 | 22.2259 | -8.0977 | 1.2024 | 0.057602 | 354.2621 | 27.66 | 22.31
2021-01-15 23:15 | 0.40334 | 0.53101 | 0.076632 | 0.89059 | 31.2284 | -4.1342 | 1.1951 | 0.035998 | 354.6758 | 27.64 | 22.12
2021-01-15 23:20 | 0.47894 | 0.39182 | 0.072486 | 0.67309 | 28.6154 | 5.7372 | 1.1951 | 0.021598 | 354.177 | 27.63 | 22.01
2021-01-15 23:25 | 0.55458 | 0.30942 | 0.080773 | 0.55506 | 21.6489 | -0.20167 | 1.1879 | 0.021598 | 355.2774 | 27.58 | 22.17
2021-01-15 23:30 | 0.44111 | 0.21482 | 0.072483 | 0.40383 | 23.5426 | 0.77635 | 1.1878 | 0.021597 | 354.827 | 27.54 | 22
2021-01-15 23:35 | 0.4789 | 0.23102 | 0.068339 | 0.42246 | 21.1524 | 1.593 | 1.1806 | 0.035993 | 356.467 | 27.5 | 21.97
2021-01-15 23:40 | 0.39067 | 0.17968 | 0.060053 | 0.3334 | 9.4466 |  | 1.1877 | 0.079182 | 355.4988 | 27.44 | 21.93
2021-01-15 23:45 | 0.45364 | 0.18642 | 0.074542 | 0.36029 | 14.2544 | -10.1313 | 1.2092 | 0.23033 | 355.06 | 27.39 | 21.77
2021-01-15 23:50 |  | 0.19181 | 0.074539 | 0.36856 | 21.4009 | 19.1731 | 1.2524 | 0.12955 | 356.1759 | 27.35 | 21.72
2021-01-15 23:55 | 0.42842 | 0.17695 | 0.064186 | 0.33749 | 16.5319 | -8.266 | 1.2739 | 0.093567 | 356.1908 | 27.34 | 21.71
2021-01-16 | 0.126 | 0.17154 | 0.049689 | 0.31263 | 17.3774 | 10.8861 | 1.2882 | 0.057575 | 357.3067 | 27.31 | 21.56
2021-01-16 00:05 | 0.12599 | 0.19179 | 0.060039 | 0.35402 | 23.6059 | -0.51405 | 1.2882 | 0.057573 | 357.8831 | 27.28 | 21.5
2021-01-16 00:10 | 0.21418 | 0.24176 | 0.068319 | 0.4389 | 17.3967 | 2.7819 | 1.2954 | 0.093555 | 356.6649 | 27.28 | 21.48
2021-01-16 00:15 | 0.12599 | 0.20529 | 0.053827 | 0.36851 | 15.7741 | -1.8143 | 1.2954 | 0.050376 | 357.8022 | 27.21 | 21.59
2021-01-16 00:20 | 0.39058 | 0.25122 | 0.07039 | 0.4534 | 17.0341 | 5.1405 | 1.2954 | 0.050377 | 356.7902 | 27.17 | 21.66
2021-01-16 00:25 | 0.28978 | 0.22961 | 0.066249 | 0.41613 | 10.8554 | -3.8402 | 1.3026 | 0.035983 | 356.3118 | 27.13 | 21.69
2021-01-16 00:30 | 0.20155 | 0.17015 | 0.062098 | 0.32084 | 12.7381 | -2.8721 | 1.3024 | 0.035977 | 355.8782 | 27.1 | 21.27
2021-01-16 00:35 | 0.11335 | 0.14581 | 0.062085 | 0.28559 | 8.7254 | 2.67 | 1.2949 | 0.03597 | 355.542 | 27 | 20.82
2021-01-16 00:40 | 0.05037 | 0.10394 | 0.055868 | 0.21519 | 0.20148 | -6.1652 | 1.3019 | 0.028771 | 355.728 | 26.89 | 20.52
2021-01-16 00:45 | 0.050365 | 0.12148 | 0.049656 | 0.2338 | 3.2234 | -6.1446 | 1.3018 | 0.028769 | 356.923 | 26.8 | 20.4
2021-01-16 00:50 | 0.050364 | 0.15792 | 0.064138 | 0.30621 | 1.1181 | 0.090655 |  |  | 356.9442 | 26.79 | 20.34
2021-01-16 00:55 | 0.088131 | 0.12417 | 0.047583 | 0.23998 | 13.9902 | -3.0922 | 1.3017 | 0.014383 | 358.063 | 26.76 | 20.19
2021-01-16 01:00 | 0.13848 | 0.1687 | 0.045512 | 0.3041 | 7.7753 | -8.6717 | 1.3016 | 0.014382 | 357.6241 | 26.7 | 20.11
2021-01-16 01:05 |  |  |  |  | -1.9033 | -3.3333 |  |  | 359.3142 | 26.65 | 19.85
2021-01-16 01:10 |  |  |  |  | 14.9112 | -5.0342 |  |  | 357.8355 | 26.62 | 19.29
2021-01-16 01:15 |  |  |  |  | 5.8391 | -0.090606 |  |  | 356.8577 | 26.58 | 19.06
2021-01-16 01:20 |  |  |  |  | 6.4328 | -5.5771 |  |  | 357.9333 | 26.58 | 18.94
2021-01-16 01:25 |  |  |  |  | 6.0994 | -16.2449 |  |  | 356.4105 | 26.58 | 18.4
2021-01-16 01:30 |  |  |  |  | -5.4546 | 1.5699 |  |  | 358.1302 | 26.51 | 18.12
2021-01-16 01:35 |  |  |  |  | 1.2881 | 5.4544 |  |  | 357.1511 | 26.45 | 18.1
2021-01-16 01:40 |  |  |  |  | 2.9381 | -17.8703 |  |  | 358.3083 | 26.41 | 17.76
2021-01-16 01:45 |  |  |  |  | 4.8799 | 2.8676 |  |  | 357.8202 | 26.39 | 17.63
2021-01-16 01:50 |  |  |  |  | 10.2525 | -3.7026 |  |  | 358.3251 | 26.42 | 17.52
2021-01-16 01:55 |  |  |  |  | 1.2174 | 2.8975 |  |  | 357.8596 | 26.38 | 17.42
2021-01-16 02:00 |  |  |  |  | 0.27162 | -13.1786 |  |  | 358.5046 | 26.31 | 17.25
2021-01-16 02:05 |  |  |  |  | 16.2343 | 5.4919 |  |  | 357.5579 | 26.26 | 16.85
2021-01-16 02:10 | 0 | 0.084908 | 0.053713 | 0.18386 | 3.0676 | -11.0736 | 1.3285 | -0.028725 | 358.1354 | 26.24 | 16.69
2021-01-16 02:15 | -0.050289 | 0.074126 | 0.045449 | 0.16114 | -9.6052 | -1.9311 | 1.3213 | -0.014362 | 357.6757 | 26.18 | 16.75
2021-01-16 02:20 | -0.050292 | 0.070086 | 0.047518 | 0.15701 | 11.4363 | -0.94548 | 1.3142 | -0.0071816 | 357.7276 | 26.12 | 16.97
2021-01-16 02:25 | -0.088013 | 0.070089 | 0.049585 | 0.15702 | 6.7393 | 12.1408 | 1.3143 | 0 | 357.7884 | 26.06 | 17.12
2021-01-16 02:30 | -0.088014 | 0.060654 | 0.04752 | 0.13843 | 3.4401 | -9.8475 | 1.3143 | -0.007182 | 358.3511 | 26.03 | 17.19
2021-01-16 02:35 | -0.012573 | 0.052566 | 0.051651 | 0.13223 | 12.5733 | -3.1584 | 1.3071 | 0 | 358.2222 | 26 | 17.19
2021-01-16 02:40 | 0.037718 | 0.19947 | 0.055781 | 0.36154 | 5.3107 | -11.7581 | 1.307 | -0.0071816 | 359.2762 | 26.02 | 17.06
2021-01-16 02:45 | 0 | 0.13343 | 0.057847 | 0.26031 | 2.072 | -8.1573 | 1.3071 | 0 | 358.379 | 26.02 | 17.07
2021-01-16 02:50 | 0.1886 | 0.19814 | 0.066114 | 0.36776 | 12.2917 | 5.5222 | 1.3071 | 0.014364 | 358.2066 | 26.01 | 17.21
2021-01-16 02:55 | 0.25145 | 0.23721 | 0.06611 | 0.42972 | -2.4844 | -13.5785 | 1.307 | 0.028726 | 359.2318 | 26.06 | 16.99
2021-01-16 03:00 | [9 empty] | 26.04 | 16.97
2021-01-16 03:05 | 0.44006 | 0.2453 | 0.086772 | 0.46278 | 13.7498 | -0.010058 | 1.3071 | 0.028727 | 359.7783 | 26.04 | 17.09
2021-01-16 03:10 | 0.40236 | 0.21701 | 0.06405 | 0.3967 | 3.581 | 4.9692 | 1.3072 | 0.057457 | 358.7494 | 25.99 | 17.34
2021-01-16 03:15 | 0.22634 | 0.1658 | 0.068186 | 0.32233 | 4.3759 | -8.6915 | 1.3072 | 0.043095 | 359.3369 | 25.93 | 17.54
2021-01-16 03:20 | 0.2012 | 0.18064 | 0.070255 | 0.34714 | 16.3476 | 5.533 | 1.3073 | 0.079012 | 358.8586 | 25.87 | 17.75
2021-01-16 03:25 | 0.12576 | 0.12942 | 0.05786 | 0.2583 | 6.2375 | -3.652 | 1.3073 | 0.057466 | 358.3575 | 25.83 | 17.93
2021-01-16 03:30 | 0.25152 | 0.13751 | 0.057862 | 0.26864 | 16.0671 | 17.1637 | 1.3146 | 0.057467 | 357.8273 | 25.82 | 18.02
2021-01-16 03:35 | 0.37729 | 0.14291 | 0.082661 | 0.30171 | 23.4723 | 9.9 | 1.3074 | 0.028734 | 358.8729 | 25.83 | 18.07
2021-01-16 03:40 | 0.36472 | 0.19279 | 0.084729 | 0.38025 | 8.6325 | 1.7607 | 1.3074 | 0.028735 | 359.9184 | 25.84 | 18.12
2021-01-16 03:45 | 0.2138 | 0.2602 | 0.082661 | 0.48357 | 25.4342 | 25.0016 | 1.3074 | 0.021551 | 357.796 | 25.84 | 18.06
2021-01-16 03:50 | 0.22637 | 0.3276 | 0.088858 | 0.59101 | 26.0371 | 16.1676 | 1.3074 | 0.02155 | 359.3801 | 25.86 | 17.95
2021-01-16 03:55 | 0.40242 | 0.30467 | 0.10332 | 0.5724 | 15.1411 | 7.7969 | 1.3145 | 0.028733 | 359.2043 | 25.87 | 17.9
2021-01-16 04:00 | 0.22637 | 0.24132 | 0.10333 | 0.47323 | 15.4234 | 8.5417 | 1.3074 | 0.021551 | 359.7457 | 25.85 | 18.05
2021-01-16 04:05 | 0.13834 | 0.25886 | 0.095064 | 0.48979 | 19.4688 | 6.4292 | 1.3075 | 0.021551 | 358.2156 | 25.78 | 18.25
2021-01-16 04:10 | 0.30184 | 0.2993 | 0.10126 | 0.56004 | 10.1921 | 9.528 | 1.3146 | 0.021551 | 358.716 | 25.81 | 18.19
2021-01-16 04:15 | 0.30185 | 0.21572 | 0.093 | 0.42367 | 14.8711 | -1.5897 | 1.3147 | 0.014368 | 359.6972 | 25.87 | 18.23
2021-01-16 04:20 | 0.20121 | 0.25748 | 0.10745 | 0.5042 | 18.8128 | 16.8108 | 1.3145 | 0.0071831 | 359.7313 | 25.88 | 17.84
2021-01-16 04:25 | 0.26403 | 0.28304 | 0.11156 | 0.54541 | 4.5362 | 8.0868 | 1.3142 | 0.0071815 | 360.306 | 25.91 | 17.17
2021-01-16 04:30 | 0.49034 | 0.38412 | 0.13016 | 0.71895 | 9.0926 | 9.7666 | 1.3214 | 0.021545 | 358.5965 | 26 | 17.1
2021-01-16 04:35 | 0.60347 | 0.56067 | 0.13841 | 0.99783 | 21.9564 | 9.7461 | 1.307 | 0.021544 | 358.4409 | 26.14 | 16.86
2021-01-16 04:40 | 0.51544 | 0.57815 | 0.17146 | 1.0577 | 14.8647 | -1.6092 | 1.3069 | 0.028724 | 358.9346 | 26.19 | 16.64
2021-01-16 04:45 | 0.76682 | 0.73713 | 0.16319 | 1.291 | 14.2201 | 24.0957 | 1.314 | 0.064624 | 360.5318 | 26.21 | 16.43
2021-01-16 04:50 | 0.96797 | 0.82339 | 0.20863 | 1.4708 | 28.2095 | 16.0608 | 1.314 | 0.078987 | 359.4353 | 26.23 | 16.47
2021-01-16 04:55 | 0.82971 | 0.65765 | 0.2169 | 1.225 | 24.1471 | 1.8907 | 1.3213 | 0.071808 | 358.8703 | 26.25 | 16.52
2021-01-16 05:00 | 1.0686 | 0.69679 | 0.21898 | 1.287 | 19.7435 | 16.0422 | 1.3214 | 0.093357 | 358.2879 | 26.27 | 16.71
2021-01-16 05:05 | 1.1693 | 0.94887 | 0.21693 | 1.6714 | 31.8147 | 43.08 | 1.3286 | 0.10054 | 358.7166 | 26.34 | 16.8
2021-01-16 05:10 | 1.1442 | 0.97856 | 0.27479 | 1.7768 | 35.5376 | 40.4061 | 1.3287 | 0.10055 | 360.2755 | 26.36 | 16.89
2021-01-16 05:15 | 1.2323 | 1.0379 | 0.2934 | 1.8864 | 34.5638 | 20.3299 | 1.3359 | 0.13646 | 358.659 | 26.36 | 17.05
2021-01-16 05:20 | 1.3832 | 1.104 | 0.29961 | 1.9919 | 47.5625 | 36.7583 | 1.336 | 0.13647 | 358.9928 | 26.37 | 17.18
2021-01-16 05:25 | 1.2952 | 1.4464 | 0.28102 | 2.4961 | 56.9889 | 45.1586 | 1.3288 | 0.10056 | 359.4749 | 26.41 | 17.16
2021-01-16 05:30 | 1.5091 | 1.4425 | 0.33476 | 2.5458 | 50.5432 | 68.9034 | 1.3432 | 0.11493 | 358.3671 | 26.43 | 17.29
2021-01-16 05:35 | 2.6033 | 1.6273 | 0.35751 | 2.8518 | 36.5719 |  | 1.3433 | 0.17241 | 410.4814 | 26.46 | 17.46
2021-01-16 05:40 | 3.0059 | 2.0467 | 0.4216 | 3.5588 |  |  | 1.3506 | 0.21552 | 475.2803 | 26.54 | 17.54
2021-01-16 05:45 | 1.9117 | 2.0305 | 0.37407 | 3.4865 | 13.362 | 34.2402 | 1.3434 | 0.15805 | 472.0487 | 26.56 | 17.56
2021-01-16 05:50 | 1.1949 | 1.3659 | 0.33069 | 2.4244 | 62.7789 | 45.3409 | 1.3507 | 0.13651 | 474.2303 | 26.51 | 17.77
2021-01-16 05:55 | 1.6352 | 1.513 | 0.35345 | 2.6746 | 80.816 | 56.1515 | 1.3436 | 0.16525 | 473.166 | 26.49 | 17.98
2021-01-16 06:00 | 1.4215 | 1.3539 | 0.33486 | 2.4081 | 76.2805 | 20.006 | 1.3436 | 0.15089 | 472.0833 | 26.49 | 18.09
2021-01-16 06:05 | 1.0568 | 1.3028 | 0.33076 | 2.3277 | 62.4907 | 29.0261 | 1.3366 | 0.12935 | 473.705 | 26.44 | 18.47
2021-01-16 06:10 | 0.72971 | 0.99129 | 0.27289 | 1.7924 | 57.0882 | 30.4665 | 1.3367 | 0.1078 | 474.7993 | 26.41 | 18.61
2021-01-16 06:15 | 0.88073 | 0.74587 | 0.23155 | 1.3728 | 52.1392 | 7.2874 | 1.3439 | 0.10061 | 473.3022 | 26.33 | 18.86
2021-01-16 06:20 | 1.447 | 0.91184 | 0.24398 | 1.6417 | 36.7418 | 26.7762 | 1.3368 | 0.115 | 473.893 | 26.27 | 19.15
2021-01-16 06:25 | 1.3464 | 1.2275 | 0.29775 | 2.1794 | 49.0755 | 32.6566 | 1.3369 | 0.12219 | 475.4818 | 26.26 | 19.31
2021-01-16 06:30 | 1.4094 | 1.0198 | 0.2626 | 1.8258 | 56.8379 | 22.3888 | 1.3441 | 0.12219 | 473.8297 | 26.29 | 19.32
2021-01-16 06:35 | 1.3718 | 1.0199 | 0.25436 | 1.8177 | 46.383 | 8.6886 | 1.3514 | 0.093451 | 473.7499 | 26.31 | 19.59
2021-01-16 06:40 | 1.7366 | 1.4718 | 0.3412 | 2.5972 | 46.8742 | 23.0143 | 1.3514 | 0.17252 | 471.5796 | 26.35 | 19.41
2021-01-16 06:45 | 1.4597 | 1.67 | 0.33291 | 2.8928 | 46.509 | 36.3817 | 1.3585 | 0.15094 | 472.0456 | 26.41 | 19.17
2021-01-16 06:50 | 1.5982 | 1.3436 | 0.28329 | 2.3449 | 70.8932 | 41.7487 | 1.3585 | 0.15814 | 472.563 | 26.41 | 19.26
2021-01-16 06:55 | 1.9505 | 1.1318 | 0.25228 | 1.9872 | 50.1957 | 28.3294 | 1.3585 | 0.13657 | 473.6688 | 26.38 | 19.33
2021-01-16 07:00 | 1.7115 | 0.96191 | 0.213 | 1.6874 | 46.8358 | 25.6933 | 1.3514 | 0.14377 | 473.6103 | 26.4 | 19.47
2021-01-16 07:05 | 1.7115 | 0.91062 | 0.21093 | 1.6068 | 64.5641 | 29.4581 | 1.337 | 0.13658 | 473.5881 | 26.42 | 19.39
2021-01-16 07:10 | 1.4849 | 0.79593 | 0.19438 | 1.4144 | 47.3875 | 33.283 | 1.3298 | 0.13658 | 473.6782 | 26.37 | 19.38
2021-01-16 07:15 | 1.2208 | 0.89854 | 0.21094 | 1.5883 | 48.5095 | 15.5255 | 1.3299 | 0.12221 | 473.6659 | 26.35 | 19.67
2021-01-16 07:20 | 1.2837 | 0.82296 | 0.19646 | 1.46 | 40.9567 | 27.8079 | 1.3299 | 0.12939 | 472.666 | 26.32 | 19.6
2021-01-16 07:25 | 1.938 | 0.70016 | 0.18611 | 1.2593 | 43.0487 | 25.058 | 1.3298 | 0.13658 | 473.7231 | 26.34 | 19.43
2021-01-16 07:30 | 1.9255 | 0.70152 | 0.17991 | 1.2552 | 41.6303 | 11.1148 | 1.3299 | 0.13658 | 473.6939 | 26.35 | 19.5
2021-01-16 07:35 | 1.8625 | 0.7811 | 0.19438 | 1.3937 | 40.9146 | 30.0617 | 1.3298 | 0.13658 | 472.6249 | 26.36 | 19.42
2021-01-16 07:40 | 1.4851 | 0.95659 | 0.26058 | 1.7269 | 44.2825 | 12.2235 | 1.3228 | 0.15816 | 474.0689 | 26.42 | 19.7
2021-01-16 07:45 | 1.8127 | 1.0849 | 0.25442 | 1.9195 | 37.814 | 32.6378 | 1.3374 | 0.18695 | 473.3708 | 26.48 | 20.06
2021-01-16 07:50 | 1.9635 | 1.0538 | 0.273 | 1.8883 | 50.5673 | 17.178 | 1.3372 | 0.24444 | 472.8133 | 26.53 | 19.68
2021-01-16 07:55 | 2.303 | 1.1116 | 0.2709 | 1.9749 | 45.7984 | 32.6096 | 1.3442 | 0.28754 | 472.2569 | 26.55 | 19.29
2021-01-16 08:00 | 2.3154 | 1.2316 | 0.29362 | 2.1815 | 47.4055 | 26.0936 | 1.3513 | 0.28751 | 472.7796 | 26.58 | 19.03
2021-01-16 08:05 | 2.177 | 1.0481 | 0.24399 | 1.8506 | 39.5528 | 18.1305 | 1.3441 | 0.2372 | 474.3979 | 26.57 | 19.01
2021-01-16 08:10 | 2.441 | 1.1047 | 0.24398 | 1.9373 | 42.8718 | 12.7035 | 1.3296 | 0.20843 | 473.3822 | 26.56 | 18.82
2021-01-16 08:15 | 2.0764 | 1.3436 | 0.28743 | 2.3491 | 35.8195 | 13.2083 | 1.337 | 0.20845 | 473.265 | 26.6 | 19.1
2021-01-16 08:20 | 2.4037 | 1.7511 | 0.36603 | 3.0502 | 36.5065 | 26.6097 | 1.3371 | 0.23722 | 471.5901 | 26.63 | 19.25
2021-01-16 08:25 | 2.001 | 1.8024 | 0.34742 | 3.1102 | 42.175 | 15.7464 | 1.3299 | 0.17253 | 471.1448 | 26.61 | 19.27
2021-01-16 08:30 | 2.1396 | 1.7526 | 0.29988 | 2.9864 | 43.8902 | 35.9258 | 1.3228 | 0.15097 | 472.6217 | 26.66 | 19.45
2021-01-16 08:35 | 1.7113 | 1.1992 | 0.25639 | 2.0925 | 42.0886 | 29.5154 | 1.3225 | 0.12219 | 472.7271 | 26.66 | 18.82
2021-01-16 08:40 | 1.661 | 1.4623 | 0.31843 | 2.5619 | 53.8376 | 37.2373 | 1.3225 | 0.10782 | 471.0316 | 26.68 | 18.88
2021-01-16 08:45 | 1.9508 | 1.3586 | 0.35778 | 2.4404 | 54.3809 | 38.5932 | 1.3228 | 0.1294 | 472.4327 | 26.75 | 19.31
2021-01-16 08:50 | 1.6235 | 1.5394 | 0.31227 | 2.6719 | 52.8888 | 11.4074 | 1.3299 | 0.13659 | 471.9127 | 26.79 | 19.14
2021-01-16 08:55 | 1.8751 | 1.3706 | 0.29984 | 2.4008 | 50.9717 | 37.0886 | 1.3298 | 0.15095 | 469.7343 | 26.81 | 18.91
2021-01-16 09:00 | 2.24 | 1.6782 | 0.38462 | 2.955 | 59.499 | 37.5719 | 1.3298 | 0.3019 | 471.7508 | 26.88 | 18.84
2021-01-16 09:05 | 3.2722 | 1.8484 | 0.29987 | 3.1331 | 55.9099 | 17.6499 | 1.3371 | 0.39539 | 471.5988 | 26.95 | 19.01
2021-01-16 09:10 | 3.6497 | 1.0968 | 0.29779 | 1.9791 | 54.5692 | 44.0279 | 1.3299 | 0.35224 | 471.6379 | 26.97 | 18.89
2021-01-16 09:15 | 3.2346 | 1.078 | 0.31436 | 1.9668 | 40.4061 | 11.9819 | 1.3372 | 0.20848 | 469.4813 | 26.97 | 19.08
2021-01-16 09:20 | 2.4918 | 1.3963 | 0.36809 | 2.5084 | 51.4061 | 26.0051 | 1.3299 | 0.17971 | 471.5755 | 27.02 | 18.74
2021-01-16 09:25 | 3.5489 | 1.4476 | 0.31225 | 2.5311 | 43.9255 | 18.8669 | 1.3298 | 0.22284 | 470.9424 | 27.05 | 18.71
2021-01-16 09:30 | 3.662 | 1.8253 | 0.31225 | 3.1121 | 45.2734 | 23.3163 | 1.3298 | 0.29472 | 471.4224 | 27.09 | 18.6
2021-01-16 09:35 | 2.9827 | 2.1532 | 0.47771 | 3.7782 | 40.8565 | 30.4259 | 1.3299 | 0.33068 | 471.3598 | 27.11 | 18.76
2021-01-16 09:40 | 3.5743 | 1.4719 | 0.33503 | 2.5913 | 32.2896 | 14.3476 | 1.3299 | 0.26599 | 469.8092 | 27.11 | 18.83
2021-01-16 09:45 | 2.6808 | 1.5664 | 0.3309 | 2.732 | 44.433 | 24.8494 | 1.33 | 0.21567 | 470.8465 | 27.12 | 18.87
2021-01-16 09:50 | 3.3851 | 1.639 | 0.41149 | 2.9239 | 47.7687 | 29.7988 | 1.3298 | 0.20845 | 471.4001 | 27.15 | 18.43
2021-01-16 09:55 | 2.7179 | 1.2734 | 0.35357 | 2.3075 | 54.4393 | 49.7383 | 1.3297 | 0.1725 | 469.763 | 27.2 | 18.18
2021-01-16 10:00 | 3.5984 | 1.4688 | 0.38868 | 2.6401 | 64.0661 | 49.4814 | 1.3367 | 0.22997 | 471.3423 | 27.24 | 17.85
2021-01-16 10:05 | 3.8747 | 1.4605 | 0.40724 | 2.646 | 67.5009 | 44.2424 | 1.3438 | 0.35929 | 469.7249 | 27.29 | 17.49
2021-01-16 10:10 | 3.2583 | 1.3095 | 0.37623 | 2.3856 | 69.2624 | 33.4335 | 1.3438 | 0.36648 | 469.6448 | 27.34 | 17.45
2021-01-16 10:15 | 2.8437 | 1.2585 | 0.30393 | 2.2309 | 54.0548 | 34.0434 | 1.3368 | 0.33061 | 470.0765 | 27.35 | 17.92
2021-01-16 10:20 | 3.0073 | 1.3704 | 0.32461 | 2.4253 | 55.4747 | 30.2589 | 1.344 | 0.24437 | 471.164 | 27.33 | 17.97
2021-01-16 10:25 | 3.0323 | 1.3407 | 0.27911 | 2.3363 | 56.7903 | 15.0078 | 1.3296 | 0.24435 | 470.565 | 27.39 | 17.76
2021-01-16 10:30 | 3.0202 | 1.4974 | 0.37221 | 2.6655 | 48.3438 | 14.5374 | 1.3298 | 0.27315 | 470.4027 | 27.44 | 18.19
2021-01-16 10:35 | 3.2712 | 1.4 | 0.37833 | 2.5243 | 45.8567 | 43.8537 | 1.3295 | 0.27309 | 471.556 | 27.45 | 17.56
2021-01-16 10:40 | 3.2086 | 1.2032 | 0.37424 | 2.2186 | 44.8959 | 36.4905 | 1.3369 | 0.25156 | 470.8892 | 27.5 | 17.84
2021-01-16 10:45 | 4.3269 | 1.1947 | 0.3555 | 2.1888 | 48.4308 | 16.4321 | 1.3435 | 0.26583 | 469.4158 | 27.54 | 16.77
2021-01-16 10:50 | 4.3148 | 1.2986 | 0.31419 | 2.3048 | 43.1828 | 15.3067 | 1.3509 | 0.28742 | 469.2715 | 27.6 | 17
2021-01-16 10:55 | 3.4973 | 1.3513 | 0.37416 | 2.4455 | 38.9987 | 24.9189 | 1.3509 | 0.27306 | 469.7268 | 27.63 | 17.13
2021-01-16 11:00 | 3.1569 | 1.1743 | 0.31 | 2.1101 | 45.6804 | 24.9632 | 1.3434 | 0.28018 | 469.278 | 27.65 | 16.47
2021-01-16 11:05 | 3.66 | 1.2108 | 0.36788 | 2.2238 | 51.5774 | 36.6857 | 1.3434 | 0.34484 | 469.2399 | 27.67 | 16.49
2021-01-16 11:10 | 4.4028 | 1.3674 | 0.35967 | 2.4557 | 53.6091 | 19.7348 | 1.3437 | 0.40957 | 470.1722 | 27.7 | 16.92
2021-01-16 11:15 | 4.0631 | 1.1112 | 0.34519 | 2.0505 | 53.5974 | 29.3347 | 1.3436 | 0.42393 | 469.6563 | 27.7 | 16.84
2021-01-16 11:20 | 2.8929 | 0.97485 | 0.30795 | 1.8022 | 46.0048 | 40.4101 | 1.3363 | 0.29456 | 469.1291 | 27.73 | 16.53
2021-01-16 11:25 | 3.798 | 0.99494 | 0.33891 | 1.864 | 48.1314 | 25.1925 | 1.3289 | 0.30171 | 470.2065 | 27.76 | 16.14
2021-01-16 11:30 | 4.6527 | 1.0811 | 0.29342 | 1.9506 | 46.789 | 19.9288 | 1.3432 | 0.33041 | 468.0512 | 27.81 | 15.85
2021-01-16 11:35 | 4.4901 | 1.2728 | 0.30381 | 2.2527 | 54.7465 | 12.5874 | 1.3434 | 0.35921 | 469.4923 | 27.85 | 16.3
2021-01-16 11:40 | 4.591 | 1.4374 | 0.31209 | 2.5174 | 55.1024 | 33.0051 | 1.3435 | 0.40952 | 468.3076 | 27.91 | 16.42
2021-01-16 11:45 | 5.5719 | 1.5951 | 0.28521 | 2.7302 | 64.7803 | 32.3398 | 1.3507 | 0.43825 | 469.8199 | 27.97 | 16.27
2021-01-16 11:50 | 4.6533 | 1.3091 | 0.30379 | 2.3104 | 56.8862 | 32.0953 | 1.3505 | 0.40229 | 467.6671 | 28.02 | 15.98
2021-01-16 11:55 | 3.8601 | 1.1767 | 0.32851 | 2.1322 | 59.0551 | 21.8879 | 1.3358 | 0.24419 | 468.233 | 28.07 | 15.3
2021-01-16 12:00 | 3.7474 | 1.1486 | 0.34715 | 2.1077 | 46.0152 | 27.9472 | 1.336 | 0.23704 | 468.6824 | 28.08 | 15.65
2021-01-16 12:05 | 3.3072 | 1.3992 | 0.42359 | 2.5684 | 55.9726 | 36.4063 | 1.3288 | 0.26576 | 469.7133 | 28.11 | 15.52
2021-01-16 12:10 | 3.9352 | 1.3424 | 0.40078 | 2.4584 | 45.9044 | 11.0537 | 1.3286 | 0.3088 | 469.1613 | 28.18 | 14.98
2021-01-16 12:15 | 3.7717 | 1.1739 | 0.37806 | 2.1754 | 51.869 | 43.4505 | 1.3286 | 0.37343 | 468.5976 | 28.2 | 14.98
2021-01-16 12:20 | 3.5458 | 1.2023 | 0.39463 | 2.2376 | 53.7854 | 10.7329 | 1.3359 | 0.35911 | 469.5477 | 28.24 | 15.2
2021-01-16 12:25 | 3.332 | 1.0851 | 0.29959 | 1.9628 | 53.7449 | 34.8944 | 1.343 | 0.40938 | 470.0327 | 28.27 | 15.16
2021-01-16 12:30 | 3.3825 | 1.1107 | 0.32853 | 2.0332 | 61.9572 | 40.8219 | 1.336 | 0.36631 | 468.9838 | 28.28 | 15.31
2021-01-16 12:35 | 3.7844 | 1.0809 | 0.33675 | 1.9957 | 67.0984 | 28.6056 | 1.3358 | 0.30881 | 469.5305 | 28.31 | 14.93
2021-01-16 12:40 | 3.3456 | 1.0099 | 0.29141 | 1.8373 | 69.9315 | 37.763 | 1.3435 | 0.24427 | 467.6714 | 28.37 | 15.86
2021-01-16 12:45 | 3.5718 | 1.022 | 0.33066 | 1.8972 | 58.7893 | 23.2823 | 1.3362 | 0.2227 | 467.6221 | 28.42 | 15.66
2021-01-16 12:50 | 3.056 | 1.1095 | 0.33684 | 2.0376 | 71.292 | 43.5237 | 1.3361 | 0.30171 | 468.1283 | 28.45 | 15.5
2021-01-16 12:55 | 3.245 | 1.1528 | 0.35135 | 2.1184 | 69.7099 | 14.2278 | 1.3363 | 0.32329 | 469.0872 | 28.48 | 15.75
2021-01-16 13:00 | 3.9621 | 1.2014 | 0.30589 | 2.1495 | 64.6309 | 38.3177 | 1.3363 | 0.33767 | 468.5424 | 28.48 | 15.84
2021-01-16 13:05 | 3.0056 | 1.2794 | 0.3327 | 2.2938 | 75.6863 | 4.5675 | 1.3361 | 0.25142 | 469.6341 | 28.51 | 15.37
2021-01-16 13:10 | 2.9556 | 1.3024 | 0.36166 | 2.3581 | 67.9863 | 18.9863 | 1.3362 | 0.21552 | 467.9896 | 28.52 | 15.6
2021-01-16 13:15 | 3.2442 | 1.3749 | 0.35332 | 2.4629 | 79.7112 | 44.1208 | 1.3359 | 0.43813 | 468.6177 | 28.52 | 15.06
2021-01-16 13:20 | 4.1495 | 1.3507 | 0.32646 | 2.3989 | 98.9149 | 28.408 | 1.3503 | 0.52432 | 468.0417 | 28.55 | 15.04
2021-01-16 13:25 | 4.1876 | 1.2106 | 0.31203 | 2.1677 | 101.761 | 29.8794 | 1.3432 | 0.56028 | 467.3621 | 28.62 | 15.21
2021-01-16 13:30 | 3.8564 | 0.98623 | 0.34169 | 1.8534 | 86.2018 | 25.0036 | 1.3461 | 0.33833 | 467.3186 | 28.68 | 20.55
2021-01-16 13:35 | 3.3027 | 1.05 | 0.34385 | 1.9533 | 101.6418 | 46.0358 | 1.3393 | 0.22321 | 467.2525 | 28.65 | 21.19
2021-01-16 13:40 | 3.2779 | 1.3002 | 0.35011 | 2.343 | 110.158 | 37.1161 | 1.3322 | 0.25925 | 467.6998 | 28.66 | 21.52
2021-01-16 13:45 | 3.2656 | 1.2989 | 0.36672 | 2.3578 | 98.4986 | 31.6426 | 1.3324 | 0.25927 | 468.226 | 28.63 | 21.81
2021-01-16 13:50 | 2.7237 | 0.91515 | 0.35018 | 1.7509 | 87.0586 | 10.8748 | 1.3253 | 0.28811 | 467.2344 | 28.56 | 22.15
2021-01-16 13:55 | 2.6862 | 0.85711 | 0.38751 | 1.7013 | 87.7325 | 18.402 | 1.3254 | 0.25212 | 466.1846 | 28.53 | 22.42
2021-01-16 14:00 | 2.6737 | 1.0897 | 0.44349 | 2.1138 | 88.2322 | 27.524 | 1.3255 | 0.15848 | 466.6675 | 28.54 | 22.56
2021-01-16 14:05 | 2.6109 | 1.0276 | 0.38135 | 1.9565 | 79.7946 | 30.7252 | 1.3256 | 0.1657 | 466.052 | 28.57 | 22.75
2021-01-16 14:10 | 2.5606 | 0.90734 | 0.3192 | 1.7079 | 72.697 | 27.7508 | 1.3185 | 0.16572 | 467.0663 | 28.57 | 22.96
2021-01-16 14:15 | 2.8635 | 0.81273 | 0.30263 | 1.5463 | 60.8026 | 3.9862 | 1.3186 | 0.16573 | 467.5848 | 28.56 | 23.1
2021-01-16 14:20 | 2.9276 | 0.65473 | 0.27578 | 1.2794 | 66.8705 | 37.9781 | 1.3191 | 0.16578 | 467.9191 | 28.58 | 23.94
2021-01-16 14:25 | 3.232 | 0.76197 | 0.3506 | 1.5206 | 73.9325 | 25.0078 | 1.3197 | 0.18029 | 465.0472 | 28.59 | 25.14
2021-01-16 14:30 | 3.2318 | 0.79575 | 0.35472 | 1.5765 | 64.8277 | 17.4113 | 1.3268 | 0.20912 | 466.6896 | 28.57 | 24.99
2021-01-16 14:35 | 3.9884 | 0.9187 | 0.29243 | 1.7006 | 65.5304 | 28.2417 | 1.3265 | 0.21628 | 464.6866 | 28.57 | 24.44
2021-01-16 14:40 | 3.6106 | 1.0015 | 0.35474 | 1.8899 | 64.7694 | 24.7039 | 1.3269 | 0.23797 | 465.59 | 28.59 | 25.05
2021-01-16 14:45 | 2.8164 | 0.97615 | 0.39638 | 1.8947 | 64.2592 | 35.3426 | 1.3202 | 0.22363 | 466.4292 | 28.61 | 26
2021-01-16 14:50 | 2.9557 | 0.98307 | 0.34247 | 1.8514 | 72.4739 | 28.8501 | 1.3204 | 0.2381 | 466.3148 | 28.64 | 26.32
2021-01-16 14:55 | 3.0195 | 1.0144 | 0.32385 | 1.8788 | 71.2442 | 34.3638 | 1.3278 | 0.25257 | 465.687 | 28.65 | 26.77
2021-01-16 15:00 | 2.7547 | 1.0566 | 0.3426 | 1.9622 | 70.5494 | 23.321 | 1.3281 | 0.20931 | 465.6033 | 28.65 | 27.22
2021-01-16 15:05 | 2.6031 | 1.0011 | 0.32807 | 1.8625 | 63.9091 | 26.3238 | 1.3209 | 0.18045 | 465.085 | 28.64 | 27.28
2021-01-16 15:10 | 3.892 | 0.98482 | 0.34676 | 1.8543 | 74.333 | 31.4902 | 1.3281 | 0.38977 | 466.6669 | 28.63 | 27.35
2021-01-16 15:15 | 4.347 | 1.0634 | 0.36961 | 1.9996 | 77.6295 | 59.7259 | 1.3281 | 0.78677 | 467.2181 | 28.61 | 27.41
2021-01-16 15:20 | 4.9665 | 1.0499 | 0.3551 | 1.9644 | 85.2774 | 51.0754 | 1.3354 | 1.2199 | 466.7107 | 28.58 | 27.61
2021-01-16 15:25 | 4.4844 | 0.88563 | 0.36325 | 1.7208 | 73.6102 | 34.2989 | 1.3349 | 0.89472 | 465.8688 | 28.57 | 26.58
2021-01-16 15:30 | 4.3223 | 0.94161 | 0.36135 | 1.8047 | 66.9936 | 24.2354 | 1.3355 | 0.35373 | 465.6243 | 28.58 | 27.8
2021-01-16 15:35 | [9 empty] | 28.6 | 27.99
2021-01-16 15:40 | 2.9324 | 0.8211 | 0.29492 | 1.5515 | 59.557 | 11.4665 | 1.3212 | 0.22381 | 466.6364 | 28.58 | 28.01
2021-01-16 15:45 | 2.528 | 0.84823 | 0.26793 | 1.5681 | 59.3773 | 25.3203 | 1.3285 | 0.23826 | 466.1089 | 28.57 | 28.12
2021-01-16 15:50 | 3.9443 | 0.90122 | 0.27213 | 1.6535 | 54.7952 | 22.1183 | 1.3287 | 0.28162 | 466.575 | 28.56 | 28.54
2021-01-16 15:55 | 3.7799 | 0.8985 | 0.2929 | 1.6702 | 51.6396 | 33.9612 | 1.3359 | 0.28884 | 467.1022 | 28.56 | 28.53
2021-01-16 16:00 | 3.9063 | 0.98252 | 0.30952 | 1.8176 | 51.174 | 39.1896 | 1.3431 | 0.25273 | 465.5296 | 28.56 | 28.51
2021-01-16 16:05 | 4.3237 | 1.0029 | 0.28668 | 1.824 | 49.8519 | 29.8666 | 1.336 | 0.23108 | 466.0291 | 28.56 | 28.65
2021-01-16 16:10 | 4.1836 | 0.86444 | 0.29284 | 1.6158 | 40.2129 | 10.9001 | 1.3284 | 0.2238 | 467.186 | 28.57 | 27.98
2021-01-16 16:15 | 4.0324 | 0.72632 | 0.29703 | 1.4083 | 52.9695 | 35.849 | 1.3285 | 0.24549 | 463.994 | 28.56 | 28.29
2021-01-16 16:20 | 4.0213 | 0.98959 | 0.32415 | 1.841 | 57.0668 | 26.7175 | 1.3291 | 0.30337 | 465.361 | 28.58 | 29.22
2021-01-16 16:25 | 4.0343 | 0.9707 | 0.29509 | 1.783 | 58.6505 | 38.7496 | 1.3364 | 0.3034 | 465.3165 | 28.58 | 29.46
2021-01-16 16:30 | 3.4147 | 0.85006 | 0.29094 | 1.5939 | 62.2027 | 26.5788 | 1.3364 | 0.27451 | 465.8343 | 28.58 | 29.5
2021-01-16 16:35 | 3.5284 | 0.83919 | 0.29925 | 1.5856 | 57.4665 | 26.7401 | 1.3364 | 0.28895 | 463.7743 | 28.56 | 29.48
2021-01-16 16:40 | 4.8295 | 0.87959 | 0.3137 | 1.662 | 60.4323 | 38.7879 | 1.3504 | 0.59939 | 465.4796 | 28.57 | 28.68
2021-01-16 16:45 | 4.615 | 0.9515 | 0.30541 | 1.7639 | 44.5063 | 15.3243 | 1.365 | 0.74388 | 466.9535 | 28.61 | 28.83
2021-01-16 16:50 | 3.6674 | 0.94355 | 0.29092 | 1.7351 | 48.6625 | 38.0903 | 1.3508 | 0.40452 | 465.8007 | 28.62 | 29.28
2021-01-16 16:55 | 2.6929 | 0.95954 | 0.3033 | 1.7741 | 49.9026 | 27.5 | 1.3432 | 0.24553 | 466.4452 | 28.63 | 28.54
2021-01-16 17:00 | 2.4905 | 0.95543 | 0.27421 | 1.7408 | 51.8121 | 27.2866 | 1.3359 | 0.18775 | 465.9533 | 28.62 | 28.46
2021-01-16 17:05 | 2.9846 | 1.1591 | 0.30132 | 2.0781 | 45.8817 | 24.1397 | 1.3364 | 0.19504 | 466.3277 | 28.61 | 29.37
2021-01-16 17:10 | 3.4284 | 1.0782 | 0.30351 | 1.9562 | 47.0414 | 22.2657 | 1.3369 | 0.20956 | 465.1607 | 28.58 | 30.3
2021-01-16 17:15 | 3.2641 | 0.85851 | 0.24947 | 1.5675 | 46.1636 | 22.5808 | 1.3369 | 0.23848 | 464.6398 | 28.56 | 30.48
2021-01-16 17:20 | 3.3781 | 0.79207 | 0.25571 | 1.4698 | 50.5977 | 16.4172 | 1.337 | 0.52033 | 465.7424 | 28.52 | 30.6
2021-01-16 17:25 | 3.1862 | 0.76851 | 0.25555 | 1.4356 | 46.5185 | 25.8436 | 1.3433 | 0.44055 | 468.2278 | 28.47 | 29.03
2021-01-16 17:30 | 3.1609 | 0.78205 | 0.25554 | 1.4543 | 35.8467 | 31.5176 | 1.3433 | 0.33943 | 466.148 | 28.46 | 29.01
2021-01-16 17:35 | 3.4659 | 0.71597 | 0.21201 | 1.3095 | 35.4485 | 18.4984 | 1.3439 | 0.26734 | 466.4726 | 28.45 | 30.2
2021-01-16 17:40 | 3.327 | 0.63466 | 0.24113 | 1.214 | 28.1952 | 39.3376 | 1.344 | 0.23845 | 468.0174 | 28.41 | 30.51
2021-01-16 17:45 | 3.0238 | 0.66594 | 0.26403 | 1.2869 | 39.4339 | 15.8201 | 1.337 | 0.21681 | 465.8985 | 28.38 | 30.9
2021-01-16 17:50 | 3.9858 | 0.7162 | 0.26198 | 1.3598 | 34.7512 | 29.2748 | 1.3299 | 0.20237 | 467.954 | 28.38 | 31.16
2021-01-16 17:55 | 3.5303 | 0.65246 | 0.21832 | 1.2205 | 33.7293 | 39.8839 | 1.3371 | 0.2096 | 468.0092 | 28.34 | 31.27
2021-01-16 18:00 | 3.4538 | 0.67133 | 0.24946 | 1.2785 | 32.4582 | 0.88053 | 1.3441 | 0.22402 | 467.0854 | 28.31 | 30.88
2021-01-16 18:05 | 3.2764 | 0.70381 | 0.27646 | 1.3553 | 19.9467 | 31.514 | 1.344 | 0.20955 | 467.1916 | 28.27 | 30.71
2021-01-16 18:10 | 2.037 | 0.69037 | 0.27859 | 1.3368 | 56.5604 | 154.7921 | 1.337 | 0.18067 | 419.8419 | 28.22 | 31.22
2021-01-16 18:15 | 2.1765 | 0.7461 | 0.27448 | 1.416 | 268.5144 | 289.2473 | 1.3372 | 0.1807 | 317.7747 | 28.17 | 31.74
2021-01-16 18:20 | 3.531 | 0.92121 | 0.23292 | 1.645 | 180.5546 | 73.7689 | 1.3446 | 0.21687 | 316.1455 | 28.18 | 32.05
2021-01-16 18:25 | 3.0505 | 0.83042 | 0.23919 | 1.5121 | 97.3015 | 30.8542 | 1.3303 | 0.19521 | 317.1349 | 28.2 | 32.35
2021-01-16 18:30 | 3.4055 | 0.84143 | 0.22051 | 1.5103 | 43.692 | 32.8348 | 1.3378 | 0.21694 | 316.3318 | 28.21 | 32.84
2021-01-16 18:35 | 2.8612 | 0.78173 | 0.22051 | 1.4188 | 13.4501 | 29.331 | 1.3451 | 0.18079 | 317.3587 | 28.23 | 32.84
2021-01-16 18:40 | 2.9118 | 0.73829 | 0.25795 | 1.3875 | 9.6722 | 24.7324 | 1.3378 | 0.18078 | 318.4058 | 28.24 | 32.78
2021-01-16 18:45 | 3.1512 | 0.72445 | 0.2641 | 1.3746 | 4.4041 | 37.7129 | 1.3373 | 0.20963 | 316.4154 | 28.24 | 31.85
2021-01-16 18:50 | 3.2518 | 0.66599 | 0.23078 | 1.2537 | -8.6749 | 25.4881 | 1.3298 | 0.20237 | 316.5274 | 28.19 | 31.46
2021-01-16 18:55 | 3.2509 | 0.69563 | 0.24735 | 1.3136 | -2.1554 | 27.4338 | 1.3295 | 0.19508 | 319.2848 | 28.16 | 30.77
2021-01-16 19:00 | 2.4544 | 0.53708 | 0.1871 | 1.0103 | -8.9067 | 19.0786 | 1.3297 | 0.15898 | 317.6784 | 28.13 | 31.29
2021-01-16 19:05 | 2.7969 | 0.52504 | 0.20588 | 1.0107 | -10.0031 | 18.3154 | 1.3301 | 0.16627 | 317.627 | 28.08 | 32.23
2021-01-16 19:10 | 4.0239 | 0.56159 | 0.18714 | 1.048 | -12.1478 | 0.1316 | 1.3372 | 0.23129 | 317.7151 | 28.04 | 31.93
2021-01-16 19:15 | 5.162 | 0.68492 | 0.21829 | 1.2682 | -9.8583 | 27.6924 | 1.3369 | 0.24571 | 318.8309 | 28.03 | 31.53
2021-01-16 19:20 | 3.8704 | 0.61287 | 0.19745 | 1.1348 | -15.6739 | 25.9342 | 1.3294 | 0.20229 | 318.2053 | 28.01 | 30.88
2021-01-16 19:25 | 3.6935 | 0.53018 | 0.1829 | 0.99558 | -3.0863 | 13.7923 | 1.3366 | 0.23843 | 318.2472 | 27.96 | 31.06
2021-01-16 19:30 | 3.112 | 0.49227 | 0.18708 | 0.94165 | 0.61733 | 19.9773 | 1.3368 | 0.20955 | 319.8678 | 27.89 | 31.49
2021-01-16 19:35 | 2.5429 | 0.54926 | 0.18917 | 1.0311 | 2.3481 | 21.4057 | 1.3369 | 0.21679 | 317.7981 | 27.83 | 31.78
2021-01-16 19:40 | 3.4413 | 0.53166 | 0.19958 | 1.0166 | -0.53644 | 12.7429 | 1.3369 | 0.24571 | 319.4078 | 27.79 | 31.99
2021-01-16 19:45 | 3.201 | 0.50048 | 0.20582 | 0.97298 | 4.484 | 24.3734 | 1.337 | 0.21681 | 318.8991 | 27.76 | 32.15
2021-01-16 19:50 | 2.9228 | 0.53848 | 0.23909 | 1.0645 | 11.5291 | 30.1437 | 1.3443 | 0.19513 | 318.8895 | 27.76 | 32.23
2021-01-16 19:55 | 2.3661 | 0.54933 | 0.22039 | 1.0624 | 15.5275 | 27.7856 | 1.3443 | 0.19514 | 319.3929 | 27.78 | 32.22
2021-01-16 20:00 | 1.9357 | 0.4964 | 0.20374 | 0.96464 | 11.5689 | 16.2248 | 1.3442 | 0.18067 | 319.4694 | 27.73 | 32.12
2021-01-16 20:05 | 1.7838 | 0.47466 | 0.21204 | 0.93753 | 10.6165 | 25.4027 | 1.3368 | 0.15897 | 317.9869 | 27.66 | 32.02
2021-01-16 20:10 | 2.5427 | 0.45023 | 0.16422 | 0.85435 | 17.6701 | 14.5328 | 1.344 | 0.26013 | 318.6199 | 27.57 | 32.11
2021-01-16 20:15 | 3.6052 | 0.49632 | 0.185 | 0.94578 | 9.3711 | 15.8782 | 1.344 | 0.35406 | 318.1776 | 27.5 | 32.14
2021-01-16 20:20 | 2.593 | 0.51525 | 0.18082 | 0.97062 | 12.2236 | 18.2747 | 1.3366 | 0.24565 | 318.7929 | 27.45 | 31.95
2021-01-16 20:25 | 2.555 | 0.45694 | 0.16835 | 0.86877 | 9.5825 | 15.5222 | 1.3366 | 0.27454 | 318.6189 | 27.42 | 32.01
2021-01-16 20:30 | 2.3272 | 0.42981 | 0.16626 | 0.82717 | 5.5044 | 7.3864 | 1.3365 | 0.20951 | 319.7219 | 27.39 | 31.96
2021-01-16 20:35 | 1.7707 | 0.42032 | 0.15587 | 0.80015 | 8.3072 | 0.80947 | 1.3293 | 0.15172 | 319.1914 | 27.39 | 31.97
2021-01-16 20:40 | 1.7834 | 0.55728 | 0.19329 | 1.0475 | 1.5482 | 18.3553 | 1.3366 | 0.14449 | 320.2091 | 27.42 | 31.99
2021-01-16 20:45 | 2.4412 | 0.46916 | 0.15381 | 0.87295 | 2.894 | 4.9381 | 1.3366 | 0.13727 | 320.1762 | 27.44 | 32.05
2021-01-16 20:50 | 2.7575 | 0.49223 | 0.14757 | 0.90208 | 1.8316 | 7.7616 | 1.3367 | 0.1445 | 320.7485 | 27.39 | 32.23
2021-01-16 20:55 | 3.2004 | 0.53157 | 0.15382 | 0.96862 | 9.7149 | 3.299 | 1.3439 | 0.26012 | 319.7331 | 27.34 | 32.41
2021-01-16 21:00 | 3.1751 | 0.54106 | 0.15382 | 0.98318 | 10.8889 | 16.0297 | 1.3439 | 0.27457 | 319.2656 | 27.28 | 32.54
2021-01-16 21:05 | 3.6559 | 0.58042 | 0.16837 | 1.0581 | 12.63 | 8.5314 | 1.3585 | 0.3902 | 320.2881 | 27.3 | 32.63
2021-01-16 21:10 | 3.1122 | 0.6008 | 0.13305 | 1.054 | 11.8516 | 21.8004 | 1.3585 | 0.38299 | 320.775 | 27.32 | 32.77
2021-01-16 21:15 | 2.2647 | 0.55472 | 0.14553 | 0.99791 | 13.0771 | 20.5063 | 1.3514 | 0.28907 | 319.208 | 27.28 | 33.03
2021-01-16 21:20 | 2.0879 | 0.50597 | 0.14763 | 0.92319 | 19.021 | 20.6002 | 1.3516 | 0.30357 | 321.3137 | 27.25 | 33.46
2021-01-16 21:25 | 1.9108 | 0.56976 | 0.12892 | 1.0023 | 13.758 | 6.7727 | 1.3517 | 0.28913 | 319.2387 | 27.19 | 33.76
2021-01-16 21:30 | 1.5945 | 0.46803 | 0.12477 | 0.84219 | 11.0048 | 11.3794 | 1.3445 | 0.18071 | 320.3178 | 27.16 | 33.92
2021-01-16 21:35 | 1.4807 | 0.43685 | 0.13101 | 0.80063 | 14.64 | 17.3432 | 1.3446 | 0.17349 | 320.3346 | 27.13 | 34.11
2021-01-16 21:40 | 1.9617 | 0.40973 | 0.13102 | 0.75699 | 10.55 | 0.29362 | 1.3518 | 0.18073 | 321.4163 | 27.1 | 34.25
2021-01-16 21:45 | 1.2023 | 0.33782 | 0.12894 | 0.64676 | 6.1254 | 2.9665 | 1.3446 | 0.15181 | 319.8312 | 27.1 | 34.22
2021-01-16 21:50 | 0.83532 | 0.26321 | 0.12478 | 0.52824 | 6.5611 | 16.4634 | 1.3447 | 0.1229 | 319.373 | 27.02 | 34.5
2021-01-16 21:55 | 1.1011 | 0.24287 | 0.099829 | 0.47211 | -0.32401 | 2.015 | 1.3447 | 0.11567 | 320.5065 | 26.94 | 34.76
2021-01-16 22:00 | 1.3164 | 0.28223 | 0.10607 | 0.53869 | -2.4505 | -1.7214 | 1.352 | 0.1446 | 321.0523 | 26.91 | 34.96
2021-01-16 22:05 | 1.1392 | 0.28903 | 0.10608 | 0.54704 | 5.0126 | 7.3519 | 1.3593 | 0.14461 | 320.504 | 26.91 | 35.12
2021-01-16 22:10 | 0.87346 | 0.20762 | 0.099845 | 0.4181 | 6.0357 | 7.17 | 1.3666 | 0.10123 | 319.9904 | 26.88 | 35.32
2021-01-16 22:15 | 0.89882 | 0.23342 | 0.091529 | 0.44932 | 7.2108 | 9.9352 | 1.3667 | 0.094004 | 321.0866 | 26.83 | 35.57
2021-01-16 22:20 | 0.96217 | 0.29722 | 0.10194 | 0.55752 | 10.8675 | 10.513 | 1.3667 | 0.12294 | 319.523 | 26.79 | 35.8
2021-01-16 22:25 | 1.8611 | 0.22123 | 0.1165 | 0.45561 | 2.1067 | 1.5091 | 1.374 | 0.13017 | 320.0619 | 26.77 | 35.95
2021-01-16 22:30 | 1.3547 | 0.21851 | 0.099859 | 0.4348 | 1.3775 | 6.2797 | 1.3668 | 0.11571 | 319.6052 | 26.7 | 36.11
2021-01-16 22:35 | 1.3928 | 0.23481 | 0.085302 | 0.44523 | 6.7359 | 4.3252 | 1.3597 | 0.12295 | 320.7207 | 26.63 | 36.43
2021-01-16 22:40 | 1.7094 | 0.25112 | 0.10611 | 0.49104 | 10.3223 | 5.1054 | 1.3598 | 0.15189 | 320.2113 | 26.59 | 36.71
2021-01-16 22:45 | 1.9628 | 0.24435 | 0.10404 | 0.47858 | 1.2866 | 10.1811 | 1.3526 | 0.15913 | 320.2236 | 26.56 | 36.95
2021-01-16 22:50 | 1.1651 | 0.24164 | 0.099883 | 0.47028 | 2.8772 | 14.548 | 1.3599 | 0.12297 | 320.7718 | 26.53 | 37.14
2021-01-16 22:55 | 0.92444 | 0.24571 | 0.10404 | 0.48068 | 8.4288 | -11.2047 | 1.3526 | 0.1302 | 319.228 | 26.49 | 37.19
2021-01-16 23:00 | 0.88651 | 0.26474 | 0.099889 | 0.50569 | 6.5247 | 14.3565 | 1.3527 | 0.12298 | 320.7831 | 26.5 | 37.39
2021-01-16 23:05 | 0.62054 | 0.2593 | 0.097806 | 0.49735 | 11.0128 | 16.1797 | 1.3527 | 0.072338 | 320.2717 | 26.49 | 37.34
2021-01-16 23:10 | 0.55723 | 0.32718 | 0.099888 | 0.60141 | 10.253 | 8.9562 | 1.3455 | 0.086806 | 319.7599 | 26.47 | 37.41
2021-01-16 23:15 | 0.94983 | 0.3394 | 0.097807 | 0.62014 | 11.6613 | 10.4152 | 1.3527 | 0.09404 | 320.3207 | 26.44 | 37.49
2021-01-16 23:20 | 1.0005 | 0.3272 | 0.099891 | 0.60143 | 12.9282 | 11.2868 | 1.36 | 0.086809 | 321.414 | 26.4 | 37.67
2021-01-16 23:25 | 0.78524 | 0.34621 | 0.10614 | 0.63683 | 8.6326 | 11.0643 | 1.3601 | 0.086812 | 320.3322 | 26.41 | 37.74
2021-01-16 23:30 | 0.81058 | 0.32042 | 0.085328 | 0.57856 | -1.3476 | -0.30397 | 1.3601 | 0.072344 | 319.8728 | 26.34 | 37.93
2021-01-16 23:35 | 0.63328 | 0.24711 | 0.10822 | 0.487 | 8.9875 | 7.1029 | 1.3529 | 0.065111 | 319.9834 | 26.23 | 38.24
2021-01-16 23:40 | 0.608 | 0.26207 | 0.091581 | 0.49121 | 9.343 | 8.4411 | 1.3602 | 0.072352 | 320.0084 | 26.18 | 38.61
2021-01-16 23:45 | 0.59537 | 0.26208 | 0.095749 | 0.49748 | 5.1582 | 10.519 | 1.3675 | 0.086827 | 319.9907 | 26.18 | 38.77
2021-01-16 23:50 |  | 0.17789 | 0.085341 | 0.35802 | 7.2355 | -2.5639 | 1.3748 | 0.072355 | 320.5567 | 26.15 | 38.81
2021-01-16 23:55 | 0.64602 | 0.21048 | 0.079096 | 0.40172 | 4.6007 | 4.1041 | 1.3747 | 0.072355 | 321.2202 | 26.03 | 39.05
2021-01-17 | 0.58266 | 0.24985 | 0.077011 | 0.45998 | 3.8709 | 4.1445 | 1.3819 | 0.086822 | 320.7887 | 25.95 | 39.11
2021-01-17 00:05 | 0.58267 | 0.2417 | 0.077012 | 0.4475 | 6.9414 | 12.7884 | 1.3892 | 0.065117 | 319.7542 | 25.92 | 39.22
2021-01-17 00:10 | 0.60796 | 0.20095 | 0.072844 | 0.38087 | 4.7016 | 12.0376 | 1.4108 | 0.057878 | 321.3817 | 25.91 | 39.03
2021-01-17 00:15 | 0.55725 | 0.13169 | 0.060351 | 0.26222 | 3.7488 | 0.85107 | 1.4107 | 0.057873 | 320.3785 | 25.88 | 38.85
2021-01-17 00:20 | 0.50662 | 0.1222 | 0.056192 | 0.24142 | 1.1956 | -6.586 | 1.3963 | 0.072345 | 322.0528 | 25.79 | 39.21
2021-01-17 00:25 | 0.68393 | 0.16836 | 0.062436 | 0.3205 | 4.438 | -0.060794 | 1.3963 | 0.065111 | 321.021 | 25.76 | 39.29
2021-01-17 00:30 | 0.49395 | 0.14392 | 0.077003 | 0.29761 | -1.5502 | -1.4489 | 1.389 | 0.057876 | 320.5027 | 25.75 | 39.29
2021-01-17 00:35 | 0.44326 | 0.13169 | 0.07908 | 0.27886 | 0.93212 | 17.2543 | 1.3817 | 0.050638 | 321.0738 | 25.73 | 39.17
2021-01-17 00:40 | 0.37992 | 0.14798 | 0.079076 | 0.3059 | 1.4082 | -10.4352 | 1.3816 | 0.05787 | 322.1521 | 25.73 | 39.03
2021-01-17 00:45 | 0.37991 | 0.16155 | 0.070751 | 0.31838 | -5.957 | -0.41537 | 1.3744 | 0.072335 | 321.2041 | 25.63 | 39.19
2021-01-17 00:50 | 0.44319 | 0.1914 | 0.070744 | 0.3662 | -7.1011 | -6.0476 | 1.3815 | 0.079561 | 321.2785 | 25.59 | 38.99
2021-01-17 00:55 | 0.39252 | 0.19953 | 0.091548 | 0.3974 | 6.6451 | -2.7451 | 1.3814 | 0.072326 | 321.3214 | 25.56 | 38.96
2021-01-17 01:00 | 0.35456 | 0.16289 | 0.091553 | 0.34124 | 4.2446 | 5.9768 | 1.3743 | 0.050631 | 321.3143 | 25.55 | 39.15
2021-01-17 01:05 |  |  |  |  | 5.1059 | 0.070916 |  |  | 321.3708 | 25.48 | 39.49
2021-01-17 01:10 |  |  |  |  | 5.4301 | 8.7327 |  |  | 321.4365 | 25.42 | 39.62
2021-01-17 01:15 |  |  |  |  | -2.1679 | 1.3777 |  |  | 320.9981 | 25.35 | 39.61
2021-01-17 01:20 |  |  |  |  | 2.7452 | -3.5455 |  |  | 321.5782 | 25.31 | 39.66
2021-01-17 01:25 |  |  |  |  | 11.8121 | -5.2071 |  |  | 321.5868 | 25.29 | 39.83
2021-01-17 01:30 |  |  |  |  | -2.5936 | 6.7879 |  |  | 322.6162 | 25.3 | 40.04
2021-01-17 01:35 |  |  |  |  | 1.3171 | 11.0032 |  |  | 322.076 | 25.29 | 40.24
2021-01-17 01:40 |  |  |  |  | 7.1837 | 3.2524 |  |  | 321.4995 | 25.32 | 40.28
2021-01-17 01:45 |  |  |  |  | 0.10132 | -0.020264 |  |  | 322.0654 | 25.29 | 40.34
2021-01-17 01:50 |  |  |  |  | 2.685 | 5.8563 |  |  | 322.6132 | 25.28 | 40.32
2021-01-17 01:55 |  |  |  |  | 3.2827 | 5.5523 |  |  | 322.1054 | 25.26 | 40.34
2021-01-17 02:00 |  |  |  |  | 7.6085 | -4.0322 |  |  | 321.6419 | 25.22 | 40.19
2021-01-17 02:05 |  |  |  |  | 2.8368 | -1.3373 |  |  | 323.2423 | 25.21 | 40.29
2021-01-17 02:10 | 0.26593 | 0.10589 | 0.064507 | 0.22473 | 3.8598 | 9.2089 | 1.4177 | -0.028934 | 322.2705 | 25.14 | 40.29
2021-01-17 02:15 | 0.32918 | 0.10044 | 0.05201 | 0.20596 | 7.4445 | 10.1387 | 1.3957 | -0.021695 | 323.4827 | 25.07 | 39.78
2021-01-17 02:20 | 0.20256 | 0.082788 | 0.054089 | 0.18099 | 2.4713 | -4.8615 | 1.3812 | 0.0072316 | 322.5148 | 24.99 | 39.86
2021-01-17 02:25 | 0.22786 | 0.074636 | 0.049922 | 0.16641 | 5.6914 | 8.5067 | 1.3811 | 0.036153 | 322.6071 | 24.94 | 39.61
2021-01-17 02:30 | 0.24048 | 0.13161 | 0.054073 | 0.25581 | 10.1253 | 1.4074 | 1.3808 | 0.028918 | 321.5528 | 24.98 | 38.98
2021-01-17 02:35 | 0.2784 | 0.11666 | 0.058222 | 0.23497 | 3.3205 | 6.9852 | 1.3661 | 0.043369 | 323.1985 | 24.99 | 38.41
2021-01-17 02:40 | 0.25309 | 0.096316 | 0.056143 | 0.20586 | 1.9437 | -1.0124 | 1.3734 | 0.043369 | 322.6631 | 24.99 | 38.43
2021-01-17 02:45 | 0.24051 | 0.09499 | 0.062401 | 0.208 | 3.5039 | 0.18228 | 1.3738 | 0.036153 | 321.5042 | 24.98 | 39.45
2021-01-17 02:50 | 0.24055 | 0.085503 | 0.06033 | 0.19139 | 1.4787 | -0.40513 | 1.3812 | 0.028926 | 322.5656 | 24.94 | 40.01
2021-01-17 02:55 | 0.22791 | 0.080083 | 0.060337 | 0.18309 | 6.736 | 3.4744 | 1.3741 | 0.036162 | 322.0321 | 24.91 | 40.4
2021-01-17 03:00 | [9 empty] | 24.86 | 40.72
2021-01-17 03:05 | 0.21527 | 0.11674 | 0.060344 | 0.24137 | 1.2967 | -5.7237 | 1.3888 | 0.043399 | 323.1587 | 24.82 | 40.98
2021-01-17 03:10 | 0.22794 | 0.16426 | 0.064505 | 0.31628 | 3.4343 | 5.5617 | 1.3888 | 0.050633 | 321.5579 | 24.82 | 40.99
2021-01-17 03:15 | 0.2406 | 0.11403 | 0.049939 | 0.22473 | 7.7397 | 3.1202 | 1.3888 | 0.043399 | 322.6603 | 24.79 | 41.03
2021-01-17 03:20 | 0.35457 | 0.08145 | 0.05202 | 0.17687 | -0.89149 | -3.6166 | 1.396 | 0.050632 | 322.2214 | 24.7 | 41.28
2021-01-17 03:25 | 0.53183 | 0.088233 | 0.054099 | 0.19143 | -3.3531 | 7.3342 | 1.4032 | 0.05063 | 323.313 | 24.69 | 41.17
2021-01-17 03:30 | 0.73449 | 0.088241 | 0.054103 | 0.19144 | 14.1428 | 13.4235 | 1.4105 | 0.072335 | 322.2297 | 24.68 | 41.46
2021-01-17 03:35 | 0.60791 | 0.10997 | 0.052027 | 0.22059 | 21.0639 | 7.0112 | 1.4179 | 0.065107 | 322.1826 | 24.7 | 41.66
2021-01-17 03:40 | 0.48128 | 0.086894 | 0.05411 | 0.18731 | 12.331 | 12.4526 | 1.418 | 0.06511 | 323.7883 | 24.68 | 41.87
2021-01-17 03:45 | 0.41798 | 0.06789 | 0.052032 | 0.1561 | 14.804 | 9.7173 | 1.4253 | 0.072348 | 321.6929 | 24.63 | 42.15
2021-01-17 03:50 | 0.40533 | 0.15751 | 0.11448 | 0.35591 | 18.9796 | 20.9252 | 1.4326 | 0.072352 | 322.1348 | 24.7 | 42.13
2021-01-17 03:55 | 0.39267 | 0.17652 | 0.10615 | 0.37673 | 10.3766 | 11.9979 | 1.4253 | 0.065117 | 323.1332 | 24.76 | 42.01
2021-01-17 04:00 | 0.38 | 0.1643 | 0.087417 | 0.33926 | 15.5342 | 15.0681 | 1.4253 | 0.065116 | 323.1053 | 24.79 | 41.89
2021-01-17 04:05 | 0.418 | 0.1806 | 0.081175 | 0.358 | 20.4695 | 10.6604 | 1.4181 | 0.065117 | 322.0111 | 24.81 | 41.9
2021-01-17 04:10 | 0.40532 | 0.1996 | 0.070765 | 0.37672 | 13.9734 | 19.2628 | 1.4253 | 0.094054 | 322.903 | 24.79 | 41.86
2021-01-17 04:15 | 0.48131 | 0.25391 | 0.093658 | 0.48286 | 10.4571 | 8.8663 | 1.4325 | 0.072349 | 322.9175 | 24.78 | 41.85
2021-01-17 04:20 | 0.58262 | 0.21588 | 0.074924 | 0.40584 | 8.2175 | -4.4989 | 1.4252 | 0.079581 | 322.4805 | 24.7 | 41.95
2021-01-17 04:25 | 0.53196 | 0.21045 | 0.0666 | 0.39127 | 9.4233 | 11.3992 | 1.4325 | 0.079582 | 323.0558 | 24.66 | 42.07
2021-01-17 04:30 | 0.49395 | 0.23081 | 0.081165 | 0.43496 | 2.9282 | 1.226 | 1.4252 | 0.094047 | 324.6815 | 24.65 | 41.97
2021-01-17 04:35 | 0.55727 | 0.21316 | 0.070759 | 0.3975 | -1.4185 | 11.7432 | 1.4252 | 0.086813 | 322.4814 | 24.71 | 41.81
2021-01-17 04:40 | 0.53196 | 0.1928 | 0.068681 | 0.36422 | 9.3321 | 3.3944 | 1.418 | 0.072347 | 322.9051 | 24.8 | 41.71
2021-01-17 04:45 | 0.37996 | 0.17515 | 0.085328 | 0.35172 | 6.4238 | 3.9921 | 1.4179 | 0.06511 | 322.8947 | 24.82 | 41.55
2021-01-17 04:50 | 0.59526 | 0.28104 | 0.10198 | 0.53277 | 7.4471 | 6.1806 | 1.4324 | 0.072343 | 323.3892 | 24.86 | 41.41
2021-01-17 04:55 | 0.48126 | 0.26203 | 0.09573 | 0.49738 | 12.8776 | 7.0416 | 1.4396 | 0.050639 | 322.8206 | 24.9 | 41.23
2021-01-17 05:00 | 0.55726 | 0.25389 | 0.10822 | 0.49738 | 8.8756 | 7.7307 | 1.4324 | 0.079576 | 321.2383 | 24.88 | 41.31
2021-01-17 05:05 | 1.4184 | 0.23215 | 0.08324 | 0.43909 | 5.9371 | 12.5935 | 1.4323 | 0.10851 | 323.3975 | 24.87 | 41.2
2021-01-17 05:10 | 1.6717 | 0.23623 | 0.085322 | 0.44534 | 12.5429 | 23.5965 | 1.4323 | 0.094041 | 322.3383 | 24.86 | 41.25
2021-01-17 05:15 | 1.8237 | 0.30412 | 0.097812 | 0.56398 | 25.2488 | 20.041 | 1.4324 | 0.10128 | 322.8391 | 24.88 | 41.31
2021-01-17 05:20 | 0.96253 | 0.3625 | 0.12278 | 0.67844 | 10.4156 | 9.0985 | 1.4324 | 0.08681 | 322.8289 | 24.89 | 41.28
2021-01-17 05:25 | 1.2285 | 0.36792 | 0.13319 | 0.69715 | 15.2886 | 11.8844 | 1.4396 | 0.086808 | 322.8052 | 24.92 | 41.12
2021-01-17 05:30 | 1.6337 | 0.3747 | 0.15191 | 0.72626 | 19.1483 | 8.7028 | 1.4468 | 0.11574 | 322.2912 | 24.91 | 41.06
2021-01-17 05:35 | 1.5578 | 0.36792 | 0.10613 | 0.6701 | 15.2381 | 11.1449 | 1.4685 | 0.13021 | 322.8021 | 24.92 | 41.15
2021-01-17 05:40 | 1.4184 | 0.36248 | 0.11237 | 0.668 | 12.5833 | 15.8051 | 1.4902 | 0.14468 | 321.7331 | 24.93 | 41.04
2021-01-17 05:45 | 1.4311 | 0.26473 | 0.087402 | 0.49528 | 10.405 | 12.5022 | 1.5191 | 0.14468 | 322.7909 | 24.94 | 41
2021-01-17 05:50 | 1.0005 | 0.21993 | 0.085321 | 0.42244 | 17.3754 | 6.2207 | 1.5408 | 0.10851 | 321.7556 | 24.91 | 41.08
2021-01-17 05:55 | 1.0638 | 0.2308 | 0.11862 | 0.4724 | 12.2087 | 8.3384 | 1.5336 | 0.12298 | 322.7929 | 24.93 | 41.11
2021-01-17 06:00 | 1.2791 | 0.36927 | 0.14359 | 0.70962 | 9.3412 | 7.5175 | 1.5263 | 0.15914 | 322.7479 | 24.98 | 40.9
2021-01-17 06:05 | 1.089 | 0.4534 | 0.1623 | 0.85729 | 18.7313 | 28.3046 | 1.5334 | 0.1519 | 322.1352 | 25.08 | 40.38
2021-01-17 06:10 | 1.089 | 0.44255 | 0.13109 | 0.80945 | 22.6421 | 13.4029 | 1.5407 | 0.1519 | 322.1075 | 25.1 | 40.39
2021-01-17 06:15 | 1.2153 | 0.37863 | 0.11857 | 0.69895 | 11.4037 | 5.1246 | 1.5475 | 0.15185 | 322.5934 | 25.04 | 39.63
2021-01-17 06:20 | 1.1648 | 0.37595 | 0.10402 | 0.68028 | 21.6342 | 25.1792 | 1.5403 | 0.15187 | 323.6365 | 25.04 | 39.87
2021-01-17 06:25 | 1.2152 | 0.49666 | 0.12064 | 0.88194 | 28.426 | 30.9678 | 1.5401 | 0.15907 | 322.0193 | 25.1 | 39.25
2021-01-17 06:30 | 1.3919 | 0.62534 | 0.18713 | 1.1457 | 24.4977 | 20.3371 | 1.554 | 0.22406 | 323.0683 | 25.23 | 37.79
2021-01-17 06:35 | 1.6444 | 0.64138 | 0.18499 | 1.1681 | 21.8679 | 18.9738 | 1.5462 | 0.20231 | 322.0518 | 25.29 | 36.55
2021-01-17 06:40 | 1.884 | 0.64385 | 0.17661 | 1.1635 | 22.2441 | 13.3424 | 1.5528 | 0.18778 | 323.7 | 25.36 | 35.25
2021-01-17 06:45 | 1.8331 | 0.63696 | 0.16411 | 1.1405 | 15.1808 | 19.2667 | 1.5453 | 0.18775 | 323.7245 | 25.39 | 34.65
2021-01-17 06:50 | 2.2116 | 0.64352 | 0.15367 | 1.1422 | 17.8549 | 13.1434 | 1.5593 | 0.21656 | 322.6681 | 25.48 | 33.44
2021-01-17 06:55 | 2.0344 | 0.61092 | 0.19518 | 1.1337 | 19.2876 | -1.5467 | 1.5735 | 0.21653 | 322.128 | 25.53 | 32.89
2021-01-17 07:00 | 2.2869 | 0.55939 | 0.14118 | 1.0007 | 16.3241 | 26.624 | 1.595 | 0.21651 | 323.164 | 25.59 | 32.47
2021-01-17 07:05 | 2.0462 | 0.46308 | 0.13906 | 0.84889 | 19.3001 | 6.7702 | 1.6017 | 0.20201 | 324.2874 | 25.63 | 31.48
2021-01-17 07:10 | 1.7679 | 0.42101 | 0.12035 | 0.76569 | 11.0015 | 20.7099 | 1.6013 | 0.17311 | 323.2719 | 25.65 | 30.75
2021-01-17 07:15 | 1.6287 | 0.47236 | 0.15145 | 0.87343 | 19.1506 | 12.8378 | 1.5938 | 0.18029 | 323.2993 | 25.68 | 30.14
2021-01-17 07:20 | 1.4773 | 0.52382 | 0.1888 | 0.99173 | 23.7778 | 11.1111 | 1.565 | 0.16588 | 323.7421 | 25.75 | 30.16
2021-01-17 07:25 | 1.4898 | 0.6226 | 0.20539 | 1.1618 | 22.8576 | 29.827 | 1.5505 | 0.1803 | 322.6339 | 25.8 | 29.94
2021-01-17 07:30 | 1.8177 | 0.61976 | 0.19083 | 1.1408 | 24.2363 | 25.3471 | 1.543 | 0.17305 | 322.6591 | 25.84 | 29.24
2021-01-17 07:35 | 2.0705 | 0.63744 | 0.1867 | 1.1638 | 34.0363 | 16.9171 | 1.5288 | 0.15144 | 322.5083 | 25.94 | 29.46
2021-01-17 07:40 | 1.8685 | 0.71054 | 0.18878 | 1.2779 | 30.9868 | 18.584 | 1.5 | 0.11538 | 321.3584 | 26.01 | 29.4
2021-01-17 07:45 | 2.411 | 0.75643 | 0.21987 | 1.3793 | 35.5866 | 30.9717 | 1.4709 | 0.23073 | 322.4462 | 26.04 | 28.87
2021-01-17 07:50 | 2.2847 | 0.74154 | 0.19497 | 1.3296 | 38.4239 | 22.0546 | 1.4492 | 0.15862 | 321.8833 | 26.07 | 28.79
2021-01-17 07:55 | 2.5503 | 0.74169 | 0.21369 | 1.3527 | 27.8771 | 10.1105 | 1.4279 | 0.19472 | 321.2281 | 26.12 | 29.32
2021-01-17 08:00 | 4.1531 | 1.1042 | 0.32151 | 2.0162 | 34.2144 | 23.227 | 1.4277 | 0.31005 | 319.627 | 26.17 | 28.75
2021-01-17 08:05 | 3.3454 | 1.2897 | 0.31323 | 2.2901 | 63.5548 | 45.1943 | 1.4278 | 0.23796 | 320.9843 | 26.38 | 28.56
2021-01-17 08:10 | 2.5629 | 1.011 | 0.26969 | 1.8194 | 40.33 | 27.9775 | 1.4207 | 0.18029 | 319.7937 | 26.47 | 28.66
2021-01-17 08:15 | 2.4117 | 1.0084 | 0.27387 | 1.8196 | 39.8289 | 23.9701 | 1.4208 | 0.20194 | 319.9859 | 26.56 | 28.82
2021-01-17 08:20 | 2.6391 | 0.98273 | 0.29671 | 1.8051 | 46.9524 | 37.3963 | 1.4281 | 0.20916 | 319.5872 | 26.62 | 28.82
2021-01-17 08:25 | 3.5856 | 1.1125 | 0.23236 | 1.9377 | 38.3309 | 24.7661 | 1.4351 | 0.29568 | 319.3184 | 26.71 | 28.34
2021-01-17 08:30 | 4.8603 | 1.2748 | 0.21781 | 2.1698 | 41.6292 | 29.6717 | 1.435 | 0.31007 | 320.3444 | 26.78 | 27.92
2021-01-17 08:35 | 5.9213 | 1.3372 | 0.19709 | 2.2468 | 55.0165 | 41.3911 | 1.4495 | 0.3101 | 319.6928 | 26.86 | 28.08
2021-01-17 08:40 | 4.9872 | 1.2831 | 0.25311 | 2.2199 | 49.7758 | 40.5842 | 1.4424 | 0.31732 | 319.588 | 26.95 | 28.01
2021-01-17 08:45 | 4.7471 | 1.233 | 0.2365 | 2.1264 | 55.9349 | 39.815 | 1.4495 | 0.375 | 320.0912 | 26.99 | 27.83
2021-01-17 08:50 | 4.4689 | 1.107 | 0.27382 | 1.9707 | 59.1717 | 30.6614 | 1.4422 | 0.36054 | 319.0229 | 27.02 | 27.53
2021-01-17 08:55 | 4.0023 | 1.0232 | 0.26763 | 1.8381 | 51.7953 | 37.4021 | 1.4279 | 0.38943 | 320.529 | 27.07 | 27.78
2021-01-17 09:00 | 3.5861 | 1.0003 | 0.26559 | 1.7969 | 56.469 | 49.8119 | 1.4137 | 0.28129 | 318.8163 | 27.14 | 28.02
2021-01-17 09:05 | 3.4218 | 1.2169 | 0.34441 | 2.2097 | 58.3749 | 37.2937 | 1.4136 | 0.25964 | 318.76 | 27.21 | 27.75
2021-01-17 09:10 | 3.3583 | 1.4062 | 0.37965 | 2.5352 | 47.3299 | 31.8563 | 1.4135 | 0.22356 | 318.7044 | 27.29 | 27.37
2021-01-17 09:15 | 3.2828 | 1.2439 | 0.31536 | 2.222 | 48.0801 | 31.7975 | 1.4136 | 0.20915 | 318.112 | 27.33 | 27.46
2021-01-17 09:20 | 3.99 | 1.1559 | 0.34026 | 2.1121 | 49.0816 | 23.0105 | 1.4064 | 0.26685 | 319.1235 | 27.37 | 27.48
2021-01-17 09:25 | 5.442 | 1.2371 | 0.32159 | 2.22 | 42.8793 | 27.1114 | 1.4136 | 0.36061 | 319.0614 | 27.43 | 27.37
2021-01-17 09:30 | 4.6722 | 1.1181 | 0.32784 | 2.0397 | 47.4489 | 44.1354 | 1.4137 | 0.31015 | 318.4823 | 27.45 | 27.56
2021-01-17 09:35 | 4.4325 | 1.0207 | 0.31541 | 1.88 | 40.2185 | 24.8524 | 1.4138 | 0.47608 | 318.4509 | 27.46 | 27.72
2021-01-17 09:40 | 5.0149 | 1.0847 | 0.38193 | 2.0445 | 43.2417 | 26.2543 | 1.4142 | 0.50508 | 318.2943 | 27.52 | 28.41
2021-01-17 09:45 | 4.6874 | 1.1133 | 0.36332 | 2.0699 | 53.0453 | 35.003 | 1.4289 | 0.57014 | 317.1009 | 27.58 | 28.88
2021-01-17 09:50 | 4.6763 | 1.1828 | 0.34267 | 2.1578 | 51.7981 | 40.302 | 1.4222 | 0.50534 | 317.5006 | 27.61 | 29.67
2021-01-17 09:55 | 4.5515 | 1.1127 | 0.38434 | 2.0879 | 53.6973 | 31.2636 | 1.4082 | 0.3322 | 317.858 | 27.67 | 30.49
2021-01-17 10:00 | 5.0581 | 1.2431 | 0.44882 | 2.3542 | 56.4077 | 39.2305 | 1.4012 | 0.29614 | 318.2589 | 27.74 | 30.83
2021-01-17 10:05 | 5.2726 | 1.2768 | 0.44878 | 2.406 | 55.5736 | 34.0078 | 1.3939 | 0.39723 | 317.7227 | 27.77 | 30.56
2021-01-17 10:10 | 4.5781 | 1.2378 | 0.44056 | 2.3379 | 51.8721 | 23.3207 | 1.387 | 0.34675 | 317.6142 | 27.81 | 31.04
2021-01-17 10:15 | 4.0731 | 1.2774 | 0.45312 | 2.409 | 56.092 | 55.3026 | 1.3873 | 0.31069 | 318.0611 | 27.83 | 31.52
2021-01-17 10:20 | 4.6309 | 1.4771 | 0.43245 | 2.6966 | 60.2779 | 53.6478 | 1.3876 | 0.3975 | 317.3795 | 27.89 | 32.14
2021-01-17 10:25 | 5.1779 | 1.4711 | 0.39317 | 2.6482 | 71.827 | 47.7834 | 1.3812 | 0.39049 | 317.1497 | 27.94 | 33.51
2021-01-17 10:30 | 5.4734 | 1.3895 | 0.38516 | 2.5129 | 63.4817 | 45.3788 | 1.3895 | 0.39804 | 316.283 | 28.02 | 35.44
2021-01-17 10:35 | 6.7303 | 1.3981 | 0.41654 | 2.5597 | 66.7302 | 48.6915 | 1.3828 | 0.36923 | 316.6288 | 28.08 | 36.3
2021-01-17 10:40 | 6.7032 | 1.52 | 0.52887 | 2.8588 | 69.2065 | 43.2249 | 1.3897 | 0.37637 | 316.1725 | 28.09 | 35.6
2021-01-17 10:45 | 6.3613 | 1.5418 | 0.52264 | 2.886 | 66.9886 | 43.4798 | 1.3897 | 0.3981 | 316.1309 | 28.12 | 35.62
2021-01-17 10:50 | 5.994 | 1.4767 | 0.49143 | 2.7549 | 61.4557 | 43.0352 | 1.3898 | 0.39811 | 318.2025 | 28.15 | 35.65
2021-01-17 10:55 | 5.8669 | 1.3951 | 0.4206 | 2.5611 | 63.7222 | 49.9661 | 1.3897 | 0.45599 | 317.125 | 28.19 | 35.39
2021-01-17 11:00 | 6.6446 | 1.7318 | 0.49174 | 3.1484 | 59.3143 | 43.4789 | 1.3907 | 0.53599 | 316.3077 | 28.25 | 37.1
2021-01-17 11:05 | 7.2042 | 1.72 | 0.42308 | 3.0595 | 62.7066 | 33.4232 | 1.3837 | 0.57958 | 317.2182 | 28.32 | 37.53
2021-01-17 11:10 | 8.3311 | 1.6639 | 0.48133 | 3.0338 | 56.322 | 55.0134 | 1.3907 | 0.51426 | 316.2223 | 28.33 | 36.94
2021-01-17 11:15 | 7.6453 | 1.5155 | 0.42709 | 2.75 | 55.4313 | 38.0665 | 1.3832 | 0.56488 | 317.2826 | 28.37 | 36.48
2021-01-17 11:20 | 6.4389 | 1.5585 | 0.43738 | 2.8284 | 54.7763 | -12.0869 | 1.3756 | 0.45612 | 316.2668 | 28.42 | 35.63
2021-01-17 11:25 | 5.7815 | 1.476 | 0.44792 | 2.7104 | 37.8635 |  | 1.3687 | 0.4128 | 316.6932 | 28.43 | 36.34
2021-01-17 11:30 | 6.9723 | 1.363 | 0.43119 | 2.5205 | 40.6166 | 13.3563 | 1.3685 | 0.38377 | 316.242 | 28.4 | 36.04
2021-01-17 11:35 | 7.0976 | 1.4416 | 0.48734 | 2.697 | 48.0305 | 48.2435 | 1.3683 | 0.37646 | 316.791 | 28.44 | 35.45
2021-01-17 11:40 | 7.6343 | 1.2888 | 0.39593 | 2.3735 | 57.7872 | 55.1798 | 1.3835 | 0.42013 | 314.9754 | 28.49 | 36.79
2021-01-17 11:45 | 8.5706 | 1.3197 | 0.41458 | 2.4375 | 61.0185 | 43.7759 | 1.3977 | 0.47796 | 317.1647 | 28.49 | 36.16
2021-01-17 11:50 | 8.8633 | 1.4504 | 0.4688 | 2.692 | 67.7211 | 70.4904 | 1.4051 | 0.53597 | 316.545 | 28.54 | 36.37
2021-01-17 11:55 | 7.2307 | 1.2892 | 0.39188 | 2.3679 | 62.6454 | 54.5674 | 1.384 | 0.442 | 316.3575 | 28.59 | 37.34
2021-01-17 12:00 | 5.239 | 1.1423 | 0.39604 | 2.147 | 55.1552 | 34.9401 | 1.3767 | 0.31881 | 316.8577 | 28.62 | 37.24
2021-01-17 12:05 | 4.5149 | 1.2222 | 0.39595 | 2.2694 | 44.5905 | 39.6698 | 1.3764 | 0.28252 | 316.9227 | 28.63 | 36.62
2021-01-17 12:10 | 4.199 | 1.1668 | 0.3502 | 2.1387 | 50.2557 | 42.076 | 1.3695 | 0.27535 | 316.813 | 28.65 | 37.28
2021-01-17 12:15 | 4.9615 | 1.2623 | 0.41285 | 2.3478 | 47.1427 | 32.7177 | 1.3771 | 0.31167 | 316.2215 | 28.63 | 38
2021-01-17 12:20 | 5.7094 | 1.3737 | 0.45866 | 2.5643 | 47.4214 | 36.845 | 1.3697 | 0.34062 | 315.7416 | 28.62 | 37.73
2021-01-17 12:25 | 6.4841 | 1.2895 | 0.39616 | 2.3749 | 49.6192 | 43.5893 | 1.3699 | 0.34065 | 316.2348 | 28.62 | 38
2021-01-17 12:30 | 5.9925 | 1.1786 | 0.41098 | 2.2155 | 38.6565 | 36.2799 | 1.3779 | 0.34084 | 315.4841 | 28.67 | 39.25
2021-01-17 12:35 | 5.3844 | 1.1599 | 0.39647 | 2.1764 | 46.7119 | 33.444 | 1.3637 | 0.36268 | 315.3664 | 28.71 | 39.76
2021-01-17 12:40 | 5.9819 | 1.4282 | 0.42156 | 2.6107 | 36.4855 | 32.6348 | 1.3711 | 0.35547 | 316.3961 | 28.7 | 40.05
2021-01-17 12:45 | 6.4652 | 1.4583 | 0.40073 | 2.6361 | 40.2799 | 27.761 | 1.3712 | 0.35551 | 314.445 | 28.72 | 40.25
2021-01-17 12:50 | 5.9578 | 1.2651 | 0.34233 | 2.2815 | 47.8149 | 36.8393 | 1.3641 | 0.40634 | 316.2719 | 28.75 | 40.5
2021-01-17 12:55
2021-01-17 13:00 | 6.3776 | 1.3033 | 0.35489 | 2.3527 | 64.7614 | 40.2472 | 1.3788 | 0.4354 | 315.13 | 28.81 | 40.57
2021-01-17 13:05 | 6.6319 | 1.3783 | 0.30897 | 2.4217 | 60.6885 | 41.3771 | 1.3788 | 0.50799 | 315.1474 | 28.78 | 40.75
2021-01-17 13:10 | 7.5447 | 1.3194 | 0.40699 | 2.4294 | 53.3564 | 37.0477 | 1.3712 | 0.47884 | 314.7048 | 28.78 | 40.09
2021-01-17 13:15 | 7.939 | 1.3494 | 0.41954 | 2.488 | 49.8851 | 40.5259 | 1.3713 | 0.45711 | 314.67 | 28.79 | 40.26
2021-01-17 13:20 | 5.6565 | 1.21 | 0.39059 | 2.2454 | 47.9876 | 37.8694 | 1.365 | 0.4066 | 314.9257 | 28.84 | 41.86
2021-01-17 13:25 | 4.5257 | 1.0303 | 0.36765 | 1.9469 | 50.9422 | 35.4124 | 1.3652 | 0.33403 | 315.9843 | 28.8 | 42.23
2021-01-17 13:30 | 3.2286 | 0.85436 | 0.31121 | 1.6208 | 39.8211 | 28.5134 | 1.3432 | 0.26864 | 315.0464 | 28.73 | 42.08
2021-01-17 13:35 | 3.3938 | 0.85298 | 0.32374 | 1.6291 | 35.3358 | 21.476 | 1.3432 | 0.27589 | 314.7911 | 28.68 | 42.1
2021-01-17 13:40 | 3.1013 | 0.75349 | 0.2924 | 1.4474 | 35.0298 | 27.8917 | 1.3431 | 0.23959 | 314.2841 | 28.67 | 42.06
2021-01-17 13:45 | 2.9734 | 0.80368 | 0.29232 | 1.5242 | 39.3608 | 25.1189 | 1.3428 | 0.21049 | 315.4333 | 28.66 | 41.39
2021-01-17 13:50 | 4.0032 | 0.90324 | 0.32577 | 1.7103 | 39.976 | 31.8425 | 1.3429 | 0.23229 | 315.3916 | 28.66 | 41.72
2021-01-17 13:55 | 4.7907 | 0.96037 | 0.29651 | 1.7686 | 40.2772 | 17.16 | 1.3501 | 0.31937 | 314.8853 | 28.67 | 41.46
2021-01-17 14:00 | 5.3253 | 0.96599 | 0.27567 | 1.7564 | 51.7431 | 46.944 | 1.3648 | 0.34847 | 314.8201 | 28.68 | 41.87
2021-01-17 14:05 | 6.0242 | 0.96597 | 0.28402 | 1.7647 | 48.7528 | 38.7277 | 1.3648 | 0.39202 | 314.8058 | 28.7 | 41.77
2021-01-17 14:10 | 6.1255 | 1.3079 | 0.26103 | 2.2679 | 43.3716 | 32.2695 | 1.3502 | 0.39199 | 315.3296 | 28.72 | 41.57
2021-01-17 14:15 | 5.4646 | 1.7915 | 0.39468 | 3.1407 | 49.3895 | 44.845 | 1.3502 | 0.36295 | 315.8395 | 28.74 | 41.48
2021-01-17 14:20 | 5.389 | 1.7004 | 0.42814 | 3.0346 | 62.0552 | 30.4734 | 1.3576 | 0.31944 | 314.2007 | 28.76 | 41.76
2021-01-17 14:25 | 4.9835 | 1.341 | 0.39482 | 2.4504 | 65.2637 | 52.2659 | 1.3579 | 0.29047 | 314.1042 | 28.78 | 42.31
2021-01-17 14:30 | 4.4867 | 1.1486 | 0.34044 | 2.1011 | 62.0061 | 42.0865 | 1.3504 | 0.28315 | 314.7172 | 28.76 | 41.83
2021-01-17 14:35 | 4.8165 | 1.1675 | 0.37171 | 2.1634 | 66.0336 | 50.214 | 1.3502 | 0.32666 | 314.7821 | 28.74 | 41.53
2021-01-17 14:40 | 4.4478 | 1.2983 | 0.43852 | 2.4285 | 67.7283 | 50.476 | 1.3429 | 0.30487 | 315.8168 | 28.77 | 41.34
2021-01-17 14:45 | 4.1572 | 1.2266 | 0.399 | 2.2791 | 69.3223 | 39.9092 | 1.3362 | 0.29773 | 313.5448 | 28.81 | 42.26
2021-01-17 14:50 | 4.9332 | 1.2853 | 0.3886 | 2.3588 | 69.3908 | 47.7252 | 1.3363 | 0.42123 | 313.5009 | 28.82 | 42.5
2021-01-17 14:55 | 5.3144 | 1.2743 | 0.37187 | 2.3252 | 74.5237 | 46.7261 | 1.3435 | 0.3849 | 314.5043 | 28.88 | 42.23
2021-01-17 15:00 | 6.6227 | 1.2264 | 0.33002 | 2.2099 | 71.0418 | 30.3753 | 1.3505 | 0.50826 | 315.0894 | 28.88 | 41.76
2021-01-17 15:05 | 5.958 | 1.4354 | 0.37992 | 2.5801 | 68.0712 | 54.8086 | 1.3497 | 0.43538 | 314.7579 | 28.88 | 40.24
2021-01-17 15:10 | 6.5297 | 1.4 | 0.40288 | 2.5488 | 62.0548 | 28.5171 | 1.3569 | 0.67484 | 315.3147 | 28.85 | 40.31
2021-01-17 15:15 | 7.1146 | 1.2448 | 0.3716 | 2.2818 | 55.108 | 38.5207 | 1.357 | 0.80552 | 315.2879 | 28.85 | 40.52
2021-01-17 15:20 | 6.5211 | 1.3831 | 0.33838 | 2.4585 | 54.7312 | 48.7313 | 1.3505 | 0.63896 | 315.1062 | 28.86 | 41.84
2021-01-17 15:25 | 4.7051 | 1.2214 | 0.31971 | 2.192 | 63.4101 | 44.6608 | 1.3438 | 0.51572 | 313.9118 | 28.88 | 42.76
2021-01-17 15:30 | 3.79 | 1.043 | 0.33437 | 1.9331 | 57.9539 | 37.432 | 1.3367 | 0.37049 | 314.9247 | 28.88 | 43.05
2021-01-17 15:35 | [9 empty] | 28.89 | 43.08
2021-01-17 15:40 | 4.3119 | 1.3417 | 0.3992 | 2.4558 | 47.2758 | 28.5222 | 1.3441 | 0.45045 | 314.3348 | 28.91 | 43.24
2021-01-17 15:45 | 7.8349 | 1.3908 | 0.41173 | 2.5414 | 42.3392 | 48.4953 | 1.3658 | 0.96626 | 313.2747 | 28.93 | 43.11
2021-01-17 15:50 | 8.4582 | 1.3812 | 0.45771 | 2.5749 | 68.5405 | 59.0368 | 1.3658 | 1.0534 | 314.345 | 28.91 | 43.16
2021-01-17 15:55 | 6.7288 | 1.1604 | 0.43265 | 2.2113 | 73.2658 | 84.6322 | 1.3587 | 0.8646 | 313.7926 | 28.92 | 43.27
2021-01-17 16:00 | 4.5794 | 1.065 | 0.39505 | 2.0275 | 87.1301 | 74.3078 | 1.3515 | 0.42142 | 313.765 | 28.93 | 43.38
2021-01-17 16:05 | 5.2787 | 1.1059 | 0.38876 | 2.0839 | 65.7056 | 38.5767 | 1.3441 | 0.29062 | 315.3127 | 28.97 | 43.16
2021-01-17 16:10 | 4.9855 | 1.1057 | 0.372 | 2.0648 | 50.4558 | 47.8511 | 1.344 | 0.30512 | 314.8486 | 28.95 | 42.9
2021-01-17 16:15 | 6.1806 | 1.1588 | 0.38659 | 2.1628 | 47.9797 | 37.2972 | 1.3511 | 0.39226 | 314.873 | 28.95 | 42.71
2021-01-17 16:20 | 5.5078 | 1.1713 | 0.35742 | 2.1529 | 53.6381 | 43.6045 | 1.3587 | 0.32696 | 314.257 | 28.97 | 43.21
2021-01-17 16:25 | 5.8887 | 1.0485 | 0.28841 | 1.8956 | 60.2659 | 47.2929 | 1.3585 | 0.36324 | 314.3039 | 28.96 | 42.95
2021-01-17 16:30 | 6.0026 | 1.0225 | 0.29047 | 1.8577 | 61.2465 | 42.3334 | 1.3657 | 0.385 | 314.3262 | 28.97 | 42.67
2021-01-17 16:35 | 5.2885 | 1.0971 | 0.36975 | 2.0514 | 58.1432 | 37.7112 | 1.3579 | 0.35582 | 314.9419 | 28.99 | 41.75
2021-01-17 16:40 | 4.6906 | 1.127 | 0.33839 | 2.0679 | 44.359 | 38.7455 | 1.3578 | 0.43566 | 314.9772 | 28.98 | 41.58
2021-01-17 16:45 | 4.3589 | 1.3732 | 0.31949 | 2.4244 | 42.9433 | 22.4476 | 1.3647 | 0.36294 | 314.5951 | 28.93 | 40.99
2021-01-17 16:50 | 5.0078 | 1.3462 | 0.33207 | 2.3955 | 54.8667 | 61.7809 | 1.3721 | 0.35574 | 315.5665 | 28.96 | 41.29
2021-01-17 16:55 | 5.3518 | 1.33 | 0.37599 | 2.4147 | 66.9775 | 67.3843 | 1.3724 | 0.33401 | 315.4945 | 28.98 | 41.64
2021-01-17 17:00 | 6.3922 | 1.2506 | 0.4072 | 2.3242 | 71.3794 | 54.7469 | 1.3647 | 0.3702 | 314.5516 | 28.97 | 40.91
2021-01-17 17:05 | 6.6743 | 1.2143 | 0.36767 | 2.229 | 61.2565 | 49.4385 | 1.3725 | 0.34856 | 314.9878 | 28.94 | 41.92
2021-01-17 17:10 | 6.3821 | 1.1462 | 0.29665 | 2.0535 | 58.4304 | 43.8965 | 1.3725 | 0.44297 | 315.002 | 28.92 | 42.02
2021-01-17 17:15 | 5.7219 | 0.99369 | 0.29878 | 1.8219 | 54.2998 | 40.2823 | 1.38 | 0.43578 | 314.9923 | 28.88 | 42.52
2021-01-17 17:20 | 5.4779 | 1.0287 | 0.37593 | 1.9527 | 49.7515 | 37.6517 | 1.3649 | 0.32669 | 315.6858 | 28.85 | 41.52
2021-01-17 17:25 | 4.6763 | 1.0149 | 0.37168 | 1.9273 | 46.1534 | 29.1763 | 1.3501 | 0.27582 | 314.695 | 28.85 | 41.05
2021-01-17 17:30 | 4.0936 | 1.0998 | 0.33633 | 2.0222 | 43.0008 | 31.0505 | 1.3507 | 0.2469 | 315.101 | 28.83 | 42.2
2021-01-17 17:35 | 4.1185 | 1.037 | 0.28407 | 1.8757 | 39.6903 | 21.8637 | 1.3432 | 0.24687 | 315.2037 | 28.77 | 42.03
2021-01-17 17:40 | 4.2431 | 0.86206 | 0.28599 | 1.6074 | 33.9652 | 21.3731 | 1.3497 | 0.24672 | 315.9378 | 28.75 | 40.6
2021-01-17 17:45 | 4.0662 | 0.78871 | 0.28397 | 1.4929 | 33.7702 | 28.4739 | 1.35 | 0.25404 | 315.8713 | 28.74 | 41.23
2021-01-17 17:50 | 3.6984 | 0.77386 | 0.28402 | 1.4723 | 35.5247 | 34.8232 | 1.3503 | 0.23956 | 315.807 | 28.75 | 41.63
2021-01-17 17:55 | 3.5588 | 0.87747 | 0.28822 | 1.6332 | 33.8904 | 32.3652 | 1.3649 | 0.24684 | 314.732 | 28.75 | 41.82
2021-01-17 18:00 | 4.8553 | 1.1554 | 0.33417 | 2.1074 | 43.6929 | 40.134 | 1.3576 | 0.2541 | 315.2646 | 28.74 | 41.87
2021-01-17 18:05 | 4.0181 | 0.95145 | 0.29461 | 1.753 | 45.349 | 40.5985 | 1.3582 | 0.21063 | 315.6888 | 28.71 | 42.99
2021-01-17 18:10 | 3.8382 | 0.7616 | 0.25061 | 1.4159 | 43.4758 | 43.6181 | 1.3575 | 0.22505 | 315.374 | 28.66 | 41.86
2021-01-17 18:15 | 3.2907 | 0.7028 | 0.24636 | 1.3236 | 42.9952 | 23.5406 | 1.3571 | 0.21046 | 314.9743 | 28.63 | 41.18
2021-01-17 18:20 | 3.4938 | 0.82669 | 0.27139 | 1.5386 | 34.9326 | 31.5887 | 1.3498 | 0.29027 | 316.583 | 28.62 | 41.04
2021-01-17 18:25 | 3.7746 | 0.84878 | 0.26313 | 1.5642 | 30.6236 | 25.2248 | 1.3575 | 0.29763 | 316.4842 | 28.61 | 41.93
2021-01-17 18:30 | 4.9544 | 1.0023 | 0.36113 | 1.8975 | 32.3485 | 36.251 | 1.3497 | 0.26848 | 316.1236 | 28.58 | 40.94
2021-01-17 18:35 | 4.9173 | 1.1196 | 0.34867 | 2.0649 | 53.3656 | 79.2149 | 1.3572 | 0.29031 | 315.8411 | 28.59 | 41.45
2021-01-17 18:40 | 4.0553 | 0.95121 | 0.34049 | 1.8006 | 66.7351 | 56.972 | 1.3506 | 0.26141 | 316.2102 | 28.59 | 42.7
2021-01-17 18:45 | 3.2405 | 0.96312 | 0.3696 | 1.8459 |  | 48.3501 | 1.3574 | 0.23228 | 316.9394 | 28.51 | 41.95
2021-01-17 18:50 | 2.7825 | 0.98476 | 0.31108 | 1.8206 |  | 64.4531 | 1.3571 | 0.2903 | 317.4745 | 28.55 | 41.45
2021-01-17 18:55 | 3.1132 | 0.93581 | 0.24638 | 1.6829 | 1.2504 | 53.511 | 1.3573 | 0.26129 | 318.0974 | 28.43 | 41.98
2021-01-17 19:00 | 3.1122 | 0.9287 | 0.22752 | 1.6511 | 33.5554 | 46.8475 | 1.3641 | 0.2467 | 318.3697 | 28.27 | 41.54
2021-01-17 19:05 | 3.5567 | 0.77344 | 0.25882 | 1.4465 | 48.7772 | 36.6642 | 1.3568 | 0.2612 | 317.9977 | 28.13 | 41.82
2021-01-17 19:10 | 2.9978 | 0.6972 | 0.24421 | 1.3129 | 44.581 | 43.5953 | 1.3568 | 0.20316 | 317.5812 | 28.02 | 42.13
2021-01-17 19:15 | 3.2139 | 0.80889 | 0.26718 | 1.5071 | 29.5319 | 15.5586 | 1.3569 | 0.21768 | 319.2597 | 27.92 | 42.46
2021-01-17 19:20 | 2.7566 | 0.80481 | 0.26092 | 1.4946 | 33.8413 | 38.9327 | 1.3496 | 0.17415 | 319.266 | 27.91 | 42.52
2021-01-17 19:25 | 3.6203 | 0.82114 | 0.24839 | 1.5071 | 36.0866 | 19.2577 | 1.3569 | 0.21042 | 318.2687 | 27.86 | 42.6
2021-01-17 19:30 | 3.7093 | 0.91239 | 0.26719 | 1.6657 | 37.327 | 42.2965 | 1.3496 | 0.23945 | 319.1632 | 27.81 | 42.81
2021-01-17 19:35 | 3.2267 | 0.96688 | 0.27345 | 1.7555 | 44.4516 | 47.1549 | 1.3496 | 0.23945 | 319.2008 | 27.77 | 42.95
2021-01-17 19:40 | 3.4045 | 0.92194 | 0.27763 | 1.6908 | 47.8664 | 35.6508 | 1.3642 | 0.21769 | 319.7606 | 27.74 | 43.03
2021-01-17 19:45 | 2.871 | 0.82253 | 0.28598 | 1.5489 | 45.0313 | 33.6795 | 1.3569 | 0.18866 | 319.2721 | 27.7 | 43.15
2021-01-17 19:50 | 2.8203 | 0.79125 | 0.26929 | 1.4821 | 49.7692 | 37.4209 | 1.3642 | 0.21044 | 318.1593 | 27.74 | 43.16
2021-01-17 19:55 | 2.3249 | 0.69048 | 0.24007 | 1.2985 | 35.9481 | 28.5389 | 1.3643 | 0.34106 | 317.666 | 27.7 | 43.32
2021-01-17 20:00 | 2.2233 | 0.85394 | 0.27139 | 1.5803 | 39.1713 | 42.7388 | 1.357 | 0.32656 | 318.215 | 27.67 | 43.49
2021-01-17 20:05 | 2.287 | 0.76138 | 0.25471 | 1.4218 | 55.8638 | 62.8976 | 1.3644 | 0.22498 | 319.2304 | 27.69 | 43.61
2021-01-17 20:10 | 2.3633 | 0.66741 | 0.22757 | 1.2506 | 65.0839 | 58.0093 | 1.3644 | 0.18144 | 320.3255 | 27.65 | 43.75
2021-01-17 20:15 | 2.249 | 0.64426 | 0.19417 | 1.1817 | 66.9147 | 53.9343 | 1.3572 | 0.14515 | 319.2837 | 27.63 | 43.85
2021-01-17 20:20 | 2.0459 | 0.62256 | 0.19211 | 1.1485 | 51.9697 | 30.2851 | 1.3574 | 0.1234 | 319.2494 | 27.62 | 44.25
2021-01-17 20:25 | 1.9444 | 0.57082 | 0.21091 | 1.0859 | 38.9587 | 11.8035 | 1.3429 | 0.11614 | 318.738 | 27.59 | 44.45
2021-01-17 20:30 | 1.6903 | 0.57765 | 0.2318 | 1.1193 | 27.8373 | 12.0072 | 1.3502 | 0.11615 | 320.3561 | 27.55 | 44.64
2021-01-17 20:35 | 1.4108 | 0.58043 | 0.20885 | 1.0965 | 23.4066 | 21.0273 | 1.3503 | 0.087119 | 319.312 | 27.51 | 44.99
2021-01-17 20:40 | 2.5801 | 0.58314 | 0.20885 | 1.1027 | 13.0147 | 1.2303 | 1.3503 | 0.12342 | 319.3497 | 27.48 | 45.02
2021-01-17 20:45 | 1.7159 | 0.47961 | 0.1817 | 0.91686 | 10.4426 | -0.91512 | 1.3431 | 0.08712 | 319.372 | 27.45 | 45.18
2021-01-17 20:50 | 1.538 | 0.48644 | 0.19215 | 0.93778 | 16.5848 | 13.1377 | 1.3504 | 0.087124 | 318.8722 | 27.41 | 45.4
2021-01-17 20:55 | 1.627 | 0.481 | 0.15247 | 0.88977 | 24.1812 | 22.8796 | 1.3504 | 0.10165 | 319.9648 | 27.37 | 45.57
2021-01-17 21:00 | 1.4744 | 0.37744 | 0.14829 | 0.72684 | 24.913 | 26.0926 | 1.3504 | 0.087124 | 320.0335 | 27.31 | 45.69
2021-01-17 21:05 | 1.3855 | 0.46602 | 0.14412 | 0.85846 | 30.6493 | 15.5992 | 1.3432 | 0.10165 | 319.0162 | 27.26 | 45.93
2021-01-17 21:10 | 1.4873 | 0.62003 | 0.12742 | 1.0778 | 24.8034 | 30.0102 | 1.3506 | 0.11618 | 319.539 | 27.25 | 46.1
2021-01-17 21:15 | 1.5 | 0.52056 | 0.15666 | 0.9546 | 30.1327 | 15.7935 | 1.3506 | 0.19605 | 320.1058 | 27.21 | 46.25
2021-01-17 21:20 | 1.8306 | 0.49606 | 0.14414 | 0.90661 | 27.1139 | 24.0526 | 1.3506 | 0.36308 | 319.5797 | 27.19 | 46.46
2021-01-17 21:25 | 1.4366 | 0.43747 | 0.13578 | 0.80635 | 20.2187 | 8.5736 | 1.3579 | 0.22511 | 319.5865 | 27.18 | 46.52
2021-01-17 21:30 | 1.3603 | 0.41976 | 0.13788 | 0.78131 | 26.0471 | 12.2251 | 1.358 | 0.21059 | 318.6038 | 27.1 | 46.82
2021-01-17 21:35 | 1.5001 | 0.35569 | 0.14623 | 0.68936 | 22.8119 | 18.7743 | 1.3506 | 0.21785 | 319.2205 | 27.03 | 46.9
2021-01-17 21:40 | 1.5639 | 0.38436 | 0.16296 | 0.75212 | 31.1144 | 33.5047 | 1.3581 | 0.22513 | 319.1938 | 27.02 | 47.25
2021-01-17 21:45 | 1.1316 | 0.22217 | 0.10864 | 0.44919 | 25.8259 | 20.9232 | 1.3508 | 0.14525 | 320.2339 | 27.03 | 47.29
2021-01-17 21:50 | 1.3477 | 0.25488 | 0.12953 | 0.52023 | 22.1539 | 15.8983 | 1.3581 | 0.27598 | 320.3092 | 26.96 | 47.48
2021-01-17 21:55 | 1.0935 | 0.16493 | 0.10447 | 0.35727 | 18.9402 | 6.1337 | 1.3509 | 0.18157 | 320.3533 | 26.91 | 47.7
2021-01-17 22:00 | 0.92824 | 0.13904 | 0.089845 | 0.30297 | 21.7488 | 16.6422 | 1.3509 | 0.17432 | 319.8715 | 26.85 | 48.01
2021-01-17 22:05 | 1.0936 | 0.20175 | 0.096118 | 0.40537 | 15.707 | 4.8118 | 1.3583 | 0.18885 | 318.8299 | 26.82 | 48.22
2021-01-17 22:10 | 0.82653 | 0.18675 | 0.10447 | 0.39073 | 9.542 | -2.6144 | 1.3437 | 0.14527 | 319.4408 | 26.75 | 48.36
2021-01-17 22:15 | 0.67395 | 0.18403 | 0.12119 | 0.40119 | 6.7345 | 9.766 | 1.351 | 0.10169 | 318.9692 | 26.69 | 48.58
2021-01-17 22:20 | 0.80114 | 0.23175 | 0.10239 | 0.45971 | 3.3978 | -3.8862 | 1.3438 | 0.094428 | 320.5497 | 26.69 | 48.66
2021-01-17 22:25 | 0.89012 | 0.15676 | 0.1003 | 0.34059 | 13.2856 | -2.4415 | 1.3437 | 0.094423 | 320.0977 | 26.63 | 48.71
2021-01-17 22:30 | 0.81382 | 0.13631 | 0.098205 | 0.30715 | 11.4138 | 20.437 | 1.3437 | 0.08716 | 320.1527 | 26.58 | 48.84
2021-01-17 22:35 | 0.81382 | 0.12541 | 0.096116 | 0.28835 | 8.6774 | -9.3793 | 1.3437 | 0.094424 | 319.6847 | 26.52 | 49.03
2021-01-17 22:40 | 0.66124 | 0.14041 | 0.083581 | 0.2988 | 6.0834 | -3.8148 | 1.3583 | 0.058108 | 319.2461 | 26.43 | 49.33
2021-01-17 22:45 | 0.57227 | 0.18949 | 0.085676 | 0.37614 | 2.9198 | 6.9181 | 1.3511 | 0.079904 | 319.774 | 26.41 | 49.6
2021-01-17 22:50 | 0.68675 | 0.18269 | 0.096129 | 0.37616 | 7.1422 | -2.747 | 1.3439 | 0.079907 | 318.7117 | 26.4 | 49.74
2021-01-17 22:55 | 0.6232 | 0.18133 | 0.087775 | 0.36573 | 11.7009 | 9.5948 | 1.3512 | 0.036324 | 319.698 | 26.45 | 49.78
2021-01-17 23:00 | 0.50874 | 0.13907 | 0.075237 | 0.28841 | 9.8289 | 1.1396 | 1.3367 | 0.050854 | 319.7359 | 26.41 | 49.94
2021-01-17 23:05 | 0.45788 | 0.14725 | 0.077328 | 0.30304 | 7.0208 | 12.6984 | 1.344 | 0.036325 | 319.2224 | 26.39 | 50.04
2021-01-17 23:10 | 0.48335 | 0.10227 | 0.079424 | 0.23618 | 8.8937 | 1.2211 | 1.3441 | 0.021797 | 319.7707 | 26.35 | 50.38
2021-01-17 23:15 | 0.50879 | 0.14181 | 0.077334 | 0.29471 | 12.4247 | 1.5264 | 1.3514 | 0.021797 | 320.3745 | 26.28 | 50.6
2021-01-17 23:20 | 0.43248 | 0.26862 | 0.037622 | 0.44938 | 8.4867 | 11.9465 | 1.3441 | 0.021797 | 318.7811 | 26.28 | 50.62
2021-01-17 23:25 | 0.48338 | 0.27682 | 0.081519 | 0.50583 | 20.3833 | 13.2496 | 1.3442 | 0.021798 | 319.2758 | 26.3 | 50.69
2021-01-17 23:30 | 0.34344 | 0.16772 | 0.073155 | 0.33024 | 10.6645 | 1.0481 | 1.3369 | 0.043594 | 320.4546 | 26.2 | 50.89
2021-01-17 23:35 | 0.36892 | 0.18138 | 0.064802 | 0.34282 | 6.9611 | -0.89559 | 1.3443 | 0.058132 | 319.3699 | 26.19 | 51.23
2021-01-17 23:40 | 0.40709 | 0.14046 | 0.075254 | 0.29056 | 9.1594 | 7.5616 | 1.337 | 0.0072665 | 320.4728 | 26.15 | 51.36
2021-01-17 23:45 | 0.39437 | 0.091371 | 0.058531 | 0.19859 | 5.0174 | 9.8312 | 1.337 | 0.0072666 | 320.5652 | 26.06 | 51.67
2021-01-17 23:50 |  | 0.088637 | 0.060617 | 0.19648 | 5.2714 | -8.8332 | 1.3369 | 0.014532 | 319.1054 | 25.96 | 51.74
2021-01-17 23:55 | 0.34347 | 0.098188 | 0.06062 | 0.21113 | 4.539 | 1.608 | 1.337 | 0.0072664 | 319.1192 | 25.93 | 52
2021-01-18 | 0.31804 | 0.073642 | 0.05435 | 0.16723 | 6.1979 | 12.1922 | 1.3443 | 0.0072665 | 320.1779 | 25.93 | 52.03
2021-01-18 00:05 | 0.20354 | 0.049095 | 0.048079 | 0.12333 | 11.7648 | -0.040709 | 1.337 | 0.014533 | 319.6889 | 25.89 | 52.16
2021-01-18 00:10 | 0.16539 | 0.032733 | 0.048084 | 0.098258 | 12.1324 | 4.1832 | 1.3444 | 0.021802 | 319.679 | 25.87 | 52.51
2021-01-18 00:15 | 0.089058 | 0.021822 | 0.039721 | 0.07317 | 12.4376 | 12.458 | 1.3372 | 0.014534 | 321.3178 | 25.83 | 52.61
2021-01-18 00:20 | 0.063615 | 0.028642 | 0.058538 | 0.10244 | 6.3716 | 0.10178 | 1.3372 | 0.014535 | 320.2686 | 25.81 | 52.75
2021-01-18 00:25 | 0.19084 | 0.050463 | 0.050174 | 0.12752 | 10.748 | -9.5776 | 1.3444 | 0.036336 | 320.2773 | 25.81 | 52.67
2021-01-18 00:30 | 0.27988 | 0.038186 | 0.04599 | 0.10661 | 4.0303 | 0.65136 | 1.3371 | 0.029067 | 320.8594 | 25.78 | 52.59
2021-01-18 00:35 | 0.17813 | 0.03819 | 0.043904 | 0.10244 | 4.6109 | 2.2189 | 1.3372 | 0.014535 | 319.7603 | 25.78 | 52.93
2021-01-18 00:40 | 0.12724 | 0.043648 | 0.039725 | 0.10663 | -0.59039 | -7.3086 | 1.3373 | 0.014536 | 319.7766 | 25.75 | 53.17
2021-01-18 00:45 | 0.1018 | 0.039558 | 0.043909 | 0.10454 | -0.57006 | -4.3263 | 1.3446 | 0.014537 | 321.0228 | 25.76 | 53.23
2021-01-18 00:50 | 0.050897 | 0.036829 | 0.039726 | 0.096179 | 7.4208 | 6.8507 | 1.3373 | 0.014536 | 320.0235 | 25.71 | 53.31
2021-01-18 00:55 | 0.15269 | 0.032737 | 0.043907 | 0.094087 | -2.6059 | 1.5676 | 1.3373 | 0.007268 | 320.0692 | 25.67 | 53.41
2021-01-18 01:00 | 0.10179 | 0.034101 | 0.045999 | 0.09827 | -4.764 | -10.2303 | 1.3373 | 0.014536 | 320.1064 | 25.63 | 53.59
2021-01-18 01:05 |  |  |  |  | 7.8489 | -0.58027 |  |  | 320.1046 | 25.61 | 53.87
2021-01-18 01:10 |  |  |  |  | 0.70244 | -1.3845 |  |  | 319.5618 | 25.62 | 53.85
2021-01-18 01:15 |  |  |  |  | 4.8049 | 6.1894 |  |  | 320.1241 | 25.6 | 53.82
2021-01-18 01:20 |  |  |  |  | 4.1334 | -7.7781 |  |  | 319.5763 | 25.59 | 54.11
2021-01-18 01:25 |  |  |  |  | -2.7589 | 1.6085 |  |  | 320.1627 | 25.55 | 54.12
2021-01-18 01:30 |  |  |  |  | -0.24433 | 5.6093 |  |  | 320.1867 | 25.53 | 54.16
2021-01-18 01:35 |  |  |  |  | 3.818 | -13.8263 |  |  | 320.6627 | 25.55 | 54.41
2021-01-18 01:40 |  |  |  |  | -1.5577 | -0.7534 |  |  | 321.2142 | 25.54 | 54.35
2021-01-18 01:45 |  |  |  |  | 0.091631 | 2.586 |  |  | 320.1042 | 25.58 | 54.27
2021-01-18 01:50 |  |  |  |  | 9.887 | 2.5354 |  |  | 319.5612 | 25.56 | 54.65
2021-01-18 01:55 |  |  |  |  | -0.75348 | -4.8874 |  |  | 320.0764 | 25.58 | 54.53
2021-01-18 02:00 |  |  |  |  | 3.5433 | 4.4801 |  |  | 320.6215 | 25.57 | 54.53
2021-01-18 02:05 |  |  |  |  | 6.6799 | 0.71279 |  |  | 320.6288 | 25.54 | 54.86
2021-01-18 02:10 | 0.12728 | 0.20331 | 0.077387 | 0.38903 | 4.9285 | -3.8593 | 1.425 | -0.079975 | 320.5649 | 25.6 | 54.66
2021-01-18 02:15 | 0.15275 | 0.14465 | 0.050201 | 0.27192 | 1.0387 | -3.33 | 1.4033 | -0.029084 | 320.2522 | 25.57 | 54.93
2021-01-18 02:20 | 0.14004 | 0.083251 | 0.048115 | 0.17572 | 1.9555 | 3.4425 | 1.3817 | -0.0072719 | 320.2877 | 25.5 | 55.53
2021-01-18 02:25 | 0.14004 | 0.08052 | 0.046022 | 0.16735 | 3.4831 | 1.3647 | 1.3744 | 0.021816 | 320.4104 | 25.39 | 55.85
2021-01-18 02:30 | 0.11458 | 0.099624 | 0.071124 | 0.22383 | 10.3983 | 10.0419 | 1.3744 | 0.021815 | 320.4811 | 25.33 | 55.99
2021-01-18 02:35 | 0.11457 | 0.27293 | 0.050203 | 0.47065 | 9.3997 | 4.4198 | 1.3743 | 0.036357 | 319.9463 | 25.35 | 55.76
2021-01-18 02:40 | 0.15275 | 0.57312 | 0.092033 | 0.96844 | 6.609 | 10.5296 | 1.3742 | 0.036355 | 319.8781 | 25.43 | 55.33
2021-01-18 02:45 | 0.19094 | 0.51309 | 0.073209 | 0.86178 | 11.9453 | -0.11202 | 1.3742 | 0.036355 | 320.3172 | 25.51 | 55.12
2021-01-18 02:50 | 0.76375 | 0.46532 | 0.081575 | 0.79483 | 8.6966 | 0.83503 | 1.3742 | 0.036355 | 320.907 | 25.46 | 55.23
2021-01-18 02:55 | 1.4001 | 0.33156 | 0.060653 | 0.57097 | 5.1829 | -1.1099 | 1.3814 | 0.036351 | 320.9988 | 25.4 | 55.17
2021-01-18 03:00 | [9 empty] | 25.3 | 55.37
2021-01-18 03:05 | 0.84003 | 0.19784 | 0.060651 | 0.36391 | 7.9828 | 12.2593 | 1.3813 | 0.03635 | 320.0873 | 25.27 | 55.5
2021-01-18 03:10 | 0.44549 | 0.32338 | 0.06902 | 0.56471 | 4.4396 | 5.3764 | 1.3959 | 0.036352 | 320.0305 | 25.31 | 55.5
2021-01-18 03:15 | 0.35639 | 0.30974 | 0.087844 | 0.56262 | 14.9788 | 7.637 | 1.4105 | 0.029082 | 320.0053 | 25.33 | 55.47
2021-01-18 03:20 | 0.33094 | 0.26471 | 0.087845 | 0.49361 | 12.1991 | -2.5457 | 1.4032 | 0.050894 | 319.4484 | 25.35 | 55.45
2021-01-18 03:25 | 0.44548 | 0.28244 | 0.092025 | 0.52496 | 0.39712 | -0.95715 | 1.4177 | 0.043622 | 320.5002 | 25.37 | 55.27
2021-01-18 03:30 | 0.28 | 0.20602 | 0.10457 | 0.42037 | 3.8386 | 9.1943 | 1.4104 | 0.04362 | 321.0578 | 25.36 | 55.15
2021-01-18 03:35 | 0.24183 | 0.19784 | 0.10457 | 0.40574 | 6.0178 | 6.7102 | 1.4104 | 0.043621 | 318.3819 | 25.37 | 55.23
2021-01-18 03:40 | 0.31819 | 0.31109 | 0.11085 | 0.58978 | 1.6902 | -3.9405 | 1.4104 | 0.043621 | 319.4045 | 25.41 | 55.06
2021-01-18 03:45 | 0.49638 | 0.30563 | 0.081565 | 0.55004 | 20.8936 | 16.7292 | 1.4104 | 0.04362 | 320.9034 | 25.5 | 54.73
2021-01-18 03:50 | 0.44546 | 0.35747 | 0.08993 | 0.63578 | 17.8796 | 16.0061 | 1.4031 | 0.07997 | 320.3322 | 25.54 | 54.58
2021-01-18 03:55 | 0.40727 | 0.3711 | 0.10666 | 0.67549 | 18.3066 | 18.2252 | 1.4103 | 0.10905 | 319.7917 | 25.56 | 54.41
2021-01-18 04:00 | 0.63639 | 0.83912 | 0.20078 | 1.487 |  |  | 1.4104 | 0.11632 | 382.8023 | 25.62 | 54.39
2021-01-18 04:05 | 0.71273 | 0.86774 | 0.18195 | 1.5141 |  |  | 1.4176 | 0.11632 | 460.184 | 25.65 | 54.17
2021-01-18 04:10 | 0.58543 | 0.59756 | 0.12129 | 1.0352 |  | -14.9564 | 1.4103 | 0.13812 | 459.754 | 25.6 | 54.18
2021-01-18 04:15 | 0.45816 | 0.5007 | 0.10875 | 0.87833 |  | 22.8776 | 1.403 | 0.1672 | 459.858 | 25.53 | 54.43
2021-01-18 04:20 | 0.73811 | 0.51568 | 0.1192 | 0.90965 | 9.5598 | 14.3652 | 1.4175 | 0.13811 | 458.9443 | 25.45 | 54.53
2021-01-18 04:25 | 0.75088 | 0.50616 | 0.12548 | 0.90133 | 28.3245 | 38.5466 | 1.4176 | 0.11631 | 459.4063 | 25.48 | 54.58
2021-01-18 04:30 | 0.71268 | 0.59346 | 0.1652 | 1.0728 | 36.5094 | 15.3327 | 1.4175 | 0.12358 | 457.2652 | 25.5 | 54.44
2021-01-18 04:35 | 0.71268 | 0.86223 | 0.17984 | 1.4994 | 41.5698 | 35.1964 | 1.4466 | 0.13812 | 458.7906 | 25.54 | 54.34
2021-01-18 04:40 | 1.2344 | 0.99587 | 0.20284 | 1.7314 | 44.978 | 30.0837 | 1.432 | 0.1163 | 458.2251 | 25.58 | 54.04
2021-01-18 04:45 | 2.3416 | 1.2987 | 0.28649 | 2.2773 | 52.0851 | 71.7748 | 1.432 | 0.23261 | 459.6688 | 25.67 | 53.81
2021-01-18 04:50 | 3.1179 | 1.4379 | 0.37431 | 2.5784 | 67.8043 | 51.2401 | 1.4393 | 0.23988 | 456.9103 | 25.74 | 53.59
2021-01-18 04:55 | 2.8888 | 1.4897 | 0.36177 | 2.6432 | 66.7255 | 50.7008 | 1.4466 | 0.37073 | 458.4365 | 25.78 | 53.48
2021-01-18 05:00 | 2.7362 | 1.4106 | 0.34923 | 2.5115 | 79.8906 | 75.0648 | 1.4539 | 0.37073 | 457.8536 | 25.81 | 53.43
2021-01-18 05:05 | 3.0416 | 1.6917 | 0.39523 | 2.9883 | 68.1617 | 46.3133 | 1.4466 | 0.44342 | 457.7073 | 25.86 | 53.31
2021-01-18 05:10 | 2.5324 | 1.8144 | 0.41822 | 3.1994 | 67.111 | 52.3083 | 1.4465 | 0.33437 | 458.1444 | 25.93 | 53
2021-01-18 05:15 | 2.736 | 1.8826 | 0.48932 | 3.375 | 81.1294 | 73.7485 | 1.4538 | 0.3271 | 458.0699 | 25.98 | 52.83
2021-01-18 05:20 | 3.2579 | 2.5716 | 0.63572 | 4.5797 | 89.7457 | 98.7559 | 1.4611 | 0.34165 | 456.8393 | 26.08 | 52.63
2021-01-18 05:25 | 3.7797 | 2.7381 | 0.60226 | 4.7993 | 114.6282 | 123.0581 | 1.4684 | 0.42162 | 453.4926 | 26.19 | 52.29
2021-01-18 05:30 | 3.9836 | 3.2103 | 0.80724 | 5.7281 | 156.1453 | 164.5553 | 1.4685 | 0.41437 | 455.205 | 26.44 | 51.69
2021-01-18 05:35 | 4.6325 | 3.5608 | 0.78003 | 6.2382 | 172.7871 | 151.4165 | 1.4612 | 0.39982 | 454.3103 | 26.69 | 50.85
2021-01-18 05:40 | 4.6451 | 3.4188 | 0.73818 | 5.9787 | 172.3739 | 126.132 | 1.4611 | 0.40708 | 452.9809 | 26.88 | 50.19
2021-01-18 05:45 | 4.6831 | 3.2673 | 0.7528 | 5.761 | 188.1485 | 168.0824 | 1.4538 | 0.46521 | 455.4712 | 26.99 | 49.78
2021-01-18 05:50 | 4.8867 | 3.506 | 0.8469 | 6.221 | 170.7292 | 142.6307 | 1.4683 | 0.55971 | 456.3155 | 27.13 | 49.37
2021-01-18 05:55 | 7.3171 | 4.2985 | 0.83432 | 7.4231 | 186.1258 | 172.9729 | 1.4683 | 0.6978 | 452.9368 | 27.28 | 48.84
2021-01-18 06:00 | 8.4364 | 5.2912 | 0.99317 | 9.1038 | 239.7504 | 248.0876 | 1.4827 | 0.87946 | 451.624 | 27.47 | 48.13
2021-01-18 06:05 | 6.9855 | 4.7754 | 0.93041 | 8.2524 | 247.6095 | 192.601 | 1.5335 | 0.69772 | 453.0288 | 27.6 | 47.66
2021-01-18 06:10 | 6.2474 | 4.5203 | 0.97849 | 7.9074 | 232.8165 | 160.8299 | 1.4972 | 0.5887 | 454.0281 | 27.64 | 47.52
2021-01-18 06:15 | 5.0895 | 3.2776 | 0.85093 | 5.8771 | 213.4719 | 151.8387 | 1.4754 | 0.55235 | 453.9468 | 27.7 | 47.3
2021-01-18 06:20 | 10.7519 | 3.2669 | 0.86352 | 5.8711 | 152.4766 | 136.6782 | 1.6935 | 0.69047 | 452.7366 | 27.79 | 47.17
2021-01-18 06:25 | 8.106 | 2.8715 | 0.70258 | 5.1042 | 117.0926 | 109.376 | 1.6645 | 0.51607 | 453.1965 | 27.81 | 47.33
2021-01-18 06:30 | 5.4714 | 2.8577 | 0.58753 | 4.9678 | 119.6279 | 102.7403 | 1.5772 | 0.45062 | 452.7512 | 27.78 | 47.2
2021-01-18 06:35 | 6.5785 | 3.1905 | 0.65862 | 5.5492 | 127.4572 | 113.5011 | 1.519 | 0.49423 | 452.2044 | 27.79 | 47.2
2021-01-18 06:40 | 6.6164 | 3.2572 | 0.64605 | 5.6388 | 153.1027 | 118.7485 | 1.4899 | 0.55235 | 451.5472 | 27.89 | 46.81
2021-01-18 06:45 | 6.6924 | 3.1834 | 0.70665 | 5.5863 | 155.3651 | 130.672 | 1.5044 | 0.59593 | 453.0596 | 27.95 | 46.52
2021-01-18 06:50 | 6.0696 | 3.2915 | 0.62309 | 5.6663 | 163.3934 | 134.2694 | 1.5481 | 0.596 | 451.7166 | 28.11 | 46.37
2021-01-18 06:55 | 7.7859 | 3.3141 | 0.71495 | 5.7949 | 160.8481 | 130.0504 | 1.5696 | 0.68309 | 452.8266 | 28.13 | 45.82
2021-01-18 07:00 | 8.3346 | 3.4197 | 0.72763 | 5.9695 | 156.7568 | 130.7885 | 1.5409 | 0.66868 | 452.6629 | 28.18 | 46.19
2021-01-18 07:05 | 7.0501 | 3.0217 | 0.63987 | 5.2716 | 156.1497 | 111.6199 | 1.541 | 0.55971 | 453.0436 | 28.25 | 46.23
2021-01-18 07:10 | 5.9307 | 2.9879 | 0.63157 | 5.2115 | 152.4169 | 98.5365 | 1.5412 | 0.53795 | 452.898 | 28.32 | 46.27
2021-01-18 07:15 | 5.4222 | 2.9336 | 0.5647 | 5.0614 | 146.9945 | 109.5942 | 1.5849 | 0.59616 | 452.2824 | 28.35 | 46.44
2021-01-18 07:20 | 6.0337 | 3.4988 | 0.67979 | 6.0407 | 154.8183 | 140.755 | 1.6214 | 0.58895 | 451.6561 | 28.39 | 46.56
2021-01-18 07:25 | 8.0325 | 3.0199 | 0.60242 | 5.2336 | 158.7246 | 128.4991 | 1.5851 | 0.53807 | 452.0448 | 28.47 | 46.44
2021-01-18 07:30 | 7.5876 | 3.027 | 0.56273 | 5.2026 | 141.5872 | 94.1063 | 1.578 | 0.5672 | 450.8354 | 28.55 | 46.44
2021-01-18 07:35 | 6.4422 | 3.5035 | 0.56277 | 5.9352 | 142.1058 | 100.3459 | 1.4908 | 0.58179 | 450.2057 | 28.6 | 46.47
2021-01-18 07:40 | 6.0606 | 3.9241 | 0.58372 | 6.5987 | 160.7428 | 171.3666 | 1.4545 | 0.58182 | 452.1645 | 28.68 | 46.38
2021-01-18 07:45 | 6.0481 | 3.4425 | 0.64442 | 5.9191 | 199.1432 | 172.8828 | 1.4328 | 0.51639 | 451.017 | 28.73 | 46.37
2021-01-18 07:50 | 6.5203 | 3.2136 | 0.63824 | 5.5642 | 193.968 | 85.11 | 1.4476 | 0.45827 | 451.3973 | 28.78 | 46.62
2021-01-18 07:55 | 6.2788 | 3.3204 | 0.70526 | 5.7928 | 164.2326 | 108.3473 | 1.4768 | 0.45104 | 450.2213 | 28.84 | 46.66
2021-01-18 08:00 | 5.5919 | 3.1365 | 0.67187 | 5.4796 | 142.7744 | 103.3079 | 1.4624 | 0.54568 | 453.2621 | 28.87 | 46.92
2021-01-18 08:05 | 5.4776 | 2.738 | 0.66982 | 4.8667 | 139.1356 | 97.0576 | 1.4261 | 0.54572 | 451.5686 | 28.93 | 46.92
2021-01-18 08:10 | 5.5422 | 2.3929 | 0.59038 | 4.2603 | 133.2667 | 101.2113 | 1.4191 | 0.50214 | 450.9419 | 28.95 | 47.26
2021-01-18 08:15 | 5.211 | 2.5704 | 0.55479 | 4.4949 | 110.4572 | 74.1715 | 1.4191 | 0.44393 | 450.4572 | 28.92 | 47.37
2021-01-18 08:20 | 4.001 | 2.5871 | 0.55485 | 4.5204 | 108.4594 | 60.2643 | 1.4047 | 0.43669 | 450.9539 | 28.91 | 47.63
2021-01-18 08:25 | 4.6233 | 2.788 | 0.5274 | 4.801 | 119.3969 | 20.3376 | 1.3968 | 0.36375 | 450.6972 | 28.86 | 46.71
2021-01-18 08:30 | 4.572 | 2.9872 | 0.59014 | 5.169 | 131.3693 | 81.1201 | 1.3967 | 0.34918 | 452.8308 | 28.86 | 46.52
2021-01-18 08:35 | 4.6861 | 2.6783 | 0.49591 | 4.5992 | 117.3566 | 91.8682 | 1.3893 | 0.32732 | 450.26 | 28.86 | 46.23
2021-01-18 08:40 | 4.5079 | 2.6975 | 0.51894 | 4.6558 | 127.1486 | 102.8721 | 1.3966 | 0.34187 | 451.2575 | 28.89 | 46.19
2021-01-18 08:45 | 3.7166 | 2.8026 | 0.59607 | 4.892 | 141.3233 | 121.1721 | 1.3814 | 0.36352 | 450.8578 | 28.95 | 44.86
2021-01-18 08:50 | 4.073 | 2.3332 | 0.51033 | 4.0847 | 136.9561 | 105.1762 | 1.4177 | 0.37079 | 451.3791 | 28.95 | 44.88
2021-01-18 08:55 | 4.9771 | 1.9186 | 0.46435 | 3.4052 | 148.565 | 157.4245 | 1.4251 | 0.35627 | 451.8707 | 28.95 | 45.06
2021-01-18 09:00 | 4.1109 | 2.0902 | 0.49564 | 3.6996 | 162.2152 | 116.7335 | 1.4103 | 0.31987 | 452.51 | 28.97 | 44.57
2021-01-18 09:05 | 3.1175 | 2.0843 | 0.51017 | 3.705 | 146.5738 | 87.7468 | 1.3955 | 0.27619 | 450.5137 | 28.97 | 44.02
2021-01-18 09:10 | 3.9439 | 1.9516 | 0.48082 | 3.4724 | 117.1271 | 68.2631 | 1.4025 | 0.27615 | 450.5975 | 28.96 | 43.67
2021-01-18 09:15 | 4.5682 | 2.0434 | 0.51228 | 3.6445 | 112.03 | 73.9877 | 1.3955 | 0.38523 | 451.002 | 28.98 | 44.11
2021-01-18 09:20 | 3.9578 | 2.1882 | 0.62526 | 3.9795 | 123.4235 | 94.4587 | 1.403 | 0.39981 | 450.3133 | 29.06 | 44.15
2021-01-18 09:25 | 2.9142 | 1.5415 | 0.46004 | 2.823 | 132.6835 | 97.2143 | 1.4029 | 0.31983 | 452.2766 | 29.16 | 43.81
2021-01-18 09:30 | 2.4433 | 1.4529 | 0.3764 | 2.6034 | 99.6575 | 29.941 | 1.3956 | 0.23987 | 452.7866 | 29.17 | 43.78
2021-01-18 09:35 | 2.889 | 1.453 | 0.40571 | 2.6329 | 98.7395 | 74.752 | 1.3885 | 0.27624 | 452.8377 | 29.11 | 44.14
2021-01-18 09:40 | 2.9512 | 1.5941 | 0.42432 | 2.8658 | 92.973 | 56.0932 | 1.3878 | 0.26158 | 452.0805 | 29.06 | 43.1
2021-01-18 09:45 | 2.8622 | 1.7946 | 0.43688 | 3.1878 | 111.9661 | 66.1905 | 1.3806 | 0.26885 | 453.2646 | 28.96 | 43.43
2021-01-18 09:50 | 3.0281 | 1.9736 | 0.51013 | 3.5374 | 110.9056 | 73.8455 | 1.3808 | 0.26163 | 450.0876 | 28.93 | 43.91
2021-01-18 09:55 | 5.026 | 2.1838 | 0.49971 | 3.8471 | 109.7933 | 70.6236 | 1.3882 | 0.30526 | 453.2198 | 28.92 | 44.1
2021-01-18 10:00 | 4.7873 | 2.0828 | 0.48956 | 3.6801 | 132.0574 | 88.7071 | 1.3891 | 0.33454 | 452.8732 | 28.96 | 45.55
2021-01-18 10:05 | 6.6786 | 1.9651 | 0.50377 | 3.5139 | 138.4781 | 57.3167 | 1.3951 | 0.49411 | 453.2609 | 28.96 | 43.45
2021-01-18 10:10 | 5.7223 | 1.7599 | 0.54745 | 3.2429 | 145.3201 |  | 1.4091 | 0.42854 | 453.4717 | 28.94 | 42.52
2021-01-18 10:15 | 5.0488 | 1.6237 | 0.50362 | 2.9925 | 123.0641 | 42.7713 | 1.402 | 0.42859 | 453.4556 | 28.92 | 42.82
2021-01-18 10:20 | 4.0321 | 1.8803 | 0.56432 | 3.4444 | 99.1309 | 48.9244 | 1.4022 | 0.34147 | 450.7423 | 28.93 | 43.2
2021-01-18 10:25 | 2.7846 | 1.9505 | 0.55577 | 3.5456 | 96.2282 | 66.902 | 1.3945 | 0.21789 | 452.9223 | 28.98 | 42.23
2021-01-18 10:30 | 2.7602 | 1.6636 | 0.50372 | 3.0537 | 93.4256 | 43.5023 | 1.4023 | 0.18891 | 453.2153 | 29.02 | 43.06
2021-01-18 10:35 | 2.5299 | 1.4146 | 0.45331 | 2.6217 | 86.9156 | 56.1198 | 1.3942 | 0.17428 | 452.0096 | 28.99 | 41.73
2021-01-18 10:40 | 2.2109 | 1.7122 | 0.46561 | 3.0922 | 86.6881 | 48.3758 | 1.3863 | 0.15967 | 452.7355 | 29.01 | 40.43
2021-01-18 10:45 | 2.212 | 1.619 | 0.46792 | 2.9475 | 81.5438 | 53.7896 | 1.3869 | 0.21058 | 453.5029 | 29.05 | 41.53
2021-01-18 10:50 | 2.5559 | 1.4681 | 0.44088 | 2.6912 | 100.4856 | 69.3572 | 1.3873 | 0.20337 | 453.8821 | 29.07 | 42.1
2021-01-18 10:55 | 3.2036 | 1.788 | 0.49926 | 3.242 | 102.911 | 80.5877 | 1.3869 | 0.21784 | 451.8259 | 29.12 | 41.36
2021-01-18 11:00 | 3.9278 | 2.5277 | 0.63288 | 4.5075 | 104.3139 | 64.6954 | 1.3868 | 0.25412 | 451.7528 | 29.2 | 40.92
2021-01-18 11:05 | 4.3957 | 1.9121 | 0.5198 | 3.4528 | 106.8883 | 50.2681 | 1.3933 | 0.24673 | 451.9293 | 29.25 | 39.46
2021-01-18 11:10 | 4.5088 | 1.5617 | 0.47167 | 2.8655 | 87.6668 | 41.1103 | 1.4002 | 0.34097 | 452.5716 | 29.25 | 38.83
2021-01-18 11:15 | 4.151 | 1.7568 | 0.52773 | 3.2206 | 81.6792 | 47.6284 | 1.3922 | 0.34804 | 453.8473 | 29.26 | 37.52
2021-01-18 11:20 | 3.8967 | 1.8056 | 0.48805 | 3.2537 | 83.3971 | 50.5988 | 1.3993 | 0.36251 | 452.2744 | 29.29 | 37.21
2021-01-18 11:25 | 3.1784 | 1.8099 | 0.48049 | 3.2548 | 83.7667 | 37.6014 | 1.3943 | 0.305 | 452.0043 | 29.33 | 41.03
2021-01-18 11:30 | 3.3498 | 1.9293 | 0.51276 | 3.47 | 96.646 | 65.1304 | 1.3896 | 0.31283 | 451.166 | 29.34 | 45.38
2021-01-18 11:35 | 3.3035 | 1.9041 | 0.51777 | 3.4365 | 104.0747 | 63.4267 | 1.3934 | 0.34836 | 453.3756 | 29.3 | 39.62
2021-01-18 11:40 | 2.954 | 1.8522 | 0.5377 | 3.3768 | 95.7794 | 62.96 | 1.3964 | 0.32 | 452.2984 | 29.38 | 44.5
2021-01-18 11:45 | 2.6255 | 1.4455 | 0.46493 | 2.6807 | 100.8187 | 25.5106 | 1.3978 | 0.27664 | 451.3317 | 29.38 | 46.85
2021-01-18 11:50 | 2.8436 | 1.6116 | 0.53221 | 3.0026 | 108.3968 | 76.4061 | 1.4057 | 0.27678 | 450.5578 | 29.4 | 47.97
2021-01-18 11:55 | 3.9503 | 1.8305 | 0.47742 | 3.2854 | 106.1443 | 54.1935 | 1.4048 | 0.42217 | 450.8076 | 29.43 | 46.33
2021-01-18 12:00 | 4.1782 | 1.9609 | 0.42701 | 3.4328 | 110.9053 | 79.6403 | 1.4043 | 0.42929 | 449.8827 | 29.46 | 45.38
2021-01-18 12:05 | 4.4206 | 1.83 | 0.41658 | 3.2217 | 110.5382 | 88.5957 | 1.4117 | 0.36384 | 450.9126 | 29.49 | 45.47
2021-01-18 12:10 | 3.9889 | 1.3702 | 0.43557 | 2.5359 | 108.038 | 53.3308 | 1.4049 | 0.28389 | 450.2047 | 29.51 | 46.24
2021-01-18 12:15 | 3.6197 | 1.5672 | 0.45447 | 2.8567 | 100.7398 | 69.4779 | 1.4051 | 0.33489 | 450.1819 | 29.49 | 46.57
2021-01-18 12:20 | 3.746 | 1.9027 | 0.50876 | 3.4253 | 87.7427 | 48.7437 | 1.4337 | 0.32023 | 451.4106 | 29.46 | 45.91
2021-01-18 12:25 | 2.8032 | 2.1158 | 0.52972 | 3.775 | 82.6284 | 35.4937 | 1.4047 | 0.32024 | 450.293 | 29.5 | 45.88
2021-01-18 12:30 | 2.6758 | 2.2279 | 0.52973 | 3.9447 | 78.0634 | 50.3161 | 1.4047 | 0.34936 | 450.6414 | 29.61 | 45.64
2021-01-18 12:35 | 2.4213 | 1.7172 | 0.43557 | 3.0678 | 78.7875 | 52.6881 | 1.4049 | 0.29845 | 450.5215 | 29.65 | 45.85
2021-01-18 12:40 | 3.0734 | 2.1135 | 0.52388 | 3.7636 | 87.6364 | 62.6412 | 1.4132 | 0.29866 | 449.1669 | 29.65 | 47.48
2021-01-18 12:45 | 3.6485 | 2.1361 | 0.56388 | 3.8382 | 93.0129 | 72.9591 | 1.4209 | 0.24775 | 449.4216 | 29.73 | 48.03
2021-01-18 12:50 | 2.7062 | 1.8405 | 0.47195 | 3.2931 | 109.3089 | 64.2741 | 1.4145 | 0.21145 | 449.0479 | 29.79 | 49.34
2021-01-18 12:55 | 2.5276 | 1.6655 | 0.43842 | 2.9913 | 101.065 | 52.33 | 1.4146 | 0.19688 | 449.0296 | 29.78 | 49.54
2021-01-18 13:00 | 3.6386 | 1.6327 | 0.46992 | 2.9727 | 100.9808 | 68.2057 | 1.422 | 0.26253 | 448.5156 | 29.8 | 49.61
2021-01-18 13:05 | 3.3066 | 1.9818 | 0.51817 | 3.5559 | 109.612 | 73.4661 | 1.4293 | 0.27711 | 446.9092 | 29.83 | 49.54
2021-01-18 13:10 | 3.0642 | 2.0366 | 0.55596 | 3.6777 | 115.0907 | 69.2301 | 1.4294 | 0.25525 | 447.9021 | 29.85 | 49.57
2021-01-18 13:15 | 2.2215 | 1.9928 | 0.52239 | 3.5749 | 102.4869 | 72.4374 | 1.4221 | 0.17503 | 447.8423 | 29.89 | 49.46
2021-01-18 13:20 | 2.9109 | 1.7984 | 0.45944 | 3.2161 | 107.898 | 70.9855 | 1.4294 | 0.18961 | 447.8665 | 29.88 | 49.44
2021-01-18 13:25 | 3.1918 | 1.5219 | 0.44476 | 2.7777 | 105.7852 | 48.996 | 1.444 | 0.26254 | 446.8216 | 29.88 | 49.47
2021-01-18 13:30 | 3.4474 | 1.5741 | 0.42801 | 2.8387 | 104.5458 | 68.9686 | 1.4441 | 0.26255 | 447.8316 | 29.88 | 49.62
2021-01-18 13:35 | 4.2393 | 1.4948 | 0.43432 | 2.7255 | 107.9228 | 66.6741 | 1.4368 | 0.28445 | 448.3404 | 29.87 | 49.78
2021-01-18 13:40 | 3.3328 | 1.5989 | 0.45952 | 2.9103 | 108.7952 | 70.5279 | 1.4369 | 0.27717 | 448.3084 | 29.88 | 49.84
2021-01-18 13:45 | 2.8475 | 1.3647 | 0.44272 | 2.5367 | 116.8613 | 78.9529 | 1.4368 | 0.25528 | 447.256 | 29.9 | 49.7
2021-01-18 13:50 | 3.0648 | 1.6003 | 0.42806 | 2.881 | 132.2752 | 72.0833 | 1.4369 | 0.26988 | 446.6602 | 29.93 | 49.78
2021-01-18 13:55 | 3.3204 | 1.6264 | 0.42809 | 2.9211 | 123.8249 | 70.1572 | 1.437 | 0.29908 | 447.6389 | 29.95 | 49.88
2021-01-18 14:00 | 3.0393 | 1.6838 | 0.36722 | 2.9483 | 116.0761 | 59.8157 | 1.437 | 0.32095 | 448.1468 | 29.97 | 49.73
2021-01-18 14:05 | 3.448 | 1.7906 | 0.45325 | 3.198 | 102.3864 | 52.317 | 1.4443 | 0.35013 | 448.666 | 29.97 | 49.73
2021-01-18 14:10 | 2.6817 | 1.6646 | 0.39869 | 2.9503 | 104.6108 | 64.7688 | 1.4588 | 0.34283 | 447.7085 | 29.97 | 49.62
2021-01-18 14:15 | 3.1159 | 1.7933 | 0.47004 | 3.2189 | 95.1419 | 56.6786 | 1.4734 | 0.34283 | 450.2965 | 29.97 | 49.65
2021-01-18 14:20 | 3.8571 | 1.8415 | 0.49949 | 3.3201 | 97.1078 | 63.4716 | 1.481 | 0.40854 | 447.0723 | 30 | 49.91
2021-01-18 14:25 | 4.2275 | 1.5293 | 0.45122 | 2.7955 | 106.2527 | 63.0323 | 1.4591 | 0.37936 | 447.5166 | 30.05 | 49.77
2021-01-18 14:30 | 4.4823 | 1.6797 | 0.41338 | 2.9881 | 101.6602 | 79.0827 | 1.4662 | 0.45225 | 448.1306 | 30.03 | 49.49
2021-01-18 14:35 | 4.7381 | 1.9194 | 0.49735 | 3.4395 | 117.7285 | 85.2901 | 1.459 | 0.4231 | 447.5498 | 30.05 | 49.6
2021-01-18 14:40 | 4.8404 | 2.2234 | 0.54564 | 3.9538 | 124.4059 | 78.5302 | 1.459 | 0.45959 | 448.0179 | 30.07 | 49.65
2021-01-18 14:45 | 4.7128 | 2.1838 | 0.53306 | 3.8784 | 115.1412 | 48.4719 | 1.4664 | 0.43772 | 447.9792 | 30.09 | 49.64
2021-01-18 14:50 | 5.0323 | 1.8457 | 0.49321 | 3.3223 | 119.7743 | 94.5361 | 1.4737 | 0.42314 | 447.4285 | 30.1 | 49.7
2021-01-18 14:55 | 3.9211 | 1.8183 | 0.5058 | 3.2929 | 113.5812 | 69.5016 | 1.4956 | 0.40855 | 446.381 | 30.11 | 49.65
2021-01-18 15:00 | 3.8317 | 1.8744 | 0.51839 | 3.3916 | 125.4244 | 62.186 | 1.5102 | 0.36478 | 447.8746 | 30.15 | 49.55
2021-01-18 15:05 | 4.6109 | 1.9018 | 0.57716 | 3.4924 | 126.5603 | 90.2659 | 1.4956 | 0.35019 | 446.832 | 30.15 | 49.58
2021-01-18 15:10 | 4.5342 | 1.9867 | 0.57925 | 3.6266 | 141.3945 | 102.1477 | 1.4591 | 0.35019 | 448.3207 | 30.2 | 49.4
2021-01-18 15:15 | 4.3937 | 1.9333 | 0.53098 | 3.4944 | 147.9137 | 116.4222 | 1.4591 | 0.35019 | 446.7946 | 30.18 | 49.46
2021-01-18 15:20 | 4.2278 | 1.6869 | 0.49532 | 3.0811 | 147.2545 | 88.8268 | 1.4592 | 0.37209 | 447.2684 | 30.2 | 49.48
2021-01-18 15:25 | 4.9814 | 1.7951 | 0.47224 | 3.2259 | 137.3548 | 95.1224 | 1.4665 | 0.39398 | 447.7662 | 30.21 | 49.48
2021-01-18 15:30 | 4.0994 | 1.5812 | 0.4218 | 2.8456 | 126.5946 | 66.2346 | 1.4662 | 0.37932 | 446.3538 | 30.21 | 49.06
2021-01-18 15:35 | 3.6908 | 1.7017 | 0.48686 | 3.0953 | 110.7085 | 91.5214 | 1.4662 | 0.35744 | 446.3948 | 30.18 | 49.16
2021-01-18 15:40 | 4.2529 | 1.9345 | 0.50996 | 3.4753 | 122.1666 | 65.0527 | 1.459 | 0.33557 | 446.3465 | 30.2 | 49.2
2021-01-18 15:45 | 4.1254 | 1.8675 | 0.49529 | 3.36 | 121.4567 | 90.4462 | 1.4591 | 0.32829 | 446.8302 | 30.21 | 49.27
2021-01-18 15:50 | 4.2403 | 1.9237 | 0.50159 | 3.4503 | 130.0303 | 103.8423 | 1.4591 | 0.36477 | 446.2941 | 30.22 | 49.26
2021-01-18 15:55 | 4.3688 | 2.7908 | 0.62342 | 4.9013 | 137.5328 | 119.0561 | 1.4885 | 0.4305 | 445.6133 | 30.28 | 49.47
2021-01-18 16:00 | 5.3643 | 2.3878 | 0.50999 | 4.1681 | 156.4032 | 128.1102 | 1.4956 | 0.45232 | 445.1382 | 30.3 | 49.05
2021-01-18 16:05 | 7.2166 | 2.021 | 0.50582 | 3.6058 | 147.2854 | 93.4354 | 1.4738 | 0.57637 | 447.1293 | 30.34 | 49.04
2021-01-18 16:10 | 6.1435 | 2.2811 | 0.51629 | 4.0149 | 136.8069 | 113.2445 | 1.4664 | 0.52528 | 445.0752 | 30.34 | 48.96
2021-01-18 16:15 | 5.6067 | 1.9962 | 0.44491 | 3.5047 | 142.9083 | 109.784 | 1.4517 | 0.47418 | 447.2468 | 30.29 | 48.96
2021-01-18 16:20 | 5.8112 | 1.9373 | 0.46171 | 3.4313 | 147.1418 |  | 1.4664 | 0.47419 | 445.2092 | 30.26 | 49.1
2021-01-18 16:25 | 5.0578 | 2.0031 | 0.54567 | 3.6182 | 125.1365 | 62.3588 | 1.5029 | 0.51068 | 447.2393 | 30.28 | 49.1
2021-01-18 16:30 | 4.2146 | 1.799 | 0.52465 | 3.2822 | 109.4661 | 71.4789 | 1.4882 | 0.37205 | 446.2604 | 30.26 | 49.02
2021-01-18 16:35 | 3.6654 | 1.7155 | 0.46799 | 3.0976 | 99.0152 | 71.3878 | 1.459 | 0.27721 | 446.7435 | 30.28 | 48.99
2021-01-18 16:40 | 4.1631 | 1.7578 | 0.44276 | 3.1371 | 96.5937 | 71.084 | 1.4662 | 0.30636 | 446.2876 | 30.27 | 48.78
2021-01-18 16:45 | 4.7503 | 1.7221 | 0.45323 | 3.0908 | 97.0187 | 78.2932 | 1.4734 | 0.34282 | 446.2625 | 30.3 | 48.6
2021-01-18 16:50 | 4.5446 | 1.4164 | 0.42792 | 2.599 | 111.9912 | 110.7964 | 1.4802 | 0.41563 | 447.4939 | 30.26 | 48.02
2021-01-18 16:55 | 3.7781 | 1.4025 | 0.49497 | 2.6447 | 110.9426 | 74.234 | 1.4727 | 0.30621 | 447.163 | 30.18 | 47.89
2021-01-18 17:00 | 4.5304 | 1.6759 | 0.50957 | 3.0805 | 104.1966 | 84.3905 | 1.4652 | 0.35718 | 446.7176 | 30.18 | 47.52
2021-01-18 17:05 | 3.636 | 1.6398 | 0.44653 | 2.9601 | 105.1758 | 79.507 | 1.4502 | 0.30607 | 446.8071 | 30.21 | 46.76
2021-01-18 17:10 | 3.5582 | 1.3439 | 0.34787 | 2.4058 | 82.7636 | 58.0019 | 1.4496 | 0.32053 | 448.0641 | 30.17 | 46.05
2021-01-18 17:15 | 3.3151 | 1.1564 | 0.34779 | 2.1224 | 71.8104 | 35.181 | 1.4566 | 0.28404 | 449.2461 | 30.14 | 45.62
2021-01-18 17:20 | 3.3651 | 1.2968 | 0.39377 | 2.3815 | 74.4709 | 75.7456 | 1.4562 | 0.26939 | 448.3863 | 30.11 | 45.02
2021-01-18 17:25 | 3.2624 | 1.2063 | 0.38531 | 2.2323 | 94.2022 | 96.0577 | 1.4559 | 0.24022 | 449.0195 | 30.1 | 44.54
2021-01-18 17:30 | 2.5347 | 1.065 | 0.31604 | 1.9485 | 87.3251 | 49.6642 | 1.4405 | 0.24736 | 449.3028 | 30.07 | 43.4
2021-01-18 17:35 | 2.2793 | 1.1207 | 0.32432 | 2.0401 | 85.621 | 57.4237 | 1.4401 | 0.2182 | 450.5208 | 30.03 | 42.89
2021-01-18 17:40 | 4.2142 | 1.1042 | 0.32845 | 2.023 | 78.1011 | 58.0055 | 1.4617 | 0.30544 | 450.1307 | 29.99 | 42.63
2021-01-18 17:45 | 5.9319 | 1.0289 | 0.32003 | 1.8951 | 75.9993 | 58.5652 | 1.4906 | 0.50897 | 450.2717 | 29.95 | 42.31
2021-01-18 17:50 | 3.8819 | 0.80363 | 0.28652 | 1.5204 | 72.6692 | 50.4621 | 1.4613 | 0.41439 | 449.9198 | 29.88 | 42.15
2021-01-18 17:55 | 2.6858 | 0.95517 | 0.30328 | 1.7695 | 73.8777 | 68.8779 | 1.4469 | 0.30537 | 449.4159 | 29.84 | 42.47
2021-01-18 18:00 | 2.1261 | 1.0222 | 0.30543 | 1.8702 | 89.5258 | 56.9747 | 1.4471 | 0.48723 | 448.8244 | 29.83 | 42.94
2021-01-18 18:05 | 1.8209 | 0.88044 | 0.29293 | 1.6425 | 95.3175 | 84.815 | 1.4619 | 0.34185 | 450.3348 | 29.81 | 43.4
2021-01-18 18:10 | 1.8466 | 0.76453 | 0.23647 | 1.4084 | 79.3164 | 37.3098 | 1.4622 | 0.26188 | 451.4085 | 29.74 | 43.94
2021-01-18 18:15 | 2.127 | 0.71681 | 0.23649 | 1.3352 | 66.0667 | 38.4948 | 1.455 | 0.2037 | 450.9856 | 29.65 | 44.36
2021-01-18 18:20 | 2.9807 | 0.63906 | 0.25536 | 1.2349 | 50.5647 | 43.2582 | 1.4697 | 0.19645 | 449.4913 | 29.57 | 44.84
2021-01-18 18:25 | 2.4463 | 0.74576 | 0.30358 | 1.4488 | 52.9832 | 56.3469 | 1.4628 | 0.18195 | 450.4755 | 29.53 | 45.55
2021-01-18 18:30 | 2.1154 | 0.63113 | 0.23871 | 1.204 | 47.8334 | 33.1939 | 1.4558 | 0.14558 | 450.4315 | 29.51 | 45.99
2021-01-18 18:35 | 1.746 | 0.64348 | 0.24502 | 1.2314 | 44.3812 | 30.5968 | 1.4559 | 0.16743 | 449.9624 | 29.45 | 46.35
2021-01-18 18:40 | 1.2744 | 0.7022 | 0.31621 | 1.3926 | 39.7409 | 42.3509 | 1.4559 | 0.16743 | 449.9918 | 29.44 | 46.3
2021-01-18 18:45 | 1.0323 | 0.65167 | 0.31412 | 1.313 | 42.1886 | 28.853 | 1.4486 | 0.13831 | 451.1429 | 29.36 | 46.56
2021-01-18 18:50 | 1.7078 | 0.80061 | 0.25131 | 1.4806 | 47.8488 | 55.4447 | 1.4487 | 0.26207 | 451.1708 | 29.33 | 46.73
2021-01-18 18:55 | 1.9116 | 0.68309 | 0.22826 | 1.2732 | 32.3294 | 36.4687 | 1.4486 | 0.32758 | 451.2957 | 29.26 | 46.81
2021-01-18 19:00 | 1.8222 | 0.46444 | 0.21776 | 0.92968 | 24.476 | 34.8332 | 1.4484 | 0.24747 | 450.4436 | 29.17 | 46.76
2021-01-18 19:05 | 1.5421 | 0.41669 | 0.23873 | 0.87745 | 25.2746 | 37.866 | 1.4486 | 0.17471 | 450.9766 | 29.12 | 47.23
2021-01-18 19:10 | 1.5422 | 0.47138 | 0.2597 | 0.98224 | 27.9381 | 24.6141 | 1.4488 | 0.13832 | 451.0114 | 29.07 | 47.58
2021-01-18 19:15 | 1.0069 | 0.55885 | 0.24714 | 1.1038 | 21.0872 | 24.1463 | 1.4416 | 0.11649 | 452.6259 | 29.02 | 47.84
2021-01-18 19:20 | 1.3003 | 0.56028 | 0.22204 | 1.0809 | 19.9373 | 24.1695 | 1.449 | 0.15291 | 452.6631 | 28.96 | 48.29
2021-01-18 19:25 | 1.2111 | 0.5193 | 0.18434 | 0.98034 | 14.3287 | 20.9882 | 1.4418 | 0.13835 | 452.7562 | 28.89 | 48.55
2021-01-18 19:30 | 1.1984 | 0.38949 | 0.19482 | 0.79394 | 21.6111 | 15.6041 | 1.4418 | 0.1602 | 451.2205 | 28.86 | 48.73
2021-01-18 19:35 | 1.1729 | 0.4428 | 0.19063 | 0.87146 | 19.5208 | 45.5281 | 1.4491 | 0.13108 | 451.2716 | 28.82 | 48.89
2021-01-18 19:40 | 1.1092 | 0.55078 | 0.19483 | 1.0391 | 20.5618 | 9.6384 | 1.4419 | 0.11652 | 452.8183 | 28.82 | 48.98
2021-01-18 19:45 | 1.1858 | 0.46748 | 0.1781 | 0.89258 | 26.0326 | 44.0676 | 1.4421 | 0.11653 | 452.3193 | 28.76 | 49.52
2021-01-18 19:50 | 1.7982 | 0.45799 | 0.17394 | 0.87597 | 23.8945 | 26.6186 | 1.4424 | 0.14569 | 454.3709 | 28.73 | 50.03
2021-01-18 19:55 | 3.0225 | 0.34452 | 0.15927 | 0.68946 | 28.7203 | 34.3011 | 1.4496 | 0.15298 | 451.2822 | 28.66 | 50.28
2021-01-18 20:00 | 2.487 | 0.28028 | 0.1488 | 0.57842 | 26.9365 | 35.8439 | 1.4497 | 0.15299 | 453.9827 | 28.58 | 50.67
2021-01-18 20:05 | 1.3522 | 0.20649 | 0.12367 | 0.44019 | 21.6352 | 15.7773 | 1.45 | 0.10201 | 452.4163 | 28.52 | 51.35
2021-01-18 20:10 | 1.0463 | 0.20381 | 0.13209 | 0.44451 | 18.5275 | 23.3253 | 1.4577 | 0.058308 | 453.9205 | 28.48 | 52.14
2021-01-18 20:15 | 0.66358 | 0.21614 | 0.13001 | 0.46132 | 22.5618 | 8.2693 | 1.4433 | 0.072892 | 453.4612 | 28.41 | 52.59
2021-01-18 20:20 | 0.68915 | 0.33518 | 0.1405 | 0.65428 | 21.7056 | 25.861 | 1.4434 | 0.065607 | 453.9541 | 28.41 | 52.75
2021-01-18 20:25 | 0.68913 | 0.28729 | 0.1384 | 0.57877 | 20.0614 | 13.8541 | 1.4433 | 0.065605 | 453.5037 | 28.37 | 52.81
2021-01-18 20:30 | 1.0464 | 0.19699 | 0.11952 | 0.42147 | 12.7097 | 25.4807 | 1.4505 | 0.051023 | 454.1946 | 28.28 | 52.9
2021-01-18 20:35 | 2.1949 | 0.26129 | 0.13211 | 0.53262 | 7.8915 | 30.2388 | 1.4505 | 0.1312 | 453.2274 | 28.22 | 53.16
2021-01-18 20:40 | 1.7611 | 0.35569 | 0.1405 | 0.68362 | 16.2736 | 9.9337 | 1.4506 | 0.094763 | 454.2844 | 28.2 | 53.32
2021-01-18 20:45 | 1.289 | 0.35298 | 0.13841 | 0.67947 | 20.522 | 22.7273 | 1.4507 | 0.087479 | 453.2421 | 28.18 | 53.54
2021-01-18 20:50 | 1.0082 | 0.30782 | 0.13631 | 0.60815 | 26.157 | 38.6842 | 1.4506 | 0.087476 | 453.7937 | 28.17 | 53.49
2021-01-18 20:55 | 0.66366 | 0.28868 | 0.12583 | 0.56623 | 28.5168 | 43.5563 | 1.458 | 0.05832 | 452.2955 | 28.11 | 53.8
2021-01-18 21:00 | 0.4594 | 0.171 | 0.10485 | 0.36696 | 24.0421 | 15.3441 | 1.4578 | 0.051024 | 453.5865 | 27.98 | 53.92
2021-01-18 21:05 | 0.4084 | 0.14502 | 0.10695 | 0.32925 | 23.0029 | 18.0715 | 1.4653 | 0.058319 | 452.1877 | 27.84 | 54.6
2021-01-18 21:10 | 0.43387 | 0.10944 | 0.092263 | 0.26001 | 13.1387 | 29.3503 | 1.4578 | 0.058313 | 454.9806 | 27.71 | 54.79
2021-01-18 21:15 | 0.52318 | 0.15458 | 0.09226 | 0.3271 | 16.3744 | -1.4394 | 1.4651 | 0.10933 | 454.5929 | 27.63 | 54.96
2021-01-18 21:20 | 1.1101 | 0.15046 | 0.10274 | 0.33338 | 17.9557 | 16.3224 | 1.4796 | 0.14577 | 454.1551 | 27.59 | 54.94
2021-01-18 21:25 | 0.86758 | 0.19969 | 0.1174 | 0.42139 | 19.4337 | 31.9982 | 1.4867 | 0.12389 | 453.741 | 27.55 | 54.78
2021-01-18 21:30 | 0.80379 | 0.18464 | 0.098536 | 0.38156 | 18.056 | 11.6563 | 1.494 | 0.10203 | 453.2256 | 27.54 | 54.85
2021-01-18 21:35 | 0.85475 | 0.20924 | 0.10272 | 0.42345 | 39.8337 | 160.1922 | 1.4866 | 0.11659 | 397.2534 | 27.5 | 54.72
2021-01-18 21:40 | 0.80381 | 0.13814 | 0.096441 | 0.30819 | 324.086 | 405.3449 | 1.4867 | 0.087455 | 279.8733 | 27.45 | 55.19
2021-01-18 21:45 | 0.76544 | 0.17368 | 0.094333 | 0.36056 | 204.1992 | 64.8073 | 1.4865 | 0.11659 | 278.9145 | 27.39 | 55.06
2021-01-18 21:50 | 0.81641 | 0.25025 | 0.10481 | 0.4884 | 91.4277 | 36.4425 | 1.4792 | 0.12387 | 278.3552 | 27.45 | 54.67
2021-01-18 21:55 | 0.62496 | 0.1504 | 0.10269 | 0.33323 | 36.4673 | 19.0806 | 1.4789 | 0.080138 | 280.5058 | 27.44 | 54.28
2021-01-18 22:00 | 0.59936 | 0.26657 | 0.098486 | 0.5071 | 15.2109 | 20.4546 | 1.486 | 0.094693 | 279.5316 | 27.41 | 53.93
2021-01-18 22:05 | 0.65031 | 0.25561 | 0.10476 | 0.49448 | 6.8754 | 21.9421 | 1.4858 | 0.058267 | 279.52 | 27.45 | 53.56
2021-01-18 22:10 | 0.48451 | 0.21322 | 0.092185 | 0.42112 | 1.989 | 7.9969 | 1.4857 | 0.05098 | 279.0239 | 27.44 | 53.41
2021-01-18 22:15 | 0.4335 | 0.19272 | 0.092184 | 0.38759 | -3.672 | 26.4588 | 1.4857 | 0.05098 | 279.0563 | 27.41 | 53.46
2021-01-18 22:20 | 0.44623 | 0.16674 | 0.096369 | 0.35196 | 0.99955 | 14.2691 | 1.4929 | 0.065542 | 280.1757 | 27.35 | 53.51
2021-01-18 22:25 | 0.40797 | 0.10524 | 0.075417 | 0.23673 | -0.59156 | 11.1988 | 1.4856 | 0.058258 | 280.2282 | 27.3 | 53.61
2021-01-18 22:30 | 0.36974 | 0.13257 | 0.0838 | 0.28702 | 0.28559 | 17.5332 | 1.4929 | 0.05826 | 279.712 | 27.28 | 53.77
2021-01-18 22:35 | 0.34424 | 0.075172 | 0.077516 | 0.19484 | 3.3863 | 23.5919 | 1.4856 | 0.058261 | 279.7478 | 27.24 | 53.91
2021-01-18 22:40 | 0.34421 | 0.065599 | 0.075415 | 0.17597 | 2.2846 | 6.5477 | 1.5001 | 0.043692 | 280.3504 | 27.18 | 53.89
2021-01-18 22:45 | 0.31869 | 0.049196 | 0.058651 | 0.13406 | -1.2034 | 19.3458 | 1.5073 | 0.05097 | 279.903 | 27.12 | 53.87
2021-01-18 22:50 | 0.30593 | 0.064226 | 0.056555 | 0.155 | 0.071385 | 13.4815 | 1.5072 | 0.036406 | 279.4229 | 27.08 | 53.92
2021-01-18 22:55 | 0.31864 | 0.05192 | 0.075397 | 0.15498 | -0.61179 | 8.6772 | 1.5143 | 0.050962 | 280.5294 | 27.06 | 53.62
2021-01-18 23:00 | 0.30588 | 0.060115 | 0.079582 | 0.17382 | 4.3333 | 15.8242 | 1.5142 | 0.058239 | 280.0363 | 27.04 | 53.55
2021-01-18 23:05 | 0.30587 | 0.058748 | 0.079579 | 0.16963 | 2.8038 | 12.0921 | 1.5215 | 0.050958 | 280.5879 | 27.02 | 53.54
2021-01-18 23:10 | 0.47159 | 0.084713 | 0.073303 | 0.20106 | 7.0356 | 17.7929 | 1.5289 | 0.058242 | 279.5335 | 27 | 53.82
2021-01-18 23:15 | 0.42069 | 0.079264 | 0.081697 | 0.2032 | 11.7182 | 1.693 | 1.5292 | 0.050973 | 279.9911 | 27.01 | 54.36
2021-01-18 23:20 | 0.36971 | 0.1107 | 0.09008 | 0.25767 | 4.4672 | 17.2873 | 1.5147 | 0.043693 | 279.9618 | 27.03 | 54.4
2021-01-18 23:25 | 0.357 | 0.13805 | 0.081708 | 0.29331 | 8.8638 | 3.0498 | 1.5221 | 0.072828 | 279.9086 | 27.06 | 54.55
2021-01-18 23:30 | 0.39529 | 0.10526 | 0.088003 | 0.24934 | 2.6319 | -1.1221 | 1.5296 | 0.087403 | 279.3793 | 27.03 | 54.96
2021-01-18 23:35 | 0.3443 | 0.1285 | 0.083815 | 0.28078 | 4.9375 | 15.3021 | 1.5296 | 0.065554 | 280.4587 | 26.99 | 55.17
2021-01-18 23:40 | 0.35709 | 0.090232 | 0.077538 | 0.21794 | 4.8564 | 9.1721 | 1.5225 | 0.080131 | 279.9477 | 26.94 | 55.65
2021-01-18 23:45 | 0.45913 | 0.10664 | 0.079635 | 0.2431 | 7.2134 | 12.9882 | 1.5225 | 0.094703 | 280.5034 | 26.9 | 55.85
2021-01-18 23:50 |  | 0.16269 | 0.077536 | 0.32691 | 7.0498 | 15.2933 | 1.5225 | 0.080129 | 280.5368 | 26.88 | 55.77
2021-01-18 23:55 | 0.44637 | 0.14082 | 0.075443 | 0.29129 | 10.9781 | 4.3872 | 1.5152 | 0.080132 | 280.5363 | 26.87 | 55.9
2021-01-19 | 0.36985 | 0.12988 | 0.079634 | 0.27872 | 4.8667 | 11.5903 | 1.4715 | 0.072848 | 278.9956 | 26.83 | 56.05
2021-01-19 00:05 | 0.40812 | 0.13125 | 0.075445 | 0.27663 | 17.3247 | 19.3245 | 1.3914 | 0.065564 | 279.5514 | 26.79 | 56.25
2021-01-19 00:10 | 0.42097 | 0.13949 | 0.079654 | 0.29346 | 12.0116 | 12.0014 |  |  | 280.5406 | 26.79 | 56.86
2021-01-19 00:15 | 0.3827 | 0.08752 | 0.088039 | 0.22219 | 4.8985 | 4.225 |  |  | 278.9645 | 26.79 | 56.86
2021-01-19 00:20 | 0.33172 | 0.084798 | 0.085956 | 0.21803 | 12.8912 | 18.2498 |  |  | 278.9396 | 26.77 | 57.36
2021-01-19 00:25 | 0.39552 | 0.095742 | 0.081764 | 0.22852 | 13.953 | 13.6162 |  |  | 279.4967 | 26.73 | 57.55
2021-01-19 00:30 | 0.42103 | 0.12036 | 0.069184 | 0.25368 | 17.617 | 14.2692 |  |  | 278.4693 | 26.71 | 57.57
2021-01-19 00:35 | 0.39561 | 0.095764 | 0.073395 | 0.21809 | 23.1345 | 30.8936 |  |  | 279.9761 | 26.71 | 58.26
2021-01-19 00:40 | 0.37014 | 0.084831 | 0.060822 | 0.19085 | 12.9473 | 18.0935 |  |  | 279.975 | 26.67 | 58.78
2021-01-19 00:45 | 0.3447 | 0.12043 | 0.054543 | 0.24125 | 19.1907 | 7.0165 |  |  | 280.4329 | 26.67 | 59.45
2021-01-19 00:50 | 0.35767 | 0.10681 | 0.060871 | 0.22459 | 22.2573 | 23.4938 |  |  | 279.765 | 26.65 | 61.13
2021-01-19 00:55 | 0.31954 | 0.11236 | 0.069309 | 0.24153 | 23.375 | 17.7306 |  |  | 279.6155 | 26.63 | 62.88
2021-01-19 01:00 | 0.3068 | 0.098667 | 0.067218 | 0.21846 | 20.3306 | 21.4249 |  |  | 280.6356 | 26.62 | 63.3
2021-01-19 01:05 |  |  |  |  | 21.3152 | 7.8653 |  |  | 279.5686 | 26.6 | 63.74
2021-01-19 01:10 | 0.29414 | 0.080887 | 0.060942 | 0.18493 | 11.602 | 17.0654 |  |  | 278.9805 | 26.58 | 64.64
2021-01-19 01:15 | 0.34527 | 0.074025 | 0.071443 | 0.18491 | 2.4348 | 18.8234 |  |  | 279.0246 | 26.56 | 64.46
2021-01-19 01:20 | 0.37076 | 0.056192 | 0.060923 | 0.14706 | 12.9382 | 3.1911 |  |  | 279.1136 | 26.53 | 63.96
2021-01-19 01:25 | 0.35804 | 0.050719 | 0.060934 | 0.13868 | 9.8717 | 23.4056 |  |  | 278.5575 | 26.51 | 64.54
2021-01-19 01:30 | 0.30684 | 0.031522 | 0.069327 | 0.11554 | 5.1651 | 15.6384 |  |  | 279.1691 | 26.47 | 64.19
2021-01-19 01:35 | 0.28125 | 0.023298 | 0.05882 | 0.094531 | 10.6058 | 0.76705 |  |  | 280.2519 | 26.45 | 64.12
2021-01-19 01:40 | 0.26854 | 0.019192 | 0.058836 | 0.088254 | 11.9489 | 14.752 |  |  | 280.1733 | 26.45 | 64.91
2021-01-19 01:45 | 0.25575 | 0.01645 | 0.052532 | 0.079848 | 10.9156 | 24.8388 |  |  | 279.6782 | 26.42 | 65.01
2021-01-19 01:50 | 0.24296 | 0.019192 | 0.054633 | 0.08405 | 17.4627 | 19.3962 |  |  | 279.1564 | 26.42 | 64.98
2021-01-19 01:55 | 0.28139 | 0.027423 | 0.063052 | 0.10509 | 12.6678 | 10.0278 |  |  | 278.5666 | 26.42 | 65.64
2021-01-19 02:00 | 0.23026 | 0.028798 | 0.050448 | 0.09459 | 12.2088 | 11.1957 |  |  | 280.1057 | 26.42 | 65.99
2021-01-19 02:05 | 0.23024 | 0.04662 | 0.069359 | 0.14292 | 15.4411 | 18.5518 |  |  | 279.0475 | 26.46 | 65.55
2021-01-19 02:10 | 0.26864 | 0.043883 | 0.054653 | 0.11982 | 14.8392 | 15.7705 |  |  | 280.0525 | 26.47 | 65.86
2021-01-19 02:15 | 0.34545 | 0.14264 | 0.073583 | 0.29223 | 9.8773 | 13.6542 |  |  | 280.018 | 26.46 | 66.34
2021-01-19 02:20 | 0.31986 | 0.10012 | 0.054662 | 0.20814 | 18.6286 | 19.4782 |  |  | 278.9795 | 26.45 | 66.37
2021-01-19 02:25 | 0.29428 | 0.18791 | 0.098816 | 0.38685 | 14.5863 | 25.723 |  |  | 280.5583 | 26.43 | 66.58
2021-01-19 02:30 | 0.35826 | 0.20437 | 0.079895 | 0.39317 | 13.9928 | 13.1432 |  |  | 280.0207 | 26.44 | 66.58
2021-01-19 02:35 | 0.51172 | 0.23863 | 0.090392 | 0.45617 | 25.6064 | 23.4163 |  |  | 280.5928 | 26.44 | 66.1
2021-01-19 02:40 | 0.39661 | 0.24687 | 0.07358 | 0.45199 | 20.4599 | 14.9227 |  |  | 279.5065 | 26.46 | 66.21
2021-01-19 02:45 | 0.371 | 0.21668 | 0.084087 | 0.41623 | 11.4217 | 16.8255 |  |  | 279.5132 | 26.47 | 66.01
2021-01-19 02:50 | 0.38371 | 0.13848 | 0.079865 | 0.29004 | 17.579 | 15.3177 |  |  | 280.632 | 26.46 | 65.44
2021-01-19 02:55 | 0.3198 | 0.16181 | 0.067264 | 0.3153 | 17.6531 | 16.4865 |  |  | 280.894 | 26.44 | 65.97
2021-01-19 03:00 | 0.31974 | 0.15767 | 0.077759 | 0.31944 | 12.6669 | 24.7506 |  |  | 279.3999 | 26.41 | 65.55
2021-01-19 03:05 | 0.33245 | 0.15215 | 0.063032 | 0.29625 | 23.8954 | 5.6567 |  |  | 279.4976 | 26.38 | 64.96
2021-01-19 03:10 | 0.35804 | 0.10555 | 0.071441 | 0.23323 | 18.741 | 18.7205 |  |  | 280.5407 | 26.37 | 65.17
2021-01-19 03:15 | 0.34519 | 0.11375 | 0.071427 | 0.24579 | 11.8949 | 20.5579 |  |  | 280.1266 | 26.31 | 64.84
2021-01-19 03:20 | 0.35788 | 0.16305 | 0.09451 | 0.34444 | 18.1085 | 14.5911 |  |  | 280.1841 | 26.33 | 63.99
2021-01-19 03:25 | 0.34514 | 0.13566 | 0.088222 | 0.29617 | 15.8101 | 16.4851 |  |  | 280.097 | 26.38 | 64.21
2021-01-19 03:30 | 0.33235 | 0.13018 | 0.079818 | 0.27936 | 12.66 | 18.8878 |  |  | 280.1232 | 26.36 | 64.21
2021-01-19 03:35 | 0.31961 | 0.14801 | 0.096633 | 0.32561 | 23.4516 | 15.556 |  |  | 281.1396 | 26.36 | 64.56
2021-01-19 03:40 | 0.35806 | 0.1974 | 0.11767 | 0.42026 | 24.6752 | 14.4655 |  |  | 280.5206 | 26.38 | 65.24
2021-01-19 03:45 | 0.40937 | 0.44845 | 0.17658 | 0.86187 | 28.4308 | 41.6944 |  |  | 280.8215 | 26.5 | 65.9
2021-01-19 03:50 | 0.5245 | 0.35382 | 0.13453 | 0.67688 | 35.3591 | 24.3267 |  |  | 279.1468 | 26.61 | 65.45
2021-01-19 03:55 | 0.47336 | 0.29212 | 0.11352 | 0.5613 | 29.9368 | 17.1433 |  |  | 280.1976 | 26.59 | 65.7
2021-01-19 04:00 | 0.63989 | 0.52819 | 0.13669 | 0.94631 | 31.4107 | 36.1817 |  |  | 280.0499 | 26.65 | 66.38
2021-01-19 04:05 | 0.78081 | 0.67374 | 0.13461 | 1.1673 | 50.3814 | 48.5381 |  |  | 278.8363 | 26.77 | 66.44
2021-01-19 04:10 | 0.74245 | 0.63947 | 0.088344 | 1.0685 | 51.4694 | 42.7956 |  |  | 278.5217 | 26.83 | 66.41
2021-01-19 04:15 | 0.83217 | 1.017 | 0.13674 | 1.6956 | 55.3075 | 55.1846 |  |  | 279.9889 | 26.9 | 66.54
2021-01-19 04:20 | 0.85765 | 1.0566 | 0.17248 | 1.7921 | 67.0655 | 63.9114 |  |  | 279.4603 | 26.95 | 65.93
2021-01-19 04:25 | 1.0369 | 1.1335 | 0.16196 | 1.8973 | 80.317 | 82.4163 |  |  | 279.4318 | 26.98 | 65.82
2021-01-19 04:30 | 1.2288 | 1.0318 | 0.18298 | 1.7625 | 95.1258 | 86.3914 |  |  | 280.4519 | 27.04 | 65.32
2021-01-19 04:35 | 1.6638 | 1.1717 | 0.23134 | 2.0273 | 107.3028 | 90.4292 |  |  | 277.7777 | 27.12 | 64.81
2021-01-19 04:40 | 2.3424 | 1.4696 | 0.25871 | 2.5135 | 72.8274 |  |  |  | 338.4314 | 27.21 | 64.8
2021-01-19 04:45 | 3.3017 | 1.4912 | 0.33435 | 2.6223 |  |  |  |  | 436.2614 | 27.37 | 63.61
2021-01-19 04:50 | 3.7624 | 1.2676 | 0.30701 | 2.25 | 17.5884 | 61.2215 |  |  | 437.1979 | 27.45 | 63.28
2021-01-19 04:55 | 3.5569 | 1.34 | 0.33639 | 2.3883 | 56.0917 | 70.3808 |  |  | 435.1157 | 27.5 | 62.58
2021-01-19 05:00 | 3.0058 | 1.6083 | 0.40984 | 2.8752 | 76.9065 | 79.5669 |  |  | 435.6801 | 27.57 | 61.46
2021-01-19 05:05 | 4.1067 | 2.0421 | 0.50454 | 3.6327 | 106.5347 | 119.7275 |  |  | 436.5196 | 27.64 | 61.85
2021-01-19 05:10 | 4.5785 | 2.2471 | 0.57371 | 4.0181 | 146.7072 | 152.6312 |  |  | 433.9655 | 27.7 | 60.73
2021-01-19 05:15 | 3.5298 | 2.3567 | 0.56531 | 4.1778 | 160.6108 | 137.9997 |  |  | 434.9423 | 27.75 | 60.54
2021-01-19 05:20 | 2.8517 | 2.6129 | 0.57156 | 4.5767 | 148.4232 | 109.5168 |  |  | 434.2512 | 27.83 | 60.1
2021-01-19 05:25 | 3.5544 | 3.3635 | 0.70171 | 5.8616 | 138.1968 | 134.6884 |  |  | 434.2194 | 27.91 | 59.32
2021-01-19 05:30 | 5.1151 | 4.1427 | 0.96028 | 7.3124 | 161.1859 | 157.3905 |  |  | 435.5608 | 28.02 | 59.36
2021-01-19 05:35 | 4.3222 | 3.3654 | 0.91405 | 6.0727 | 197.8204 | 178.8026 |  |  | 433.2499 | 28.17 | 58.85
2021-01-19 05:40 | 4.2206 | 3.4784 | 0.86796 | 6.1997 | 199.7035 | 177.1527 |  |  | 433.5323 | 28.29 | 58.84
2021-01-19 05:45 | 5.1527 | 3.9433 | 0.90971 | 6.9563 | 194.6398 | 169.5593 |  |  | 433.5372 | 28.38 | 57.75
2021-01-19 05:50 | 6.3284 | 3.9717 | 0.96636 | 7.0544 | 212.8796 |  |  |  | 435.0424 | 28.45 | 57.3
2021-01-19 05:55 | 5.3552 | 3.6459 | 0.87157 | 6.4622 | 201.4999 | 106.2969 |  |  | 433.9625 | 28.56 | 56.22
2021-01-19 06:00 | 5.3798 | 3.963 | 0.9134 | 6.9881 | 194.3676 | 157.8617 |  |  | 434.4227 | 28.66 | 55.43
2021-01-19 06:05 | 5.9424 | 3.3372 | 0.77486 | 5.8902 | 189.7374 | 137.383 |  |  | 434.8192 | 28.73 | 55.35
2021-01-19 06:10 | 5.7107 | 3.0472 | 0.77043 | 5.4413 | 170.8857 | 160.3382 |  |  | 434.397 | 28.75 | 54.55
2021-01-19 06:15 | 5.2387 | 3.0929 | 0.76844 | 5.5093 | 187.5304 | 181.8675 |  |  | 434.2785 | 28.79 | 54.77
2021-01-19 06:20 | 7.7683 | 3.5858 | 0.8251 | 6.3236 | 193.1235 | 148.9772 |  |  | 434.6747 | 28.83 | 54.59
2021-01-19 06:25 | 8.5086 | 3.5608 | 0.83972 | 6.3 | 195.1611 | 174.9858 |  |  | 435.6863 | 28.88 | 54.22
2021-01-19 06:30 | 7.6407 | 3.6105 | 0.81252 | 6.3469 | 204.3113 | 189.3161 |  |  | 433.9817 | 28.94 | 54.31
2021-01-19 06:35 | 6.8737 | 3.2419 | 0.74529 | 5.7146 | 199.578 | 149.5659 |  |  | 435.502 | 28.99 | 54.02
2021-01-19 06:40 | 5.9537 | 3.3295 | 0.72009 | 5.8237 | 190.8256 | 161.8695 |  |  | 435.5091 | 28.99 | 53.98
2021-01-19 06:45 | 6.6686 | 3.7894 | 0.80609 | 6.6146 | 185.3402 | 178.8505 |  |  | 433.9233 | 29.03 | 53.63
2021-01-19 06:50 | 6.2738 | 3.5504 | 0.69917 | 6.1414 | 193.6465 | 146.3491 |  |  | 434.739 | 29.13 | 53.8
2021-01-19 06:55 | 7.0664 | 3.4273 | 0.71391 | 5.9675 | 182.8638 | 168.7463 |  |  | 434.1023 | 29.19 | 53.77
2021-01-19 07:00 | 5.7751 | 2.6106 | 0.62565 | 4.6273 | 174.7153 | 141.9964 |  |  | 433.5903 | 29.22 | 53.38
2021-01-19 07:05 | 6.1076 | 2.5244 | 0.58998 | 4.4595 | 161.1684 | 135.3172 |  |  | 434.0801 | 29.23 | 53.45
2021-01-19 07:10 | 5.4924 | 2.5756 | 0.5562 | 4.5042 | 159.5917 | 140.1664 |  |  | 433.6748 | 29.25 | 52.58
2021-01-19 07:15 | 5.1993 | 2.5349 | 0.4996 | 4.3851 | 152.919 | 124.6203 |  |  | 433.5882 | 29.27 | 52.84
2021-01-19 07:20 | 6.7837 | 2.7582 | 0.58149 | 4.8093 | 156.8597 | 131.4829 |  |  | 432.9632 | 29.33 | 52.75
2021-01-19 07:25 | 8.4217 | 2.956 | 0.62692 | 5.158 | 159.1539 | 143.4641 |  |  | 434.4493 | 29.32 | 49.98
2021-01-19 07:30 | 8.0992 | 2.8672 | 0.59941 | 4.9944 | 155.5464 | 113.2619 |  |  | 435.6071 | 29.37 | 48.83
2021-01-19 07:35 | 8.442 | 2.6944 | 0.51416 | 4.6463 | 142.9591 | 118.1211 |  |  | 433.8455 | 29.47 | 51.68
2021-01-19 07:40 | 7.8483 | 3.2064 | 0.5419 | 5.4589 | 153.3355 | 121.2879 |  |  | 434.4691 | 29.51 | 53.55
2021-01-19 07:45 | 6.1273 | 2.9716 | 0.50447 | 5.0594 | 163.8983 | 148.1798 |  |  | 433.6231 | 29.51 | 55.32
2021-01-19 07:50 | 5.9623 | 2.7679 | 0.63073 | 4.8755 | 182.8725 | 163.9978 |  |  | 433.5225 | 29.51 | 55.87
2021-01-19 07:55 | 9.7775 | 2.999 | 0.74234 | 5.3372 | 197.9155 | 155.6213 |  |  | 433.7679 | 29.63 | 56.05
2021-01-19 08:00 | 9.6017 | 3.0852 | 0.65424 | 5.3854 | 184.9877 | 160.479 |  |  | 433.0383 | 29.67 | 56.74
2021-01-19 08:05 | 8.3356 | 3.4796 | 0.61647 | 5.948 | 190.4861 | 165.9225 |  |  | 433.5355 | 29.64 | 57.2
2021-01-19 08:10 | 7.133 | 2.9859 | 0.52397 | 5.1009 | 180.7209 | 141.4827 |  |  | 433.9621 | 29.66 | 57.49
2021-01-19 08:15 | 4.5222 | 2.2261 | 0.48627 | 3.8986 | 134.5531 | 117.2125 |  |  | 434.3595 | 29.64 | 58.38
2021-01-19 08:20 | 4.395 | 2.3337 | 0.56006 | 4.1373 | 120.0159 | 107.4279 |  |  | 434.3803 | 29.56 | 59.16
2021-01-19 08:25 | 4.5746 | 2.8984 | 0.51797 | 4.9586 | 104.5818 | 93.7054 |  |  | 434.4659 | 29.49 | 59.48
2021-01-19 08:30 | 4.3949 | 2.8639 | 0.52004 | 4.9099 | 112.0781 | 111.6579 |  |  | 434.9576 | 29.47 | 59.45
2021-01-19 08:35 | 4.6378 | 2.6383 | 0.50946 | 4.5557 | 120.9629 | 111.3696 |  |  | 435.0604 | 29.43 | 59.34
2021-01-19 08:40 | 6.8796 | 2.575 | 0.59575 | 4.545 | 135.1014 | 103.8832 |  |  | 435.7011 | 29.36 | 59.48
2021-01-19 08:45 | 6.3757 | 2.4663 | 0.59115 | 4.3715 | 140.1115 | 106.2102 |  |  | 435.0349 | 29.3 | 58.08
2021-01-19 08:50 | 6.0072 | 2.6252 | 0.54815 | 4.5701 | 126.7079 | 113.7937 |  |  | 435.892 | 29.21 | 54.35
2021-01-19 08:55 | 5.8568 | 3.0161 | 0.63111 | 5.2543 | 127.0575 | 121.045 |  |  | 435.6457 | 29.16 | 50.45
2021-01-19 09:00 | 4.9344 | 2.6339 | 0.59083 | 4.6282 | 154.3814 | 146.8638 |  |  | 438.0249 | 29.19 | 48.56
2021-01-19 09:05 | 5.3891 | 2.2972 | 0.58617 | 4.1095 | 137.6248 | 87.673 |  |  | 436.7846 | 29.2 | 46.6
2021-01-19 09:10 | 3.8458 | 1.9931 | 0.49802 | 3.5531 | 103.3429 | 59.2306 |  |  | 438.6 | 29.17 | 45.59
2021-01-19 09:15 | 3.5642 | 2.0714 | 0.51246 | 3.6877 | 83.2197 | 59.1458 |  |  | 438.9062 | 29.08 | 44.85
2021-01-19 09:20 | 3.13 | 1.8346 | 0.45369 | 3.2658 | 62.4378 | 47.6376 |  |  | 437.6116 | 29.02 | 43.91
2021-01-19 09:25 | 2.9257 | 1.6936 | 0.46194 | 3.0601 | 55.6339 | 33.0425 |  |  | 439.8593 | 29 | 43.32
2021-01-19 09:30 | 3.0394 | 1.8023 | 0.50153 | 3.262 | 47.4708 | 48.4271 |  |  | 439.4866 | 28.97 | 42.78
2021-01-19 09:35 | 3.75 | 1.8315 | 0.54935 | 3.3588 | 73.3517 | 77.5415 |  |  | 438.0793 | 28.92 | 41.88
2021-01-19 09:40 | 3.3931 | 1.9835 | 0.46776 | 3.5082 | 96.9282 | 67.4451 |  |  | 439.2544 | 28.92 | 41.2
2021-01-19 09:45 | 3.3787 | 2.0874 | 0.45501 | 3.6547 | 99.076 | 86.2114 |  |  | 442.2082 | 28.85 | 40.16
2021-01-19 09:50 | 3.1753 | 2.0178 | 0.45289 | 3.5459 | 135.962 | 145.9805 |  |  | 440.6607 | 28.85 | 39.96
2021-01-19 09:55 | 2.9209 | 1.7739 | 0.53422 | 3.2533 | 138.7707 | 110.6691 |  |  | 441.7962 | 28.83 | 39.72
2021-01-19 10:00 | 4.1911 | 1.8598 | 0.47164 | 3.3223 | 106.9562 | 57.8622 |  |  | 441.7294 | 28.86 | 39.78
2021-01-19 10:05 | 3.3154 | 1.7117 | 0.40702 | 3.0308 | 104.4059 | 74.8645 |  |  | 440.0611 | 28.86 | 40.26
2021-01-19 10:10 |  |  |  |  | 90.8468 | 55.8979 |  |  | 441.3307 | 28.79 | 39.79
2021-01-19 10:15 |  |  |  |  | 93.5778 | 70.0157 |  |  | 440.1489 | 28.85 | 39.87
2021-01-19 10:20 |  |  |  |  | 81.856 | 47.6106 |  |  | 441.405 | 28.85 | 38.74
2021-01-19 10:25 |  |  |  |  | 73.0633 | 53.3428 |  |  | 439.7958 | 28.9 | 38.36
2021-01-19 10:30 |  |  |  |  | 60.8174 | 51.3039 |  |  | 440.3632 | 28.92 | 37.93
2021-01-19 10:35 |  |  |  |  | 68.2028 | 51.1242 |  |  | 441.4806 | 28.86 | 38.21
2021-01-19 10:40 |  |  |  |  | 84.9414 | 59.5453 |  |  | 440.456 | 28.82 | 38.45
2021-01-19 10:45 |  |  |  |  | 81.8502 | 43.6108 |  |  | 441.5352 | 28.82 | 38.32
2021-01-19 10:50 |  |  |  |  | 77.9911 | 66.101 |  |  | 441.0107 | 28.82 | 38.3
2021-01-19 10:55 |  |  |  |  | 88.4018 | 62.799 |  |  | 439.9962 | 28.85 | 37.75
2021-01-19 11:00 |  |  |  |  | 107.5196 | 93.3055 |  |  | 439.3457 | 28.9 | 37.92
2021-01-19 11:05 |  |  |  |  | 92.0851 | 48.3675 |  |  | 440.9688 | 28.88 | 37.91
2021-01-19 11:10 |  |  |  |  | 67.7955 | 48.846 |  |  | 441.437 | 28.85 | 38.56
2021-01-19 11:15 |  |  |  |  | 66.9509 | 39.5531 |  |  | 439.8785 | 28.84 | 38.52
2021-01-19 11:20 | 2.3736 | 1.6574 | 0.44427 | 2.9847 | 77.845 | 68.1271 | 1.3413 | 0.15951 | 440.9753 | 28.82 | 38.5
2021-01-19 11:25 | 2.6784 | 1.8915 | 0.38589 | 3.2852 | 74.1328 | 51.9132 | 1.3341 | 0.20302 | 440.9204 | 28.84 | 38.6
2021-01-19 11:30 | 3.0342 | 2.07 | 0.43182 | 3.6027 | 67.3361 | 38.3196 | 1.3198 | 0.28281 | 439.8166 | 28.84 | 38.87
2021-01-19 11:35 | 3.3003 | 1.8629 | 0.44428 | 3.2998 | 78.0302 | 68.3831 | 1.3196 | 0.32628 | 440.3897 | 28.85 | 38.51
2021-01-19 11:40 | 4.011 | 1.9703 | 0.47137 | 3.4915 | 74.9492 | 61.0276 | 1.3195 | 0.36251 | 441.4407 | 28.87 | 38.33
2021-01-19 11:45 | 4.138 | 1.9309 | 0.42549 | 3.3852 | 66.8479 | 86.8017 | 1.3051 | 0.36252 | 440.3872 | 28.86 | 38.42
2021-01-19 11:50 | 3.9738 | 2.1517 | 0.56535 | 3.8636 | 87.0833 | 73.1687 | 1.3126 | 0.3771 | 440.8699 | 28.83 | 38.99
2021-01-19 11:55 | 3.4152 | 1.7339 | 0.41515 | 3.0708 | 100.7534 | 66.1397 | 1.3053 | 0.27557 | 440.3454 | 28.83 | 38.97
2021-01-19 12:00 | 4.3419 | 1.6209 | 0.43392 | 2.9164 | 82.1359 | 42.5762 | 1.3198 | 0.25381 | 441.4182 | 28.82 | 38.98
2021-01-19 12:05 | 2.7045 | 1.6157 | 0.45067 | 2.9273 | 62.0138 | 36.2839 | 1.32 | 0.23209 | 442.974 | 28.8 | 39.35
2021-01-19 12:10 | 2.1334 | 1.5355 | 0.4215 | 2.7752 | 71.346 | 54.6955 | 1.3201 | 0.23211 | 440.3183 | 28.78 | 39.65
2021-01-19 12:15 | 1.7393 | 1.4794 | 0.38386 | 2.6515 | 85.6413 | 64.1091 | 1.3198 | 0.18855 | 442.0565 | 28.74 | 39.2
2021-01-19 12:20 | 2.145 | 1.6001 | 0.48178 | 2.9324 | 89.1619 | 84.1357 | 1.3195 | 0.203 | 440.6784 | 28.68 | 38.66
2021-01-19 12:25 | 2.5005 | 1.7172 | 0.43174 | 3.0639 | 97.7873 | 87.5618 | 1.3123 | 0.25376 | 440.6573 | 28.68 | 38.78
2021-01-19 12:30 | 2.7666 | 1.6353 | 0.47963 | 2.9862 | 96.3087 | 59.5356 | 1.3048 | 0.23922 | 440.776 | 28.65 | 38.42
2021-01-19 12:35 | 2.5635 | 1.8434 | 0.53175 | 3.3573 | 83.0265 | 65.7877 | 1.312 | 0.25371 | 440.2897 | 28.63 | 38.39
2021-01-19 12:40 | 2.4623 | 2.0913 | 0.47552 | 3.6811 | 73.4122 | 38.6861 | 1.3195 | 0.23924 | 442.2254 | 28.71 | 38.56
2021-01-19 12:45 | 2.6531 | 1.8099 | 0.40258 | 3.1748 | 65.4412 | 64.7608 | 1.3124 | 0.28279 | 439.9869 | 28.75 | 38.85
2021-01-19 12:50 | 3.8469 | 1.7598 | 0.4381 | 3.1377 | 81.6608 | 95.5249 | 1.3199 | 0.34809 | 440.4668 | 28.74 | 39.23
2021-01-19 12:55 | 3.4536 | 1.5054 | 0.42771 | 2.7352 | 87.3756 | 49.8332 | 1.32 | 0.26109 | 442.0613 | 28.71 | 39.49
2021-01-19 13:00 | 2.2222 | 1.27 | 0.3568 | 2.3035 | 71.4443 | 31.2982 | 1.3128 | 0.21759 | 442.6553 | 28.64 | 39.86
2021-01-19 13:05 | 2.1464 | 1.1682 | 0.33183 | 2.1225 | 60.5165 | 45.7227 | 1.3058 | 0.20313 | 442.5916 | 28.56 | 40.62
2021-01-19 13:10 | 2.5017 | 1.5901 | 0.35474 | 2.792 | 61.7486 | 51.701 | 1.3057 | 0.23212 | 440.603 | 28.51 | 40.43
2021-01-19 13:15 | 2.3239 | 1.7316 | 0.42778 | 3.0821 | 75.7577 | 59.0051 | 1.3129 | 0.21761 | 441.1794 | 28.48 | 40.48
2021-01-19 13:20 | 2.6922 | 1.6948 | 0.37143 | 2.9694 | 78.6927 | 72.4956 | 1.3057 | 0.28289 | 442.2579 | 28.47 | 40.47
2021-01-19 13:25 | 2.6534 | 1.5529 | 0.3463 | 2.7266 | 75.8697 | 73.3204 | 1.3126 | 0.33358 | 442.3692 | 28.47 | 39.83
2021-01-19 13:30 | 5.0895 | 1.4858 | 0.35663 | 2.6341 | 83.6462 | 59.0945 | 1.3122 | 0.35524 | 442.5095 | 28.46 | 39.13
2021-01-19 13:35 | 5.4688 | 1.5915 | 0.36071 | 2.8002 | 61.9513 | 48.9378 | 1.3118 | 0.34065 | 442.6144 | 28.47 | 38.42
2021-01-19 13:40 | 3.6156 | 1.4049 | 0.40442 | 2.5579 | 56.1553 | 54.9983 | 1.3116 | 0.28261 | 442.1631 | 28.47 | 37.97
2021-01-19 13:45 | 3.273 | 1.5517 | 0.44402 | 2.8246 | 64.2938 | 40.3321 | 1.2971 | 0.25362 | 442.2001 | 28.45 | 37.97
2021-01-19 13:50 | 3.1592 | 1.5546 | 0.42322 | 2.8083 | 53.4916 | 47.5131 | 1.3045 | 0.22466 | 442.118 | 28.47 | 38.23
2021-01-19 13:55 | 3.1086 | 1.5288 | 0.43158 | 2.7751 | 61.4622 | 63.9491 | 1.3046 | 0.26091 | 442.0838 | 28.48 | 38.32
2021-01-19 14:00 | 3.0954 | 1.5286 | 0.37939 | 2.7224 | 57.8484 | 31.1772 | 1.3043 | 0.31884 | 443.2512 | 28.46 | 37.91
2021-01-19 14:05 | 3.1972 | 1.6947 | 0.39819 | 2.9979 | 63.4267 | 58.098 | 1.3045 | 0.31162 | 441.1161 | 28.44 | 38.22
2021-01-19 14:10 | 3.8061 | 1.9612 | 0.44405 | 3.4481 | 77.8371 | 70.2147 | 1.3044 | 0.25364 | 442.1307 | 28.48 | 38.05
2021-01-19 14:15 | 3.4885 | 1.8971 | 0.36896 | 3.2768 | 80.2844 | 62.9813 | 1.355 | 0.28984 | 442.1794 | 28.48 | 37.77
2021-01-19 14:20 | 3.5267 | 1.7951 | 0.419 | 3.1706 | 64.2726 | 34.7496 | 1.384 | 0.25362 | 442.177 | 28.47 | 37.89
2021-01-19 14:25 | 4.1353 | 1.7147 | 0.44397 | 3.0724 | 71.8368 | 66.7223 | 1.3767 | 0.28258 | 442.7633 | 28.46 | 37.67
2021-01-19 14:30 | 4.2623 | 1.5204 | 0.4169 | 2.7474 | 75.1998 | 64.8484 | 1.326 | 0.28984 | 442.6956 | 28.49 | 37.74
2021-01-19 14:35 | 3.7678 | 1.8414 | 0.45862 | 3.2812 | 71.5001 | 49.091 | 1.3044 | 0.37681 | 443.1389 | 28.53 | 37.81
2021-01-19 14:40 | 2.9422 | 1.8802 | 0.39177 | 3.2738 | 61.9187 | 32.9124 | 1.3401 | 0.33322 | 442.7595 | 28.53 | 36.95
2021-01-19 14:45 | 3.2087 | 1.6655 | 0.3772 | 2.9301 | 61.3017 | 51.4196 | 1.3619 | 0.3115 | 441.6863 | 28.53 | 37.03
2021-01-19 14:50 | 4.389 | 1.7066 | 0.40854 | 3.0245 | 62.8671 | 54.6167 | 1.3622 | 0.26085 | 443.7421 | 28.51 | 37.6
2021-01-19 14:55 | 4.5038 | 1.987 | 0.50033 | 3.5461 | 85.4179 | 78.2523 | 1.3189 | 0.26088 | 442.577 | 28.54 | 37.89
2021-01-19 15:00 | 3.5393 | 2.1976 | 0.54198 | 3.9106 | 106.7436 | 97.8534 | 1.3116 | 0.25361 | 442.0825 | 28.54 | 37.69
2021-01-19 15:05 | 2.9683 | 2.0765 | 0.48984 | 3.6728 | 107.8849 | 93.9413 | 1.3115 | 0.2536 | 441.4878 | 28.6 | 37.43
2021-01-19 15:10 | 3.3491 | 2.0535 | 0.43359 | 3.5792 | 114.7622 | 103.5579 | 1.3261 | 0.34057 | 442.9315 | 28.68 | 37.41
2021-01-19 15:15 | 3.4376 | 2.3511 | 0.43772 | 4.0396 | 123.5007 | 99.653 | 1.3404 | 0.32605 | 441.3492 | 28.7 | 37.17
2021-01-19 15:20 | 3.031 | 1.7986 | 0.43346 | 3.1905 | 104.2876 | 67.3776 | 1.3546 | 0.30425 | 441.9918 | 28.69 | 36.63
2021-01-19 15:25 | 3.4372 | 2.0055 | 0.48352 | 3.5597 | 91.5446 | 57.5731 | 1.4055 | 0.31153 | 441.9574 | 28.68 | 36.93
2021-01-19 15:30 | 5.0599 | 2.0718 | 0.42302 | 3.5988 | 79.1933 | 70.5395 | 1.3691 | 0.34045 | 442.102 | 28.63 | 36.63
2021-01-19 15:35 | 4.9206 | 1.9509 | 0.42929 | 3.4197 | 91.4834 | 65.3685 | 1.3329 | 0.41291 | 442.6253 | 28.62 | 36.77
2021-01-19 15:40 | 3.9441 | 1.9197 | 0.4793 | 3.4218 | 83.4485 |  | 1.3184 | 0.34771 | 442.0643 | 28.64 | 36.74
2021-01-19 15:45 | 4.0961 | 2.0351 | 0.44802 | 3.5696 | 77.894 | -3.0232 | 1.3256 | 0.35494 | 442.0181 | 28.69 | 36.48
2021-01-19 15:50 | 3.4751 | 2.0095 | 0.42306 | 3.5032 | 90.8083 | 65.2298 | 1.4054 | 0.36222 | 441.8833 | 28.75 | 36.62
2021-01-19 15:55 | 4.463 | 2.1298 | 0.45626 | 3.7189 | 94.25 | 69.4602 | 1.434 | 0.44177 | 442.5301 | 28.76 | 35.85
2021-01-19 16:00 | 4.6274 | 2.3267 | 0.44789 | 4.0144 | 94.2828 | 91.0271 | 1.3687 | 0.57209 | 443.5963 | 28.78 | 35.6
2021-01-19 16:05 | 4.1963 | 1.9828 | 0.41872 | 3.4581 | 102.7288 | 96.8972 | 1.3179 | 0.52138 | 443.607 | 28.78 | 35.54
2021-01-19 16:10 | 4.0568 | 1.6186 | 0.38122 | 2.8623 | 109.0671 | 94.0873 | 1.3179 | 0.37655 | 443.1385 | 28.74 | 35.61
2021-01-19 16:15 | 3.9049 | 1.3469 | 0.33125 | 2.3937 | 49.9326 | 62.7023 | 1.3108 | 0.29692 | 442.0775 | 28.72 | 35.83
2021-01-19 16:20 | 3.3346 | 1.4136 | 0.31876 | 2.4855 | 49.5699 | 52.9172 | 1.3181 | 0.30417 | 442.6878 | 28.65 | 36.1
2021-01-19 16:25 | 4.7809 | 1.717 | 0.41259 | 3.0465 | 65.6894 | 62.1386 | 1.3328 | 0.42013 | 442.0775 | 28.65 | 36.56
2021-01-19 16:30 | 6.4309 | 2.0709 | 0.51482 | 3.6892 | 77.7695 | 71.5593 | 1.3331 | 0.50717 | 443.5356 | 28.67 | 37.09
2021-01-19 16:35 | 7.6868 | 2.0451 | 0.38768 | 3.5225 | 92.9209 | 69.2061 | 1.3476 | 0.48544 | 442.9413 | 28.71 | 37.04
2021-01-19 16:40 | 6.1252 | 1.9671 | 0.43135 | 3.4467 | 96.9479 | 66.9383 | 1.3546 | 0.39116 | 442.453 | 28.75 | 36.39
2021-01-19 16:45 | 6.4042 | 1.7891 | 0.39384 | 3.1362 | 88.6998 | 71.179 | 1.3546 | 0.36943 | 442.9971 | 28.74 | 36.41
2021-01-19 16:50 | 5.7839 | 1.4549 | 0.37725 | 2.6074 | 90.4121 | 78.0832 | 1.3186 | 0.33328 | 442.3647 | 28.75 | 36.89
2021-01-19 16:55 | 5.0614 | 1.4659 | 0.35019 | 2.5951 | 93.3132 | 73.2704 | 1.326 | 0.34056 | 441.8511 | 28.71 | 37.22
2021-01-19 17:00 | 4.4271 | 1.7053 | 0.33143 | 2.9453 | 83.4992 | 61.5791 | 1.3332 | 0.35504 | 442.913 | 28.71 | 37.2
2021-01-19 17:05 | 4.0209 | 1.7799 | 0.41269 | 3.141 | 87.5016 | 60.0629 | 1.3331 | 0.41298 | 442.2534 | 28.82 | 36.79
2021-01-19 17:10 | 3.5518 | 1.3802 | 0.31474 | 2.4304 | 86.9879 | 64.6523 | 1.3694 | 0.43474 | 443.2042 | 28.88 | 36.77
2021-01-19 17:15 | 4.0082 | 1.1748 | 0.29179 | 2.0926 | 76.4596 | 48.9301 | 1.3548 | 0.38399 | 442.1601 | 28.89 | 36.59
2021-01-19 17:20 | 4.1725 | 1.2712 | 0.30218 | 2.2507 | 66.7404 | 58.7352 | 1.3185 | 0.3767 | 442.7294 | 28.9 | 36.26
2021-01-19 17:25 | 3.0819 | 1.3772 | 0.3001 | 2.4112 | 63.9913 | 55.1135 | 1.3112 | 0.30426 | 442.2117 | 28.89 | 36.3
2021-01-19 17:30 | 2.9046 | 1.2428 | 0.28137 | 2.1884 | 55.0886 | 29.9846 | 1.3186 | 0.26082 | 444.8267 | 28.88 | 36.57
2021-01-19 17:35 | 2.1053 | 1.0373 | 0.27509 | 1.8631 | 40.8072 | 35.6327 | 1.304 | 0.22457 | 443.9195 | 28.81 | 36.45
2021-01-19 17:40 | 1.8135 | 0.99108 | 0.28341 | 1.8047 | 45.5335 | 35.2864 | 1.3039 | 0.1811 | 445.0111 | 28.74 | 36.54
2021-01-19 17:45 | 1.7246 | 0.85504 | 0.24171 | 1.5544 | 41.8663 | 37.7984 | 1.311 | 0.16659 | 445.6935 | 28.67 | 36.41
2021-01-19 17:50 | 1.8641 | 0.82516 | 0.22921 | 1.494 | 33.8836 | 27.3706 | 1.3038 | 0.18833 | 444.9304 | 28.46 | 36.93
2021-01-19 17:55 | 1.9664 | 0.89758 | 0.25015 | 1.6281 | 42.5851 | 27.4124 | 1.3043 | 0.18116 | 445.4689 | 28.33 | 38.27
2021-01-19 18:00 | 2.0937 | 1.0148 | 0.2523 | 1.8078 | 42.4226 | 37.7022 | 1.3047 | 0.1812 | 446.056 | 28.22 | 39.13
2021-01-19 18:05 | 2.729 | 0.91303 | 0.28575 | 1.6853 | 47.6855 | 24.7161 | 1.3051 | 0.18126 | 445.9487 | 28.2 | 39.97
2021-01-19 18:10 | 2.1326 | 0.93759 | 0.23779 | 1.675 | 44.0329 | 35.7463 | 1.3051 | 0.15952 | 446.5523 | 28.13 | 40.31
2021-01-19 18:15 | 1.7892 | 0.95356 | 0.23979 | 1.7014 | 46.1685 | 44.8386 | 1.3264 | 0.21744 | 446.323 | 28.04 | 39.54
2021-01-19 18:20 | 2.6639 | 0.75609 | 0.22929 | 1.3882 | 54.6384 | 26.7509 | 1.3188 | 0.20288 | 446.592 | 27.95 | 38.95
2021-01-19 18:25 | 2.981 | 0.89205 | 0.27931 | 1.6488 | 41.5053 | 50.8618 | 1.3115 | 0.22462 | 446.1034 | 27.93 | 38.92
2021-01-19 18:30 | 1.4461 | 0.47459 | 0.21886 | 0.94424 | 42.4697 | 20.5397 | 1.3042 | 0.11593 | 447.1622 | 27.93 | 38.94
2021-01-19 18:35 | 1.2053 | 0.56715 | 0.23558 | 1.107 | 36.3161 | 15.2248 | 1.29 | 0.10146 | 447.2036 | 27.85 | 39.58
2021-01-19 18:40 | 1.1926 | 0.52907 | 0.20639 | 1.0174 | 32.8953 | 21.4058 | 1.3044 | 0.10146 | 447.8426 | 27.78 | 39.72
2021-01-19 18:45 | 1.7888 | 0.47328 | 0.14593 | 0.87138 | 25.6876 | 28.6715 | 1.3044 | 0.15942 | 447.4102 | 27.73 | 39.69
2021-01-19 18:50 | 2.0044 | 0.49503 | 0.17094 | 0.92973 | 25.0274 | 14.7769 | 1.3043 | 0.14493 | 448.5724 | 27.67 | 39.77
2021-01-19 18:55 | 0.92604 | 0.38349 | 0.1876 | 0.77751 | 36.392 | 16.3185 | 1.297 | 0.086951 | 448.0569 | 27.62 | 39.76
2021-01-19 19:00 | 1.0275 | 0.35085 | 0.15634 | 0.69205 | 39.7212 | 19.7489 | 1.297 | 0.12318 | 448.155 | 27.55 | 39.96
2021-01-19 19:05 | 1.2179 | 0.38895 | 0.14592 | 0.74212 | 36.9729 | 34.2631 | 1.3044 | 0.12319 | 448.161 | 27.53 | 40.15
2021-01-19 19:10 | 1.1674 | 0.42578 | 0.14179 | 0.79653 | 26.5973 | 23.2472 | 1.3047 | 0.10872 | 448.0757 | 27.51 | 40.89
2021-01-19 19:15 | 1.2562 | 0.3972 | 0.13136 | 0.7402 | 24.3428 | 7.451 | 1.3046 | 0.13771 | 447.3395 | 27.3 | 41.3
2021-01-19 19:20 | 1.2053 | 0.8541 | 0.18971 | 1.501 | 18.6548 | 1.36 | 1.3044 | 0.15218 | 447.6556 | 27.14 | 41.21
2021-01-19 19:25 | 1.1931 | 0.62723 | 0.13348 | 1.0949 | 20.8149 | 31.1615 | 1.3049 | 0.14499 | 448.7341 | 27.01 | 42.65
2021-01-19 19:30 | 1.4983 | 0.58392 | 0.12727 | 1.0223 | 28.472 | 28.0149 | 1.3055 | 0.1523 | 447.638 | 26.91 | 44.02
2021-01-19 19:35 | 1.1174 | 0.42877 | 0.13979 | 0.79703 | 49.2669 | 45.4169 | 1.3128 | 0.10154 | 448.8645 | 26.79 | 44.45
2021-01-19 19:40 | 1.2317 | 0.60981 | 0.15648 | 1.0912 | 57.6164 | 43.3545 | 1.3128 | 0.1233 | 448.4397 | 26.72 | 44.61
2021-01-19 19:45 | 1.358 | 0.53196 | 0.14598 | 0.9614 | 50.5627 | 42.8057 | 1.2976 | 0.11599 | 449.7973 | 26.67 | 43.38
2021-01-19 19:50 | 1.2437 | 0.46934 | 0.12512 | 0.84454 | 42.2131 | 14.3553 | 1.2975 | 0.10148 | 448.3406 | 26.6 | 43.31
2021-01-19 19:55 | 0.863 | 0.34965 | 0.11261 | 0.64856 | 31.3826 | 22.0115 | 1.3049 | 0.10149 | 449.5594 | 26.48 | 43.8
2021-01-19 20:00 | 0.87566 | 0.30338 | 0.1001 | 0.56513 | 18.0716 | 18.7214 | 1.2976 | 0.086987 | 450.7612 | 26.4 | 43.92
2021-01-19 20:05 | 0.77387 | 0.2652 | 0.093808 | 0.50031 | 15.173 | -2.2937 | 1.3044 | 0.072465 | 450.5013 | 26.32 | 43.14
2021-01-19 20:10 | 0.87542 | 0.21489 | 0.10007 | 0.42946 | 15.8743 | 16.4224 | 1.3045 | 0.079717 | 448.9432 | 26.27 | 43.46
2021-01-19 20:15 | 0.82457 | 0.22167 | 0.10214 | 0.44192 | 11.4375 | 16.8061 | 1.3043 | 0.079707 | 450.6758 | 26.22 | 43.24
2021-01-19 20:20 | 0.81199 | 0.23121 | 0.11466 | 0.46908 | 19.0006 | 23.2128 | 1.3045 | 0.07247 | 450.4856 | 26.25 | 43.58
2021-01-19 20:25 | 0.82491 | 0.17142 | 0.091756 | 0.35451 | 12.6605 | -5.3809 | 1.3048 | 0.065241 | 450.405 | 26.22 | 44.47
2021-01-19 20:30 | 0.9138 | 0.1864 | 0.10219 | 0.38582 | 16.7328 | 9.4426 | 1.3049 | 0.079745 | 450.4962 | 26.14 | 44.87
2021-01-19 20:35 | 0.83761 | 0.23128 | 0.10427 | 0.45878 | 16.1633 | 16.4678 | 1.3048 | 0.07974 | 451.1478 | 26.08 | 44.86
2021-01-19 20:40 | 0.77415 | 0.20679 | 0.089672 | 0.40874 | 3.8581 | -2.2133 | 1.3048 | 0.072491 | 451.7573 | 26.03 | 45
2021-01-19 20:45 | 0.87564 | 0.23535 | 0.093839 | 0.4546 | 12.6702 | 17.8987 | 1.3048 | 0.072488 | 451.8371 | 25.99 | 44.98
2021-01-19 20:50 | 0.81222 | 0.34284 | 0.10635 | 0.63187 | 19.808 | 0.89344 | 1.3048 | 0.072491 | 450.1707 | 26.02 | 45
2021-01-19 20:55 | 0.63455 | 0.48841 | 0.11678 | 0.86335 | 15.016 | 5.6551 | 1.3048 | 0.065242 | 451.2236 | 26.03 | 44.99
2021-01-19 21:00 | 0.59647 | 0.4231 | 0.11469 | 0.76324 | 10.5181 | -2.1422 | 1.3048 | 0.050743 | 450.2364 | 25.98 | 45.07
2021-01-19 21:05 | 0.65985 | 0.39585 | 0.10009 | 0.70686 | 7.6543 | 17.9277 | 1.3047 | 0.057986 | 450.3578 | 25.93 | 44.9
2021-01-19 21:10 | 0.67246 | 0.389 | 0.11258 | 0.70886 | 10.2824 | 12.9012 | 1.2973 | 0.050732 | 451.4952 | 25.92 | 44.59
2021-01-19 21:15 | 0.609 | 0.3305 | 0.10632 | 0.61293 | 16.1181 | -0.5481 | 1.3045 | 0.050729 | 451.026 | 25.89 | 44.53
2021-01-19 21:20 | 0.57098 | 0.31965 | 0.091738 | 0.5817 | 7.8262 | 11.653 | 1.3046 | 0.050733 | 451.0524 | 25.85 | 44.86
2021-01-19 21:25 | 0.44429 | 0.25174 | 0.089692 | 0.47349 | 11.6276 | 15.6693 | 1.3124 | 0.050755 | 450.9024 | 25.82 | 46.23
2021-01-19 21:30 | 0.5459 | 0.2613 | 0.089703 | 0.49024 | 23.1362 | 5.3727 | 1.3053 | 0.08702 | 450.3714 | 25.78 | 46.71
2021-01-19 21:35 | 0.58393 | 0.1946 | 0.087608 | 0.38589 | 14.8674 | 1.5436 | 1.3052 | 0.094262 | 451.5792 | 25.72 | 46.57
2021-01-19 21:40 | 0.58392 | 0.1701 | 0.073006 | 0.33583 | 12.2167 | 3.2903 | 1.3051 | 0.087009 | 451.1558 | 25.65 | 46.72
2021-01-19 21:45 | 0.43159 | 0.15921 | 0.075091 | 0.31914 | 13.4353 | 18.4418 | 1.3124 | 0.087009 | 451.2162 | 25.61 | 46.83
2021-01-19 21:50 | 0.35545 | 0.11567 | 0.064665 | 0.24197 | 12.654 | -2.153 | 1.3125 | 0.072511 | 451.3152 | 25.53 | 47.2
2021-01-19 21:55 | 0.38083 | 0.13064 | 0.079265 | 0.2816 | 13.4051 | 3.006 | 1.3124 | 0.058007 | 451.4339 | 25.46 | 47.31
2021-01-19 22:00 | 0.4443 | 0.12928 | 0.081351 | 0.27951 | 11.8209 | 14.6949 | 1.3052 | 0.050757 | 450.9259 | 25.44 | 47.38
2021-01-19 22:05 | 0.53319 | 0.14153 | 0.085527 | 0.30247 | 13.8223 | 4.235 | 1.3125 | 0.050759 | 450.3053 | 25.48 | 47.43
2021-01-19 22:10 | 0.29198 | 0.080291 | 0.066751 | 0.18982 | 6.3778 | 5.1185 | 1.3052 | 0.036256 | 451.4488 | 25.44 | 47.47
2021-01-19 22:15 | 0.43167 | 0.12249 | 0.075104 | 0.26495 | 9.771 | 17.2465 | 1.3054 | 0.03626 | 451.5161 | 25.36 | 48.06
2021-01-19 22:20 | 0.36831 | 0.093942 | 0.068869 | 0.21287 | 16.8052 | -5.385 | 1.2985 | 0.014509 | 450.8896 | 25.32 | 49.2
2021-01-19 22:25 | 0.27938 | 0.078959 | 0.064689 | 0.18781 | 2.4992 | 7.2742 | 1.2984 | 0.029015 | 452.7185 | 25.2 | 49.29
2021-01-19 22:30 | 0.25403 | 0.16067 | 0.070961 | 0.31724 | 6.8791 | 6.8892 | 1.3059 | 0.036275 | 451.0665 | 25.18 | 49.85
2021-01-19 22:35 | 0.35567 | 0.16204 | 0.077229 | 0.32561 | 22.6815 | 17.0213 | 1.306 | 0.036278 | 451.503 | 25.22 | 50
2021-01-19 22:40 | 0.49551 | 0.23563 | 0.077247 | 0.43843 | 28.1043 | 22.1074 | 1.2918 | 0.014515 | 450.3723 | 25.19 | 50.8
2021-01-19 22:45 | 0.30508 | 0.23574 | 0.079374 | 0.44073 | 31.4333 | 19.5556 | 1.2924 | 0.029044 | 450.7173 | 25.17 | 52.38
2021-01-19 22:50 | 0.26701 | 0.21945 | 0.071036 | 0.40741 | 18.7773 | 7.2831 | 1.2928 | 0.050839 | 451.797 | 25.09 | 53.41
2021-01-19 22:55 | 0.33058 | 0.19355 | 0.060589 | 0.35726 | 17.8615 | -6.2251 | 1.3 | 0.087151 | 451.9262 | 25.01 | 53.61
2021-01-19 23:00 | 0.27959 | 0.1158 | 0.058471 | 0.23597 | 17.924 | 25.9862 | 1.2994 | 0.043554 | 451.7908 | 24.89 | 52.47
2021-01-19 23:05 | 0.5846 | 0.11308 | 0.054295 | 0.22762 | 6.3746 | 11.4378 | 1.2921 | 0.058073 | 451.3992 | 24.79 | 52.83
2021-01-19 23:10 | 0.43211 | 0.096731 | 0.054297 | 0.20048 | 12.0075 | -2.6231 | 1.2994 | 0.043556 | 452.5958 | 24.7 | 53.21
2021-01-19 23:15 | 0.36864 | 0.08585 | 0.054309 | 0.1859 | 15.7321 | -10.8304 | 1.2997 | 0.058088 | 451.4847 | 24.66 | 54.03
2021-01-19 23:20 | 0.61019 | 0.12674 | 0.060577 | 0.25484 | 9.9867 | 25.994 | 1.2925 | 0.05809 | 452.02 | 24.65 | 54.18
2021-01-19 23:25 | 0.45776 | 0.11859 | 0.050146 | 0.22983 | 13.1732 | 0.64086 | 1.2856 | 0.058104 | 452.4435 | 24.65 | 54.98
2021-01-19 23:30 | 0.26712 | 0.11182 | 0.045984 | 0.21738 | 10.2575 | 16.6074 | 1.3006 | 0.036329 | 452.3817 | 24.58 | 56.4
2021-01-19 23:35 | 0.35624 | 0.12002 | 0.048085 | 0.23415 | 5.0892 | 10.2191 | 1.2936 | 0.043604 | 452.3734 | 24.52 | 57.31
2021-01-19 23:40 | 0.33076 | 0.12274 | 0.048079 | 0.23621 | 14.2174 | 13.1895 | 1.2862 | 0.050865 | 453.0728 | 24.45 | 57.15
2021-01-19 23:45 | 0.21624 | 0.14999 | 0.048074 | 0.27799 | 5.5052 | 0.62074 | 1.2933 | 0.05086 | 453.1349 | 24.44 | 56.85
2021-01-19 23:50 |  | 0.076341 | 0.048061 | 0.16508 | -12.9203 | -1.0072 | 1.293 | 0.029055 | 452.866 | 24.34 | 56.36
2021-01-19 23:55 | 0.21617 | 0.06543 | 0.03761 | 0.1379 | -6.9987 | -9.4605 | 1.2929 | 0.036316 | 453.1015 | 24.21 | 56.53
2021-01-20 | 0.10172 | 0.059975 | 0.035519 | 0.12745 | -2.2786 | 9.3788 | 1.3001 | 0.029052 | 453.2704 | 24.11 | 56.75
2021-01-20 00:05 | 0.15258 | 0.12677 | 0.037609 | 0.23192 | -12.8781 | -5.7982 | 1.2928 | 0.050841 | 452.2685 | 24.06 | 56.94
2021-01-20 00:10 | 0.13988 | 0.095421 | 0.045969 | 0.19223 | -6.2156 | -1.6378 | 1.3001 | 0.036317 | 451.7246 | 24.05 | 57.13
2021-01-20 00:15 | 0.11447 | 0.070898 | 0.045978 | 0.15465 | -4.6295 | -8.852 | 1.2931 | 0.021794 | 452.2197 | 24.02 | 57.88
2021-01-20 00:20 | 0.12719 | 0.084533 | 0.039709 | 0.16928 | -10.1648 | -2.442 | 1.2932 | 0.036325 | 451.6131 | 24.06 | 57.8
2021-01-20 00:25 | 0.11444 | 0.10905 | 0.048056 | 0.21521 | -1.18 | 14.0784 | 1.2855 | 0.036315 | 453.837 | 24.09 | 56.83
2021-01-20 00:30 | 0.10171 | 0.074959 | 0.043871 | 0.15877 | -1.1798 | -17.1887 | 1.2926 | 0.029048 | 453.3941 | 24.07 | 56.43
2021-01-20 00:35 | 0.089001 | 0.068149 | 0.043874 | 0.14834 | -7.4456 | -12.0126 | 1.3 | 0.02905 | 452.8707 | 24.04 | 56.76
2021-01-20 00:40 | 0.076287 | 0.10086 | 0.043874 | 0.19848 | -0.66115 | 9.5104 | 1.2855 | 0.036312 | 452.3013 | 24.06 | 56.7
2021-01-20 00:45 | 0.10171 | 0.065419 | 0.043871 | 0.14415 | 5.7771 | -4.6074 | 1.2854 | 0.029048 | 454.4642 | 24.07 | 56.47
2021-01-20 00:50 | 0.16525 | 0.049057 | 0.037598 | 0.11279 | -6.4067 | 9.8541 | 1.2924 | 0.021783 | 451.9678 | 23.99 | 56.22
2021-01-20 00:55 | 0.39401 | 0.036787 | 0.033416 | 0.087716 | -1.5964 | -14.3062 | 1.2923 | 0.02178 | 454.2762 | 23.93 | 55.95
2021-01-20 01:00 | 0.25421 | 0.029976 | 0.033417 | 0.079366 | 1.0575 | -6.7721 | 1.2923 | 0.029041 | 452.2052 | 23.92 | 56.09
2021-01-20 01:05 |  |  |  |  | -5.9982 | -6.171 |  |  | 453.3534 | 23.93 | 55.41
2021-01-20 01:10 |  |  |  |  | -2.7549 | -7.5226 |  |  | 452.8639 | 23.92 | 55.2
2021-01-20 01:15 |  |  |  |  | 4.8796 | 16.1841 |  |  | 453.3209 | 23.91 | 55.35
2021-01-20 01:20 |  |  |  |  | 1.3011 | -1.7382 |  |  | 454.4631 | 23.89 | 55.16
2021-01-20 01:25 |  |  |  |  | 19.7072 | 10.1892 |  |  | 451.6504 | 23.86 | 56.49
2021-01-20 01:30 |  |  |  |  | 6.8642 | -5.349 |  |  | 452.82 | 23.79 | 56.83
2021-01-20 01:35 |  |  |  |  | -3.0089 | -10.2871 |  |  | 453.0766 | 23.74 | 55.66
2021-01-20 01:40 |  |  |  |  | -1.1181 | -0.18297 |  |  | 453.2023 | 23.72 | 55.62
2021-01-20 01:45 |  |  |  |  | 2.2361 | -1.1181 |  |  | 452.708 | 23.71 | 55.44
2021-01-20 01:50 |  |  |  |  | -5.5593 | -14.503 |  |  | 454.3817 | 23.7 | 55.15
2021-01-20 01:55 |  |  |  |  | -2.1651 | 5.4789 |  |  | 452.6798 | 23.71 | 55.65
2021-01-20 02:00 |  |  |  |  | -4.9292 | 3.7299 |  |  | 452.7966 | 23.68 | 55.22
2021-01-20 02:05 |  |  |  |  | -1.311 | -4.502 |  |  | 452.8117 | 23.69 | 54.96
2021-01-20 02:10 | 0.13973 | 0.025873 | 0.048008 | 0.087666 | 2.0426 | -2.8657 | 1.3568 | -0.05079 | 452.2532 | 23.72 | 54.67
2021-01-20 02:15 | 0.076211 | 0.025871 | 0.037569 | 0.077225 | -4.8064 | 4.2678 | 1.335 | -0.021766 | 453.3712 | 23.71 | 54.51
2021-01-20 02:20 | 0.050819 | 0.020429 | 0.03549 | 0.066805 | 4.1265 | -0.12197 | 1.3208 | 0.014514 | 453.8191 | 23.7 | 55.33
2021-01-20 02:25 | 0.050839 | 0.020437 | 0.031327 | 0.064742 | 7.0971 | -6.4565 | 1.3213 | 0.021779 | 452.5708 | 23.7 | 56.61
2021-01-20 02:30 | 0.076268 | 0.02044 | 0.035508 | 0.066839 | 6.5488 | 2.4609 | 1.2997 | 0.029043 | 451.9895 | 23.69 | 57.08
2021-01-20 02:35 | 0.076273 | 0.031343 | 0.039688 | 0.087732 | 8.1154 | 0.40679 | 1.3143 | 0.029045 | 452.4665 | 23.71 | 57.24
2021-01-20 02:40 | 0.063567 | 0.053152 | 0.054316 | 0.13579 | 3.3563 | 0.20341 | 1.3071 | 0.014524 | 452.3746 | 23.74 | 57.48
2021-01-20 02:45 | 0.050843 | 0.074943 | 0.056393 | 0.17336 | -3.8641 | 7.0164 | 1.2996 | 0.014521 | 451.8531 | 23.79 | 56.62
2021-01-20 02:50 | 0.076229 | 0.34049 | 0.060542 | 0.58246 | 6.3626 | -4.462 | 1.299 | 0.021771 | 453.5419 | 23.88 | 54.75
2021-01-20 02:55 | 0.063528 | 0.1362 | 0.03758 | 0.24427 | 8.4467 | 6.6476 | 1.2918 | 0.021772 | 452.5014 | 23.84 | 55.07
2021-01-20 03:00 | 0.16522 | 0.24523 | 0.058473 | 0.43437 | 1.0981 | 4.8802 | 1.2922 | 0.029037 | 453.0122 | 23.78 | 56.15
2021-01-20 03:05 | 0.19065 | 0.1962 | 0.045948 | 0.3467 | -1.5252 | 17.5908 | 1.2923 | 0.04356 | 452.4771 | 23.75 | 56.57
2021-01-20 03:10 | 0.24153 | 0.20714 | 0.064755 | 0.38226 | 8.1256 | 0.20339 | 1.2925 | 0.036306 | 454.0646 | 23.72 | 57.21
2021-01-20 03:15 | 0.26694 | 0.16215 | 0.043863 | 0.29242 | 7.3827 | 7.5047 | 1.2997 | 0.014521 | 452.5896 | 23.65 | 57.21
2021-01-20 03:20 | 0.2542 | 0.12399 | 0.052214 | 0.24227 | 14.0728 | 9.6801 | 1.2996 | 0.02178 | 453.7181 | 23.64 | 56.97
2021-01-20 03:25 | 0.17796 | 0.11037 | 0.045952 | 0.21305 | 10.352 | 6.0709 | 1.2924 | 0.029043 | 452.128 | 23.6 | 57.38
2021-01-20 03:30 | 0.088973 | 0.15261 | 0.066834 | 0.30075 | 5.2672 | -11.1953 | 1.3068 | 0.021781 | 452.6652 | 23.62 | 57.09
2021-01-20 03:35 | 0.1398 | 0.203 | 0.091887 | 0.40305 | 2.7858 | 15.3525 | 1.2994 | 0.021778 | 452.6396 | 23.67 | 56.54
2021-01-20 03:40 | 0.38123 | 0.20843 | 0.079349 | 0.39883 | 10.1052 | 22.3045 | 1.2993 | 0.05081 | 452.5487 | 23.76 | 55.89
2021-01-20 03:45 | 0.63516 | 0.2315 | 0.079321 | 0.43418 | 10.2946 | -3.2825 | 1.3133 | 0.058048 | 454.1914 | 23.79 | 54.65
2021-01-20 03:50 | 0.62262 | 0.51761 | 0.10022 | 0.89363 | 12.7064 | 13.5908 | 1.3137 | 0.058063 | 453.9678 | 23.86 | 55.28
2021-01-20 03:55 | 0.63553 | 0.63087 | 0.14829 | 1.1153 | 12.5581 | 23.7943 | 1.3141 | 0.043562 | 453.0965 | 23.98 | 55.98
2021-01-20 04:00 | 0.47029 | 0.47962 | 0.11278 | 0.84796 | 13.412 | 3.4572 | 1.3068 | 0.065342 | 452.5508 | 23.99 | 55.89
2021-01-20 04:05 | 0.43219 | 0.52735 | 0.13368 | 0.94202 | 21.8839 | 7.9726 | 1.2997 | 0.065347 | 451.9185 | 24.03 | 56
2021-01-20 04:10 | 0.40689 | 0.47298 | 0.12745 | 0.85246 | 13.8138 | 11.9726 | 1.3001 | 0.058103 | 451.706 | 24.08 | 56.83
2021-01-20 04:15 | 0.38146 | 0.61611 | 0.17342 | 1.1178 | 16.0721 | 21.3921 | 1.3073 | 0.072629 | 451.537 | 24.19 | 56.47
2021-01-20 04:20 | 0.36877 | 0.6666 | 0.18388 | 1.2057 | 22.2179 | 15.5444 | 1.3002 | 0.036318 | 451.7939 | 24.35 | 56.2
2021-01-20 04:25 | 0.30523 | 0.59987 | 0.1233 | 1.0407 | 27.8164 | 32.1303 | 1.3003 | 0.058115 | 450.0685 | 24.39 | 56.45
2021-01-20 04:30 | 0.57222 | 0.72792 | 0.13791 | 1.2537 | 27.4868 | 31.6984 | 1.3074 | 0.079897 | 450.5799 | 24.45 | 55.78
2021-01-20 04:35 | 1.2334 | 0.97598 | 0.21103 | 1.7071 | 41.7679 | 34.1183 | 1.3074 | 0.09442 | 450.9662 | 24.56 | 55.3
2021-01-20 04:40 | 1.8564 | 1.2172 | 0.26743 | 2.1311 | 45.9261 | 53.6363 | 1.3073 | 0.14525 | 450.8079 | 24.68 | 54.74
2021-01-20 04:45 | 1.8305 | 1.0166 | 0.27573 | 1.834 | 51.7226 | 32.1461 | 1.307 | 0.14522 | 451.3243 | 24.76 | 53.77
2021-01-20 04:50 | 1.729 | 1.2647 | 0.31126 | 2.2499 | 62.7417 | 47.8928 | 1.3071 | 0.1525 | 448.9285 | 24.9 | 53.59
2021-01-20 04:55 | 2.3903 | 1.8359 | 0.47843 | 3.2926 | 73.4372 | 94.9598 | 1.3217 | 0.18156 | 447.0256 | 25.07 | 53.32
2021-01-20 05:00 | 3.3565 | 2.1862 | 0.51602 | 3.867 | 95.4056 | 88.3468 | 1.329 | 0.26144 | 448.2062 | 25.36 | 52.35
2021-01-20 05:05 | 4.0945 | 2.3596 | 0.57461 | 4.1915 | 94.9118 | 49.1141 | 1.3292 | 0.39222 | 446.7062 | 25.6 | 52.08
2021-01-20 05:10 | 4.3486 | 2.4822 | 0.55369 | 4.3584 | 87.9493 | 91.4791 | 1.3437 | 0.43578 | 445.9246 | 25.78 | 51.38
2021-01-20 05:15 | 3.0263 | 2.429 | 0.60801 | 4.3313 | 110.2682 | 125.8827 | 1.3437 | 0.37768 | 445.1927 | 25.91 | 51.01
2021-01-20 05:20 | 3.1411 | 2.7961 | 0.75647 | 5.0424 | 131.9024 | 103.5584 | 1.3511 | 0.43584 | 444.8938 | 26.07 | 50.93
2021-01-20 05:25 | 3.7767 | 3.2826 | 0.67492 | 5.7044 | 126.0439 | 99.8381 | 1.351 | 0.48666 | 445.2948 | 26.18 | 50.4
2021-01-20 05:30 | 4.4378 | 3.5742 | 0.64774 | 6.1263 | 130.0681 | 121.5231 | 1.3655 | 0.53022 | 444.6119 | 26.29 | 49.98
2021-01-20 05:35 | 6.4224 | 4.3872 | 0.96129 | 7.6861 | 144.2381 | 132.894 | 1.3584 | 0.55209 | 443.7168 | 26.43 | 50.01
2021-01-20 05:40 | 4.4364 | 3.588 | 0.93787 | 6.4398 | 144.2737 | 134.4908 | 1.3505 | 0.4284 | 444.929 | 26.47 | 48.58
2021-01-20 05:45 | 5.263 | 3.7886 | 0.90033 | 6.7076 | 167.4196 | 155.6732 | 1.3797 | 0.52282 | 443.2696 | 26.49 | 48.7
2021-01-20 05:50 | 5.2391 | 4.2108 | 0.91312 | 7.3635 | 186.419 | 162.2379 | 1.3873 | 0.61013 | 441.8849 | 26.62 | 49.13
2021-01-20 05:55 | 5.6212 | 4.0641 | 0.978 | 7.2055 | 173.6202 | 129.1087 | 1.3802 | 0.63199 | 445.4529 | 26.7 | 49.21
2021-01-20 06:00 | 5.5323 | 3.7029 | 0.84847 | 6.5244 | 167.8367 | 159.4021 | 1.3803 | 0.68286 | 443.7343 | 26.77 | 49.1
2021-01-20 06:05 | 6.9967 | 4.1757 | 0.85077 | 7.2535 | 191.7855 | 190.9612 | 1.4605 | 0.8211 | 443.5019 | 26.85 | 49.59
2021-01-20 06:10 | 5.3678 | 3.9135 | 0.75036 | 6.7491 | 203.3457 | 169.7448 | 1.4604 | 0.58125 | 442.8528 | 26.96 | 48.98
2021-01-20 06:15 | 6.435 | 3.7954 | 0.79827 | 6.616 | 183.7811 | 146.9313 | 1.4819 | 0.64651 | 445.0593 | 26.97 | 48.39
2021-01-20 06:20 | 5.0235 | 3.1997 | 0.75859 | 5.6633 | 177.4677 | 134.3802 | 1.4383 | 0.47945 | 443.9079 | 27.02 | 48.32
2021-01-20 06:25 | 5.6834 | 3.3952 | 0.75422 | 5.9585 | 138.6182 | 131.9965 | 1.4525 | 0.47206 | 444.5385 | 27.03 | 47.59
2021-01-20 06:30 | 5.124 | 3.9036 | 0.73751 | 6.7211 | 134.9062 | 141.4873 | 1.4816 | 0.47933 | 444.9508 | 27.11 | 47.38
2021-01-20 06:35 | 6.0645 | 3.4523 | 0.67688 | 5.9687 | 147.9279 | 122.9478 | 1.4234 | 0.46478 | 445.02 | 27.08 | 47.31
2021-01-20 06:40 | 4.7289 | 2.9353 | 0.72066 | 5.2201 | 146.0983 | 110.8398 | 1.4014 | 0.44293 | 443.4053 | 27.13 | 46.81
2021-01-20 06:45 | 4.563 | 2.9621 | 0.72472 | 5.2673 | 147.8655 | 137.1381 | 1.4448 | 0.51547 | 443.4585 | 27.14 | 46.36
2021-01-20 06:50 | 5.9229 | 3.6298 | 0.60567 | 6.1695 | 164.2552 | 147.5185 | 1.4593 | 0.56628 | 443.3442 | 27.22 | 46.12
2021-01-20 06:55 | 6.687 | 4.1021 | 0.75621 | 7.0441 | 170.8106 | 138.7029 | 1.416 | 0.52284 | 445.2439 | 27.31 | 46.48
2021-01-20 07:00 | 7.3488 | 3.9308 | 0.76255 | 6.7878 | 173.5221 | 148.9076 | 1.4089 | 0.61003 | 444.5955 | 27.36 | 46.6
2021-01-20 07:05 | 8.3775 | 3.61 | 0.69352 | 6.227 | 157.5938 | 134.7927 | 1.4232 | 0.63174 | 444.0613 | 27.4 | 46.14
2021-01-20 07:10 | 9.267 | 3.2733 | 0.67887 | 5.6962 | 153.1739 | 130.6687 | 1.4377 | 0.6898 | 445.5875 | 27.46 | 45.87
2021-01-20 07:15 | 8.4533 | 3.6588 | 0.65797 | 6.2664 | 158.1443 | 130.2904 | 1.4304 | 0.6317 | 445.4908 | 27.53 | 45.64
2021-01-20 07:20 | 6.2932 | 3.3445 | 0.64761 | 5.7742 | 171.7029 | 141.8313 | 1.4088 | 0.50107 | 443.214 | 27.59 | 45.84
2021-01-20 07:25 | 6.4449 | 3.4272 | 0.69975 | 5.9531 | 146.4615 | 115.4038 | 1.4086 | 0.51553 | 442.2625 | 27.55 | 45.62
2021-01-20 07:30 | 7.7283 | 3.2294 | 0.60154 | 5.5496 | 141.6423 | 102.7057 | 1.4231 | 0.58811 | 442.7344 | 27.61 | 45.29
2021-01-20 07:35 | 5.7829 | 3.1582 | 0.58685 | 5.4299 | 122.4595 | 95.9117 | 1.4229 | 0.57352 | 443.6703 | 27.67 | 44.86
2021-01-20 07:40 | 5.2998 | 3.2739 | 0.63278 | 5.6491 | 115.0139 | 98.502 | 1.4229 | 0.47913 | 444.7613 | 27.66 | 44.82
2021-01-20 07:45 | 5.5405 | 3.5446 | 0.66402 | 6.0973 | 138.6354 | 132.6882 | 1.4154 | 0.48633 | 443.2792 | 27.62 | 44.58
2021-01-20 07:50 | 4.7139 | 3.1505 | 0.62844 | 5.4576 | 157.0463 | 125.7997 | 1.4298 | 0.44998 | 444.8759 | 27.66 | 44.13
2021-01-20 07:55 | 3.8629 | 2.8837 | 0.59508 | 5.0133 | 141.8397 | 104.4102 | 1.4299 | 0.45001 | 443.2163 | 27.68 | 44.27
2021-01-20 08:00 | 5.2858 | 2.9422 | 0.60131 | 5.1111 | 122.8235 | 81.9603 | 1.4878 | 0.43547 | 444.9273 | 27.62 | 44.28
2021-01-20 08:05 | 5.8069 | 2.7216 | 0.54704 | 4.7167 | 95.5642 | 80.7229 | 1.4516 | 0.5008 | 444.3796 | 27.62 | 44.37
2021-01-20 08:10 | 6.5058 | 2.9613 | 0.59924 | 5.1364 | 92.1281 | 80.6718 | 1.4298 | 0.58064 | 444.3954 | 27.61 | 44.39
2021-01-20 08:15 | 6.0735 | 2.6302 | 0.52614 | 4.5578 | 99.8086 | 81.2171 | 1.437 | 0.54433 | 444.3713 | 27.64 | 44.19
2021-01-20 08:20 | 5.0818 | 2.6408 | 0.55739 | 4.6073 | 96.0763 | 80.211 | 1.4441 | 0.66037 | 444.4855 | 27.6 | 43.96
2021-01-20 08:25 | 5.1193 | 2.7126 | 0.5949 | 4.7529 | 99.5313 | 78.3527 | 1.4585 | 0.63127 | 444.593 | 27.56 | 43.77
2021-01-20 08:30 | 4.115 | 2.4984 | 0.54888 | 4.3806 | 108.8908 | 91.1708 | 1.4437 | 0.49332 | 444.158 | 27.55 | 43.29
2021-01-20 08:35 | 3.7849 | 2.7816 | 0.50297 | 4.7688 | 101.4952 | 73.848 | 1.4437 | 0.44254 | 443.6338 | 27.54 | 43.35
2021-01-20 08:40 | 4.9155 | 2.9696 | 0.49256 | 5.0445 | 108.0031 | 88.7172 | 1.4365 | 0.45707 | 444.1316 | 27.55 | 43.45
2021-01-20 08:45 | 4.8646 | 2.9397 | 0.51342 | 5.0194 | 126.2816 | 114.6472 | 1.4365 | 0.45706 | 443.6034 | 27.55 | 43.42
2021-01-20 08:50 | 4.7498 | 2.8386 | 0.58014 | 4.9312 | 138.3681 | 117.6316 | 1.4508 | 0.428 | 443.6232 | 27.57 | 43.07
2021-01-20 08:55 | 3.5428 | 2.6054 | 0.5133 | 4.507 | 114.5893 | 62.7397 | 1.4216 | 0.3264 | 445.265 | 27.58 | 42.7
2021-01-20 09:00 | 3.6942 | 2.8075 | 0.5528 | 4.8563 | 103.9559 | 86.4471 | 1.414 | 0.42783 | 444.8802 | 27.56 | 42.03
2021-01-20 09:05 | 3.5542 | 2.3786 | 0.54439 | 4.1904 | 115.6833 | 90.9463 | 1.4211 | 0.47128 | 445.8928 | 27.63 | 41.56
2021-01-20 09:10 | 3.325 | 2.355 | 0.50466 | 4.1165 | 104.5932 | 79.2419 | 1.4063 | 0.51468 | 444.9172 | 27.63 | 41.01
2021-01-20 09:15 | 3.5031 | 2.3035 | 0.4922 | 4.021 | 103.1022 | 67.7871 | 1.4137 | 0.41324 | 443.7852 | 27.64 | 41.29
2021-01-20 09:20 | 3.3891 | 2.2806 | 0.46096 | 3.9567 | 89.1682 | 55.3227 | 1.3921 | 0.44228 | 444.8604 | 27.61 | 41.58
2021-01-20 09:25 | 3.6415 | 2.4401 | 0.47536 | 4.2178 | 82.0056 | 59.3599 | 1.3988 | 0.44209 | 444.4967 | 27.62 | 40.44
2021-01-20 09:30 | 3.8959 | 2.1739 | 0.47335 | 3.8056 | 81.3587 | 44.4457 | 1.4062 | 0.45666 | 445.0193 | 27.58 | 40.96
2021-01-20 09:35 | 3.7429 | 1.9395 | 0.48369 | 3.4567 | 70.7572 | 57.6533 | 1.3915 | 0.43484 | 446.2415 | 27.53 | 40.59
2021-01-20 09:40 | 3.5645 | 1.9568 | 0.51068 | 3.5101 | 85.6999 | 75.1156 | 1.3912 | 0.36953 | 445.7606 | 27.56 | 39.93
2021-01-20 09:45 | 4.0083 | 1.9771 | 0.45229 | 3.487 | 93.1952 | 70.1907 | 1.3911 | 0.39125 | 445.7804 | 27.56 | 39.81
2021-01-20 09:50 | 5.0598 | 2.0895 | 0.46677 | 3.6716 | 95.7388 | 66.3283 | 1.4053 | 0.43461 | 446.4097 | 27.57 | 39.12
2021-01-20 09:55 | 5.3625 | 2.12 | 0.42912 | 3.6788 | 96.4382 | 74.7247 | 1.3976 | 0.34758 | 447.0727 | 27.58 | 38.23
2021-01-20 10:00 | 4.3464 | 2.3854 | 0.4331 | 4.0895 | 87.9114 | 70.4751 | 1.3752 | 0.33295 | 446.2131 | 27.57 | 37.08
2021-01-20 10:05 | 4.8403 | 2.6365 | 0.51219 | 4.5535 | 79.3811 | 53.4005 | 1.3607 | 0.40531 | 447.3235 | 27.56 | 36.94
2021-01-20 10:10 | 4.1187 | 2.0595 | 0.46229 | 3.6192 | 72.3058 | 36.7004 | 1.3536 | 0.39089 | 447.8236 | 27.54 | 37.37
2021-01-20 10:15 | 3.9278 | 2.0075 | 0.42681 | 3.5061 | 62.6217 | 55.1715 | 1.3606 | 0.4849 | 448.0008 | 27.48 | 36.97
2021-01-20 10:20 | 4.9416 | 2.3023 | 0.5101 | 4.0371 | 66.7696 | 42.2391 | 1.3462 | 0.50663 | 445.2241 | 27.54 | 36.93
2021-01-20 10:25 | 4.2815 | 2.8462 | 0.5724 | 4.9351 | 69.395 | 59.8492 | 1.3313 | 0.36177 | 446.3934 | 27.56 | 36.1
2021-01-20 10:30 | 2.5841 | 2.5638 | 0.55784 | 4.4898 | 69.0623 | 49.1493 | 1.3386 | 0.2243 | 446.8429 | 27.61 | 36.06
2021-01-20 10:35 | 2.7741 | 2.5502 | 0.61819 | 4.5272 | 83.7853 | 86.3694 | 1.3386 | 0.31836 | 446.3017 | 27.62 | 35.99
2021-01-20 10:40 | 3.2172 | 2.4454 | 0.5224 | 4.2708 | 88.7331 | 62.1041 | 1.3529 | 0.34004 | 445.2408 | 27.64 | 35.72
2021-01-20 10:45 | 3.4957 | 2.4657 | 0.52446 | 4.3039 | 83.2881 | 72.487 | 1.3746 | 0.31832 | 446.3297 | 27.64 | 35.6
2021-01-20 10:50 | 3.2296 | 1.9361 | 0.50779 | 3.4754 | 81.9675 | 41.4701 | 1.3673 | 0.28213 | 446.3629 | 27.63 | 35.51
2021-01-20 10:55 | 3.6351 | 1.7094 | 0.46204 | 3.0823 | 71.0604 | 49.7919 | 1.3746 | 0.36174 | 445.8118 | 27.62 | 35.72
2021-01-20 11:00 | 3.7612 | 1.9631 | 0.44533 | 3.4544 | 64.7996 | 38.1848 | 1.3889 | 0.37615 | 448.0416 | 27.6 | 35.39
2021-01-20 11:05 | 4.2424 | 2.4789 | 0.48486 | 4.2847 | 59.2067 | 40.4539 | 1.3599 | 0.38338 | 447.5103 | 27.6 | 35.37
2021-01-20 11:10 | 4.6736 | 2.3 | 0.3996 | 3.9252 | 69.2661 | 37.4702 | 1.3456 | 0.41237 | 445.3309 | 27.65 | 35.59
2021-01-20 11:15 | 4.3572 | 2.0205 | 0.44957 | 3.5487 | 64.4871 | 57.2622 | 1.3457 | 0.37622 | 446.3589 | 27.66 | 35.72
2021-01-20 11:20 | 3.2678 | 2.4046 | 0.5557 | 4.2437 | 75.4181 | 47.3199 | 1.3457 | 0.3328 | 446.3157 | 27.7 | 35.54
2021-01-20 11:25 | 2.838 | 2.9337 | 0.56835 | 5.0652 | 88.1096 | 68.8822 | 1.3461 | 0.31842 | 445.5636 | 27.76 | 36.19
2021-01-20 11:30 | 3.0408 | 3.0302 | 0.52464 | 5.1673 | 79.6482 | 43.1588 | 1.3968 | 0.34014 | 444.4415 | 27.79 | 36.19
2021-01-20 11:35 | 2.5972 | 2.5615 | 0.42053 | 4.3468 | 75.7928 | 41.2107 | 1.375 | 0.20263 | 444.9968 | 27.79 | 36.06
2021-01-20 11:40 | 2.8629 | 2.2176 | 0.44962 | 3.8488 | 85.6142 | 74.0408 | 1.3603 | 0.26049 | 445.6121 | 27.77 | 35.79
2021-01-20 11:45 | 3.8256 | 1.9364 | 0.44128 | 3.4095 | 80.1497 | 35.2663 | 1.4688 | 0.34008 | 445.594 | 27.79 | 35.68
2021-01-20 11:50 | 3.6861 | 2.0803 | 0.52036 | 3.7112 | 53.8195 | 39.6325 | 1.5122 | 0.28942 | 446.7379 | 27.75 | 35.66
2021-01-20 11:55 | 3.8251 | 2.1059 | 0.52447 | 3.7546 | 50.2476 | 27.8343 | 1.418 | 0.1881 | 446.2625 | 27.74 | 35.42
2021-01-20 12:00 | 3.1918 | 1.7977 | 0.56402 | 3.3175 | 53.4195 | 38.9906 | 1.3312 | 0.29662 | 446.2592 | 27.74 | 35.44
2021-01-20 12:05 | 2.774 | 1.7557 | 0.52242 | 3.2136 | 49.8148 | 23.0936 | 1.324 | 0.29664 | 445.7619 | 27.7 | 35.66
2021-01-20 12:10 | 3.1035 | 2.1048 | 0.49331 | 3.7196 | 69.335 | 60.0322 | 1.3313 | 0.33283 | 446.2723 | 27.7 | 35.8
2021-01-20 12:15 | 2.6089 | 2.0758 | 0.50986 | 3.6897 | 67.7205 | 59.0072 | 1.3311 | 0.34723 | 443.706 | 27.69 | 35.29
2021-01-20 12:20 | 2.3175 | 1.7554 | 0.51608 | 3.2047 | 61.1116 | 38.8026 | 1.331 | 0.29658 | 445.8484 | 27.7 | 35.14
2021-01-20 12:25 | 2.7863 | 1.5505 | 0.41415 | 2.7908 | 61.7859 | 33.4361 | 1.3384 | 0.2532 | 447.8991 | 27.73 | 35.32
2021-01-20 12:30 | 2.9387 | 1.3131 | 0.36424 | 2.3769 | 49.0757 | 37.8479 | 1.3385 | 0.246 | 445.223 | 27.7 | 35.69
2021-01-20 12:35 | 3.9135 | 1.4704 | 0.38917 | 2.643 | 42.757 | 33.547 | 1.3383 | 0.26043 | 445.8749 | 27.66 | 35.42
2021-01-20 12:40 | 2.647 | 1.5437 | 0.39541 | 2.7616 | 53.0304 | 28.5416 | 1.3239 | 0.23873 | 445.8483 | 27.68 | 35.36
2021-01-20 12:45 | 2.8492 | 1.8625 | 0.41824 | 3.2752 | 58.7165 | 42.5279 | 1.3164 | 0.24593 | 444.8418 | 27.68 | 34.99
2021-01-20 12:50 | 2.7604 | 2.0795 | 0.44318 | 3.6328 | 70.3821 | 57.6185 | 1.3308 | 0.29654 | 446.3994 | 27.73 | 34.71
2021-01-20 12:55 | 2.5196 | 2.3617 | 0.46187 | 4.0798 | 67.9854 | 36.6667 | 1.3307 | 0.27482 | 446.3801 | 27.77 | 34.39
2021-01-20 13:00 | 2.6337 | 2.3998 | 0.49311 | 4.1696 | 75.0306 | 64.4653 | 1.3308 | 0.32547 | 446.3615 | 27.76 | 34.61
2021-01-20 13:05 | 1.798 | 2.0374 | 0.37451 | 3.4955 | 68.4159 | 48.4199 | 1.3091 | 0.24591 | 446.9102 | 27.75 | 34.63
2021-01-20 13:10 | 1.9879 | 1.827 | 0.40155 | 3.202 | 65.2836 | 47.3243 | 1.3163 | 0.21697 | 445.8723 | 27.74 | 34.56
2021-01-20 13:15 | 2.5324 | 1.77 | 0.46189 | 3.175 | 63.4404 | 42.4118 | 1.3163 | 0.2893 | 443.8419 | 27.73 | 34.56
2021-01-20 13:20 | 3.2794 | 1.9681 | 0.49726 | 3.5099 | 63.8454 | 38.0763 |  |  | 443.8288 | 27.74 | 34.53
2021-01-20 13:25 | 3.0137 | 2.1461 | 0.55971 | 3.8493 | 68.783 | 59.4127 | 1.3164 | 0.28208 | 444.3027 | 27.76 | 34.67
2021-01-20 13:30 | 2.3675 | 2.3873 | 0.54922 | 4.2086 | 72.9747 | 56.1009 | 1.3162 | 0.25311 | 446.4374 | 27.81 | 34.12
2021-01-20 13:35 | 2.5323 | 2.3074 | 0.53261 | 4.0695 | 69.3534 | 42.0861 | 1.3162 | 0.26036 | 445.3405 | 27.81 | 34.3
2021-01-20 13:40 | 2.684 | 2.0711 | 0.51386 | 3.6885 | 62.0066 | 36.7057 | 1.3162 | 0.24588 | 445.9418 | 27.78 | 34.22
2021-01-20 13:45 | 2.7349 | 2.1622 | 0.53471 | 3.8491 | 63.3389 | 41.2164 | 1.3235 | 0.27483 | 444.3032 | 27.78 | 34.45
2021-01-20 13:50 | 2.6081 | 1.7386 | 0.44937 | 3.1144 | 57.5609 | 41.7096 | 1.3234 | 0.25311 | 444.9439 | 27.73 | 34.35
2021-01-20 13:55 | 2.2916 | 1.6816 | 0.44105 | 3.0208 | 60.0939 | 43.3207 | 1.3234 | 0.23865 | 447.1158 | 27.7 | 34.45
2021-01-20 14:00 | 2.5702 | 1.6762 | 0.4265 | 2.9959 | 72.0469 | 43.4733 | 1.3307 | 0.29651 | 445.4492 | 27.74 | 34.41
2021-01-20 14:05 | 3.4819 | 1.9342 | 0.43483 | 3.3996 | 69.0711 | 64.7054 | 1.3597 | 0.32545 | 446.4285 | 27.79 | 34.39
2021-01-20 14:10 | 3.5707 | 1.8691 | 0.42861 | 3.2937 | 76.4692 | 46.7993 | 1.3597 | 0.2893 | 444.7919 | 27.8 | 34.5
2021-01-20 14:15 | 3.3432 | 1.6847 | 0.44323 | 3.0235 | 71.0175 | 51.1407 | 1.3382 | 0.27487 | 444.7846 | 27.77 | 34.87
2021-01-20 14:20 | 3.6478 | 1.8086 | 0.4995 | 3.2718 | 67.3422 | 41.3923 | 1.324 | 0.3111 | 443.1179 | 27.76 | 35.38
2021-01-20 14:25 | 3.5339 | 1.886 | 0.50784 | 3.3988 | 74.3764 | 70.2016 | 1.324 | 0.33281 | 443.6098 | 27.78 | 35.41
2021-01-20 14:30 | 3.7613 | 1.7568 | 0.40788 | 3.1028 | 92.095 | 70.0186 | 1.3166 | 0.31106 | 445.7368 | 27.83 | 34.9
2021-01-20 14:35 | 3.6468 | 1.6099 | 0.38702 | 2.8548 | 87.3724 | 63.4551 | 1.3236 | 0.36888 | 447.4102 | 27.82 | 34.57
2021-01-20 14:40 | 4.0646 | 2.0252 | 0.38284 | 3.4872 | 75.0209 | 40.5089 | 1.338 | 0.54245 | 446.3753 | 27.81 | 34.49
2021-01-20 14:45 | 4.6979 | 2.1 | 0.45985 | 3.6767 | 71.7531 | 55.1191 | 1.3309 | 0.50631 | 445.802 | 27.82 | 34.62
2021-01-20 14:50 | 4.331 | 1.8463 | 0.46196 | 3.292 | 64.6964 | 42.9047 | 1.3237 | 0.39061 | 444.159 | 27.83 | 34.77
2021-01-20 14:55 | 3.9889 | 2.0457 | 0.46194 | 3.5977 | 69.7691 | 53.8135 | 1.3164 | 0.33996 | 444.1034 | 27.88 | 34.56
2021-01-20 15:00 | 3.9002 | 2.0946 | 0.48482 | 3.6934 | 68.0148 | 53.569 | 1.3164 | 0.31825 | 446.1143 | 27.97 | 34.31
2021-01-20 15:05 | 3.3685 | 2.7531 | 0.57848 | 4.7985 | 71.6146 | 67.2583 | 1.3237 | 0.3255 | 444.3901 | 28.04 | 34.3
2021-01-20 15:10 | 2.7605 | 2.5928 | 0.54308 | 4.5132 | 88.8129 | 71.1556 | 1.3309 | 0.31826 | 444.8384 | 28.11 | 34.05
2021-01-20 15:15 | 3.3429 | 1.9303 | 0.49105 | 3.4498 | 87.027 | 61.4689 | 1.3308 | 0.29655 | 446.4816 | 28.09 | 34
2021-01-20 15:20 | 2.9504 | 1.5855 | 0.42447 | 2.8548 | 79.2784 | 52.464 | 1.3236 | 0.28932 | 444.3747 | 28.07 | 34.07
2021-01-20 15:25 | 3.6215 | 2.138 | 0.50146 | 3.7786 | 80.96 | 63.9515 | 1.3453 | 0.32548 | 444.3747 | 28.07 | 34.07
2021-01-20 15:30 | 4.0648 | 2.6281 | 0.50563 | 4.5361 | 78.8547 | 45.3536 | 1.3671 | 0.34719 | 442.7221 | 28.1 | 34.07
2021-01-20 15:35 | 4.0527 | 2.3922 | 0.49737 | 4.1642 | 65.9072 | 59.3722 | 1.3817 | 0.39064 | 444.2462 | 28.17 | 34.26
2021-01-20 15:40 | 2.9636 | 1.9822 | 0.43494 | 3.4712 | 82.017 | 75.7657 | 1.36 | 0.3183 | 444.1856 | 28.21 | 34.19
2021-01-20 15:45 | 3.1155 | 1.9591 | 0.44535 | 3.4483 | 64.3266 | 65.0257 | 1.3238 | 0.30383 | 444.7193 | 28.21 | 34.18
2021-01-20 15:50 | 2.6345 | 1.9525 | 0.45579 | 3.4465 | 72.1235 | 66.2568 | 1.3167 | 0.23151 | 444.6407 | 28.24 | 34.32
2021-01-20 15:55 | 2.9514 | 2.1305 | 0.53493 | 3.8007 | 90.2898 | 79.3658 | 1.3096 | 0.25324 | 444.583 | 28.25 | 34.55
2021-01-20 16:00 | 5.0541 | 2.3845 | 0.5266 | 4.1816 | 113.2317 | 86.2563 | 1.3747 | 0.35453 | 443.4328 | 28.31 | 34.42
2021-01-20 16:05 | 6.46 | 2.4985 | 0.53492 | 4.3647 | 118.6918 | 88.8491 | 1.3675 | 0.52093 | 443.3662 | 28.36 | 34.28
2021-01-20 16:10 | 4.9653 | 2.3491 | 0.52867 | 4.1274 | 99.6715 | 65.7349 | 1.3602 | 0.47752 | 443.3221 | 28.39 | 34.22
2021-01-20 16:15 | 3.7364 | 2.0964 | 0.47453 | 3.688 | 87.6276 | 51.2107 | 1.3818 | 0.36174 | 443.3937 | 28.36 | 34.12
2021-01-20 16:20 | 3.6602 | 1.9659 | 0.47866 | 3.4921 | 84.0449 | 60.7616 | 1.3962 | 0.33278 | 444.0153 | 28.32 | 34.02
2021-01-20 16:25 | 3.7997 | 1.8452 | 0.41832 | 3.2467 | 96.421 | 68.9011 | 1.3673 | 0.27492 | 443.9929 | 28.32 | 34.15
2021-01-20 16:30 | 4.3571 | 2.0543 | 0.42458 | 3.5735 | 84.7202 | 46.2967 | 1.3312 | 0.38344 | 443.4932 | 28.29 | 34.28
2021-01-20 16:35 | 5.9404 | 2.0272 | 0.4454 | 3.5528 | 82.5423 | 76.0471 | 1.3095 | 0.52091 | 443.4456 | 28.32 | 34.24
2021-01-20 16:40 | 6.8143 | 1.8045 | 0.45372 | 3.2176 | 86.3921 | 57.6657 | 1.3312 | 0.47026 | 443.4784 | 28.3 | 34.26
2021-01-20 16:45 | 6.2443 | 1.776 | 0.42041 | 3.1427 | 88.4687 | 58.7494 | 1.3384 | 0.45579 | 442.3891 | 28.32 | 34.2
2021-01-20 16:50 | 6.3833 | 1.617 | 0.43912 | 2.9178 | 65.2207 | 53.7916 | 1.3818 | 0.42683 | 444.5254 | 28.33 | 34.04
2021-01-20 16:55 | 5.8258 | 1.655 | 0.39957 | 2.9385 | 63.0507 | 60.0213 | 1.3745 | 0.34724 | 444.5963 | 28.29 | 34.05
2021-01-20 17:00 | 4.8003 | 1.7542 | 0.40792 | 3.0969 | 81.9324 | 63.106 | 1.3457 | 0.31833 | 445.0658 | 28.31 | 34.2
2021-01-20 17:05 | 4.0154 | 1.6621 | 0.41837 | 2.966 | 75.5154 | 53.7383 | 1.3385 | 0.28941 | 444.5074 | 28.3 | 34.46
2021-01-20 17:10 | 3.9771 | 1.9579 | 0.45996 | 3.4632 | 73.472 | 55.2737 | 1.3384 | 0.26045 | 444.5913 | 28.27 | 34.29
2021-01-20 17:15 | 4.2936 | 1.8995 | 0.47243 | 3.384 | 74.6954 | 49.0607 | 1.3311 | 0.29661 | 443.5285 | 28.28 | 34.18
2021-01-20 17:20 | 4.1672 | 1.4936 | 0.37464 | 2.6641 | 84.885 | 89.0294 | 1.3312 | 0.2894 | 443.0359 | 28.23 | 34.48
2021-01-20 17:25 | 3.9136 | 1.1758 | 0.31218 | 2.1145 | 86.5307 | 52.5061 | 1.3167 | 0.28215 | 444.2631 | 28.14 | 34.48
2021-01-20 17:30 | 3.6099 | 1.146 | 0.33509 | 2.0917 | 67.9523 | 43.3897 | 1.3385 | 0.31834 | 443.7759 | 28.09 | 34.75
2021-01-20 17:35 | 2.9894 | 1.3375 | 0.35177 | 2.402 | 50.476 | 12.1199 | 1.3458 | 0.26048 | 444.8112 | 28.09 | 34.92
2021-01-20 17:40 | 3.8509 | 1.3091 | 0.34553 | 2.3521 | 42.8866 | 38.8736 | 1.3386 | 0.27495 | 443.857 | 28.01 | 35.13
2021-01-20 17:45 | 3.8003 | 1.2005 | 0.33097 | 2.1711 | 57.6939 | 60.1363 | 1.3242 | 0.25325 | 444.4796 | 27.94 | 35.35
2021-01-20 17:50 | 3.1669 | 0.97637 | 0.25186 | 1.7485 | 71.1102 | 42.9884 | 1.3024 | 0.21707 | 444.5475 | 27.9 | 35.38
2021-01-20 17:55 | 2.2041 | 1.0062 | 0.26851 | 1.8088 | 76.7737 | 42.5822 | 1.3024 | 0.21707 | 445.7832 | 27.79 | 35.56
2021-01-20 18:00 | 1.6974 | 0.87044 | 0.27684 | 1.6111 | 60.7425 | 24.4835 | 1.3024 | 0.18089 | 445.9577 | 27.67 | 35.83
2021-01-20 18:05 | 2.0395 | 1.0959 | 0.27477 | 1.9546 | 47.6613 | 33.8281 | 1.3097 | 0.2026 | 447.0818 | 27.62 | 36.03
2021-01-20 18:10 | 1.8368 | 1.2887 | 0.31223 | 2.2876 | 48.7253 | 26.2679 | 1.3024 | 0.21707 | 445.4698 | 27.63 | 36
2021-01-20 18:15 | 2.3942 | 1.2941 | 0.27476 | 2.2585 | 36.7966 | 33.9996 | 1.3169 | 0.27496 | 445.4931 | 27.62 | 35.97
2021-01-20 18:20 | 2.4067 | 0.95594 | 0.25185 | 1.7171 | 41.2732 | 26.9142 | 1.324 | 0.28217 | 445.6845 | 27.51 | 36.03
2021-01-20 18:25 | 2.0773 | 0.7319 | 0.20814 | 1.33 | 31.14 | 17.3687 | 1.3096 | 0.23153 | 445.9049 | 27.36 | 36.36
2021-01-20 18:30 | 2.508 | 0.90299 | 0.21855 | 1.6027 | 35.4772 | 14.7441 | 1.3168 | 0.27494 | 446.5859 | 27.26 | 36.58
2021-01-20 18:35 | 2.3815 | 0.79714 | 0.21232 | 1.4342 | 28.0111 | 18.799 | 1.3097 | 0.23878 | 447.602 | 27.27 | 36.78
2021-01-20 18:40 | 2.0904 | 0.7266 | 0.20193 | 1.3157 | 18.274 | 5.6251 | 1.3026 | 0.17368 | 447.7489 | 27.14 | 37.35
2021-01-20 18:45 | 2.3312 | 0.81084 | 0.19986 | 1.4427 | 21.204 | 21.4269 | 1.3171 | 0.18816 | 446.7822 | 27.06 | 37.64
2021-01-20 18:50 | 1.6724 | 0.66415 | 0.16447 | 1.1846 | 21.5281 | 14.2912 | 1.3026 | 0.15921 | 446.3717 | 26.98 | 37.79
2021-01-20 18:55 | 1.2416 | 0.56093 | 0.17071 | 1.0305 | 13.3891 | 10.0647 | 1.2954 | 0.2171 | 447.0703 | 26.87 | 38.03
2021-01-20 19:00 | 0.98822 | 0.52969 | 0.17279 | 0.9868 | 14.3317 | 6.1118 | 1.3026 | 0.1375 | 448.2442 | 26.8 | 38.18
2021-01-20 19:05 | 0.72219 | 0.46994 | 0.15198 | 0.87233 | 15.802 | 22.887 | 1.3099 | 0.11579 | 447.3374 | 26.68 | 38.56
2021-01-20 19:10 | 0.89959 | 0.59763 | 0.16864 | 1.0847 | 26.2834 | 12.9542 | 1.2955 | 0.094085 | 446.8347 | 26.65 | 38.71
2021-01-20 19:15 | 0.91222 | 0.62205 | 0.11867 | 1.0722 | 31.289 | 33.2047 | 1.2954 | 0.09408 | 447.4374 | 26.62 | 38.63
2021-01-20 19:20 | 0.83622 | 0.50118 | 0.11451 | 0.88274 | 30.7525 | 28.3402 | 1.2954 | 0.094082 | 447.517 | 26.56 | 38.83
2021-01-20 19:25 | 0.82358 | 0.65333 | 0.14366 | 1.143 | 34.3624 | 21.3776 | 1.3172 | 0.057899 | 447.5582 | 26.52 | 39.04
2021-01-20 19:30 | 0.92494 | 0.6737 | 0.17072 | 1.2034 | 27.6012 | 12.0622 | 1.2882 | 0.094085 | 447.6508 | 26.46 | 39.16
2021-01-20 19:35 | 0.79822 | 0.46995 | 0.13949 | 0.86194 | 24.5498 | 12.7919 | 1.2955 | 0.10132 | 448.7715 | 26.43 | 39.19
2021-01-20 19:40 | 0.65887 | 0.3776 | 0.12909 | 0.70997 | 23.4153 | 10.1973 | 1.3027 | 0.086849 | 446.7829 | 26.32 | 39.53
2021-01-20 19:45 | 0.65887 | 0.35723 | 0.14782 | 0.69748 | 27.5103 | 27.0947 | 1.3027 | 0.086849 | 447.8855 | 26.3 | 39.56
2021-01-20 19:50 | 0.87429 | 0.3912 | 0.13117 | 0.7329 | 14.6882 | -7.1363 | 1.2955 | 0.094089 | 446.786 | 26.31 | 39.63
2021-01-20 19:55 | 1.4699 | 0.51892 | 0.11661 | 0.91202 | 23.4379 | 6.4576 | 1.2884 | 0.19543 | 447.9431 | 26.23 | 40.03
2021-01-20 20:00 | 1.1785 | 0.47002 | 0.10828 | 0.82873 | 13.9492 | 10.9789 | 1.3101 | 0.12305 | 447.5119 | 26.16 | 40.2
2021-01-20 20:05 | 1.7361 | 0.51079 | 0.11453 | 0.89748 | 175.8418 | 498.2269 | 1.3102 | 0.14477 | 354.4979 | 26.04 | 40.6
2021-01-20 20:10 | 2.1543 | 0.75665 | 0.13951 | 1.2993 | 201.5569 | 122.8887 | 1.3101 | 0.152 | 352.3643 | 26.04 | 40.53
2021-01-20 20:15 | 1.4192 | 0.68736 | 0.16033 | 1.2139 | 105.6123 | 41.1987 | 1.3029 | 0.18819 | 352.2527 | 26.14 | 40.24
2021-01-20 20:20 | 1.0391 | 0.46595 | 0.13951 | 0.85581 | 56.781 | 25.0197 | 1.3101 | 0.39811 | 352.7233 | 26.19 | 40.17
2021-01-20 20:25 | 0.9504 | 0.41025 | 0.11661 | 0.74545 | 43.024 | 19.5757 | 1.3029 | 0.23162 | 353.2953 | 26.16 | 40.23
2021-01-20 20:30 | 1.0011 | 0.39395 | 0.13118 | 0.73504 | 26.4895 | 16.7473 | 1.3174 | 0.152 | 352.7135 | 26.2 | 40.13
2021-01-20 20:35 | 0.70965 | 0.3926 | 0.11869 | 0.72048 | 19.3734 | 15.2574 | 1.3174 | 0.11581 | 352.6585 | 26.24 | 40.1
2021-01-20 20:40 | 0.58298 | 0.42252 | 0.10413 | 0.75179 | 22.3257 | 23.4815 | 1.3248 | 0.11583 | 354.0574 | 26.23 | 40.45
2021-01-20 20:45 | 0.95054 | 0.62225 | 0.13745 | 1.0913 | 25.1753 | 22.2248 | 1.3176 | 0.1665 | 354.0723 | 26.21 | 40.57
2021-01-20 20:50 | 1.0266 | 0.59918 | 0.091636 | 1.0101 | 30.2255 | 27.9239 | 1.3248 | 0.16651 | 354.0257 | 26.24 | 40.59
2021-01-20 20:55 | 1.0394 | 0.45519 | 0.11455 | 0.81228 | 32.1541 | 23.89 | 1.3249 | 0.15928 | 352.4659 | 26.18 | 40.93
2021-01-20 21:00 | 1.217 | 0.41449 | 0.10832 | 0.74366 | 25.6379 | 22.5143 | 1.3324 | 0.18103 | 353.0312 | 26.11 | 41.54
2021-01-20 21:05 | 1.61 | 0.39954 | 0.12082 | 0.73325 | 17.18 | 10.9429 | 1.3396 | 0.18827 | 353.0634 | 26.08 | 41.64
2021-01-20 21:10 | 1.141 | 0.37103 | 0.13541 | 0.70413 | 19.0574 | 1.5721 | 1.3469 | 0.15207 | 354.112 | 26.08 | 41.83
2021-01-20 21:15 | 0.95086 | 0.36424 | 0.11666 | 0.67498 | 17.2423 | 4.4221 | 1.3614 | 0.16656 | 352.0806 | 25.98 | 42.13
2021-01-20 21:20 | 0.82409 | 0.37104 | 0.10625 | 0.67499 | 8.3474 | 16.7454 | 1.3615 | 0.15932 | 352.7197 | 25.89 | 42.38
2021-01-20 21:25 | 1.0395 | 0.29627 | 0.11041 | 0.56662 | 10.9736 | 1.6633 | 1.3541 | 0.18828 | 353.3729 | 25.81 | 42.39
2021-01-20 21:30 | 0.86211 | 0.25007 | 0.066664 | 0.45207 | 8.5602 | 7.0794 | 1.3614 | 0.14483 | 354.0214 | 25.7 | 42.82
2021-01-20 21:35 | 0.88754 | 0.23107 | 0.068754 | 0.42086 | 13.2269 | 6.8366 | 1.3543 | 0.19554 | 354.1327 | 25.58 | 43.39
2021-01-20 21:40 | 1.3441 | 0.30856 | 0.085425 | 0.56047 | 8.8759 | 15.7636 | 1.3689 | 0.21728 | 353.6139 | 25.55 | 43.62
2021-01-20 21:45 | 1.306 | 0.29903 | 0.089589 | 0.54795 | 16.0267 | 11.2795 | 1.3761 | 0.20279 | 354.1519 | 25.56 | 43.48
2021-01-20 21:50 | 0.91297 | 0.23924 | 0.064592 | 0.42922 | 16.0277 | 11.0165 | 1.3834 | 0.18107 | 353.2882 | 25.52 | 43.74
2021-01-20 21:55 | 1.116 | 0.28276 | 0.083352 | 0.51678 | 14.0205 | 13.3509 | 1.3835 | 0.27526 | 353.803 | 25.51 | 44.05
2021-01-20 22:00 | 0.913 | 0.2474 | 0.068761 | 0.45007 | 14.0703 | 20.6641 | 1.3689 | 0.26799 | 353.386 | 25.43 | 44.05
2021-01-20 22:05 | 1.0145 | 0.36704 | 0.10836 | 0.67097 | 20.7971 | 14.3348 | 1.3763 | 0.34044 | 352.8665 | 25.4 | 44.29
2021-01-20 22:10 | 0.92575 | 0.2583 | 0.091689 | 0.48762 | 20.047 | -8.2582 | 1.3691 | 0.27526 | 354.4878 | 25.38 | 44.44
2021-01-20 22:15 | 0.8496 | 0.28954 | 0.087515 | 0.53342 | 4.7172 | 10.1648 | 1.3617 | 0.19557 | 353.5126 | 25.32 | 44.37
2021-01-20 22:20 | 0.596 | 0.21614 | 0.075014 | 0.40633 | 8.5317 | 12.9447 | 1.3545 | 0.15935 | 353.587 | 25.25 | 44.63
2021-01-20 22:25 | 0.58335 | 0.25286 | 0.091688 | 0.47928 | 17.8555 | 8.5016 | 1.3546 | 0.14487 | 353.6202 | 25.21 | 44.86
2021-01-20 22:30 | 0.55799 | 0.20664 | 0.08127 | 0.39802 | 9.4757 | -0.13189 | 1.3546 | 0.13039 | 353.6616 | 25.17 | 45.02
2021-01-20 22:35 | 0.83696 | 0.26373 | 0.095854 | 0.50011 | 6.7464 | 13.7364 | 1.3618 | 0.15936 | 354.7096 | 25.2 | 44.85
2021-01-20 22:40 | 0.71003 | 0.16446 | 0.07292 | 0.32502 | 12.1111 | 12.0604 | 1.3688 | 0.1883 | 353.7198 | 25.18 | 44.38
2021-01-20 22:45 | 0.53254 | 0.12777 | 0.075005 | 0.27085 | 13.1866 | -1.7244 | 1.3688 | 0.15209 | 353.8425 | 25.07 | 44.74
2021-01-20 22:50 | 0.4438 | 0.21341 | 0.079176 | 0.40422 | 5.3763 | 1.8361 | 1.3544 | 0.10864 | 354.4453 | 25 | 45.08
2021-01-20 22:55 | 0.40572 | 0.1699 | 0.072918 | 0.33334 | -4.5847 | -2.059 | 1.3543 | 0.10139 | 353.9905 | 24.96 | 44.88
2021-01-20 23:00 | 0.36772 | 0.1468 | 0.068757 | 0.29378 | 3.7127 | 4.3923 | 1.3616 | 0.086913 | 353.5541 | 24.85 | 45.44
2021-01-20 23:05 | 0.60864 | 0.18215 | 0.056257 | 0.33546 | 11.1788 | 0.010144 | 1.3617 | 0.1014 | 354.1448 | 24.8 | 45.63
2021-01-20 23:10 | 0.50715 | 0.15494 | 0.037501 | 0.27709 | -0.64915 | -6.2176 | 1.3543 | 0.10139 | 354.2429 | 24.75 | 45.42
2021-01-20 23:15 | 0.5071 | 0.12367 | 0.049996 | 0.23956 | -9.7059 | -5.2738 | 1.3614 | 0.094138 | 354.4196 | 24.63 | 45.44
2021-01-20 23:20 | 0.77334 | 0.22288 | 0.066663 | 0.40831 | 4.0264 | -4.1583 | 1.3831 | 0.072415 | 354.4246 | 24.62 | 45.53
2021-01-20 23:25 | 0.49445 | 0.18212 | 0.064582 | 0.34374 | 5.69 | -4.4424 | 1.3687 | 0.07966 | 354.9375 | 24.63 | 45.62
2021-01-20 23:30 | 0.60851 | 0.41314 | 0.064578 | 0.69785 | 2.2921 | 9.7159 | 1.3831 | 0.094137 | 354.984 | 24.61 | 45.47
2021-01-20 23:35 | 0.50708 | 0.31256 | 0.068741 | 0.54785 | 2.2616 | 0.58821 | 1.3758 | 0.086893 | 353.8742 | 24.65 | 45.24
2021-01-20 23:40 | 0.38029 | 0.28945 | 0.064572 | 0.50825 | 0.52734 | -6.7337 | 1.3685 | 0.079648 | 353.9012 | 24.64 | 45.13
2021-01-20 23:45 | 0.46901 | 0.21062 | 0.058322 | 0.38117 | 9.4816 | -1.7442 | 1.3612 | 0.079646 | 355.0354 | 24.6 | 45.14
2021-01-20 23:50 |  | 0.26634 | 0.060405 | 0.46866 | 0.38535 | 8.8428 | 1.3612 | 0.072405 | 355.1062 | 24.54 | 45.31
2021-01-20 23:55 | 0.26619 | 0.25547 | 0.04999 | 0.44158 | -11.4894 | -5.1413 | 1.3395 | 0.079645 | 352.9919 | 24.51 | 45.37
2021-01-21 | 0.20281 | 0.15355 | 0.043739 | 0.2791 | -3.3666 | -8.8627 | 1.3467 | 0.079642 | 355.2295 | 24.45 | 45.41
2021-01-21 00:05 | 0.17747 | 0.15492 | 0.049992 | 0.28745 | 1.0243 | -4.4216 | 1.354 | 0.079649 | 354.243 | 24.35 | 45.95
2021-01-21 00:10 | 0.21551 | 0.13861 | 0.049993 | 0.26246 | -4.3202 | -12.2711 | 1.3468 | 0.079651 | 352.8301 | 24.33 | 46.04
2021-01-21 00:15 | 0.17748 | 0.10057 | 0.043746 | 0.1979 | -4.6856 | 0.10142 | 1.3469 | 0.072413 | 354.4624 | 24.3 | 46.28
2021-01-21 00:20 | 0.24086 | 0.15764 | 0.047911 | 0.28955 | 8.6102 | 7.0281 | 1.3396 | 0.079652 | 354.4488 | 24.32 | 46.13
2021-01-21 00:25 | 0.25352 | 0.11279 | 0.04999 | 0.22287 | 3.4276 | 0.52732 | 1.3395 | 0.057924 | 353.9287 | 24.33 | 45.83
2021-01-21 00:30 | 0.11408 | 0.088321 | 0.045821 | 0.1812 | -4.1777 | 1.7745 | 1.3467 | 0.05068 | 355.5886 | 24.31 | 45.68
2021-01-21 00:35 | 0.17744 | 0.088316 | 0.047902 | 0.18119 | 1.3993 | 6.4387 | 1.3466 | 0.050678 | 354.601 | 24.25 | 45.69
2021-01-21 00:40 | 0.20279 | 0.12228 | 0.052067 | 0.24159 | 10.383 | 1.815 | 1.3466 | 0.065158 | 355.1624 | 24.23 | 45.75
2021-01-21 00:45 | 0.25349 | 0.13179 | 0.045819 | 0.24784 | 5.2928 | -8.1927 | 1.3393 | 0.065157 | 354.6053 | 24.25 | 45.65
2021-01-21 00:50 | 0.19012 | 0.089676 | 0.047902 | 0.18536 | -5.5363 | -9.288 | 1.3394 | 0.050678 | 353.5934 | 24.19 | 45.88
2021-01-21 00:55 | 0.11407 | 0.088317 | 0.049985 | 0.18536 | -4.5527 | -11.2044 | 1.3394 | 0.065158 | 354.7303 | 24.14 | 46.01
2021-01-21 01:00 | 0.088722 | 0.070653 | 0.058315 | 0.16661 | -0.38531 | 1.7339 | 1.3538 | 0.036199 | 354.7802 | 24.1 | 46.1
2021-01-21 01:05 |  |  |  |  | 0.040558 | -1.7237 |  |  | 352.5995 | 24.13 | 45.94
2021-01-21 01:10 |  |  |  |  | -2.5348 | -4.9985 |  |  | 354.24 | 24.12 | 45.84
2021-01-21 01:15 |  |  |  |  | 0.43597 | -2.7882 |  |  | 353.778 | 24.06 | 45.96
2021-01-21 01:20 |  |  |  |  | 7.9298 | -3.9345 |  |  | 353.75 | 24.04 | 46.5
2021-01-21 01:25 |  |  |  |  | 10.9023 | 3.6916 |  |  | 355.2956 | 24.06 | 46.87
2021-01-21 01:30 |  |  |  |  | 4.9999 | 7.7483 |  |  | 355.4262 | 23.95 | 47.19
2021-01-21 01:35 |  |  |  |  | 11.7861 | 7.1407 |  |  | 354.3044 | 23.95 | 47.61
2021-01-21 01:40 |  |  |  |  | 15.5209 | 17.1136 |  |  | 355.1175 | 24.13 | 47.55
2021-01-21 01:45 |  |  |  |  | 8.3295 | 2.1813 |  |  | 354.1173 | 24.03 | 48.24
2021-01-21 01:50 |  |  |  |  | 1.4713 | -1.3698 |  |  | 354.7733 | 23.9 | 48.97
2021-01-21 01:55 |  |  |  |  | 7.7394 | -1.4607 |  |  | 353.8571 | 23.86 | 48.02
2021-01-21 02:00 |  |  |  |  | 12.7395 | 3.5196 |  |  | 355.9209 | 23.95 | 47.6
2021-01-21 02:05 |  |  |  |  | 4.4533 | 0.8724 |  |  | 354.8368 | 23.92 | 48.09
2021-01-21 02:10 | 0.48187 | 0.2311 | 0.043758 | 0.39799 | -4.2303 | 6.2998 | 1.4487 | 0.036216 | 354.8435 | 23.9 | 48.31
2021-01-21 02:15 | 0.5073 | 0.13732 | 0.035428 | 0.24591 | 4.0787 | -3.4192 | 1.4344 | 0.043465 | 355.8973 | 23.88 | 48.81
2021-01-21 02:20 | 0.46932 | 0.096543 | 0.041686 | 0.18967 | 12.1059 | 1.4612 | 1.4201 | 0.10143 | 355.9658 | 23.78 | 49.59
2021-01-21 02:25 | 0.32974 | 0.12372 | 0.062519 | 0.25216 | 8.1574 | 1.9379 | 1.4126 | 0.10142 | 354.9772 | 23.75 | 49.18
2021-01-21 02:30 | 0.22822 | 0.14 | 0.081254 | 0.29585 | 1.9475 | 9.3826 | 1.4195 | 0.10863 | 356.1 | 23.79 | 48.18
2021-01-21 02:35 | 0.25356 | 0.1427 | 0.047915 | 0.26874 | 9.615 | 3.0732 | 1.4194 | 0.10863 | 353.4732 | 23.76 | 47.97
2021-01-21 02:40 | 0.20285 | 0.12368 | 0.056248 | 0.24582 | 13.1649 | 6.623 | 1.4266 | 0.10863 | 354.011 | 23.76 | 47.98
2021-01-21 02:45 | 0.20283 | 0.11279 | 0.056242 | 0.22914 | 2.9613 | -0.030424 | 1.4337 | 0.10861 | 355.1718 | 23.72 | 47.76
2021-01-21 02:50 | 0.17747 | 0.14132 | 0.058323 | 0.27495 | -2.1397 | 3.6812 | 1.4336 | 0.11585 | 355.165 | 23.74 | 47.54
2021-01-21 02:55 | 0.19015 | 0.13317 | 0.058324 | 0.26246 | 1.724 | -2.2108 | 1.4409 | 0.14482 | 355.1952 | 23.71 | 47.68
2021-01-21 03:00 | 0.22818 | 0.13725 | 0.056242 | 0.26663 | 5.4053 | -0.99385 | 1.4409 | 0.15206 | 355.7397 | 23.7 | 47.77
2021-01-21 03:05 | 0.20282 | 0.13589 | 0.047909 | 0.25412 | 6.2976 | 6.2266 | 1.4481 | 0.13033 | 355.2673 | 23.65 | 47.85
2021-01-21 03:10 | 0.16479 | 0.18617 | 0.052074 | 0.33952 | -4.675 | -8.5692 | 1.4554 | 0.15205 | 353.8636 | 23.63 | 47.83
2021-01-21 03:15 | 0.2662 | 0.36826 | 0.081235 | 0.64572 | 3.5493 | 4.7358 | 1.4626 | 0.17378 | 355.3611 | 23.73 | 47.53
2021-01-21 03:20 | 0.26619 | 0.35602 | 0.10415 | 0.64987 | 8.6602 | 3.5797 | 1.4698 | 0.18101 | 354.6758 | 23.86 | 47.08
2021-01-21 03:25 | 0.29154 | 0.32341 | 0.10206 | 0.59779 | 12.5136 | 8.4979 | 1.4843 | 0.18101 | 355.169 | 23.9 | 46.94
2021-01-21 03:30 | 0.27886 | 0.27992 | 0.087479 | 0.51654 | 5.4353 | 8.2239 | 1.4843 | 0.16653 | 354.6746 | 23.87 | 46.95
2021-01-21 03:35 | 0.27886 | 0.35193 | 0.068734 | 0.60819 | -1.7036 | 0.53744 | 1.4843 | 0.17377 | 354.6746 | 23.87 | 46.95
2021-01-21 03:40 | 0.24083 | 0.42122 | 0.085393 | 0.73105 | 6.4997 | 5.435 | 1.4914 | 0.15204 | 353.5768 | 23.9 | 46.73
2021-01-21 03:45 | 0.32956 | 0.44704 | 0.10206 | 0.78522 | 15.8593 | 3.4375 | 1.4842 | 0.13756 | 353.4143 | 24.03 | 46.44
2021-01-21 03:50 | 0.32954 | 0.52446 | 0.14787 | 0.95179 |  |  | 1.4769 | 0.16651 | 479.0901 | 24.17 | 45.86
2021-01-21 03:55 | 0.76047 | 0.63859 | 0.1562 | 1.1351 |  |  | 1.4841 | 0.18823 | 502.6694 | 24.22 | 45.69
2021-01-21 04:00 | 0.70978 | 0.54893 | 0.14995 | 0.98928 |  | -2.464 | 1.4842 | 0.16652 | 502.3073 | 24.11 | 46.06
2021-01-21 04:05 | 0.57035 | 0.47011 | 0.11246 | 0.83306 | -7.6046 | -8.5983 | 1.4841 | 0.17375 | 503.6834 | 23.94 | 46.45
2021-01-21 04:10 | 0.51965 | 0.47554 | 0.11871 | 0.84763 | 15.4221 | 7.9189 | 1.4769 | 0.14479 | 501.7542 | 23.81 | 46.79
2021-01-21 04:15 | 0.43098 | 0.66583 | 0.14788 | 1.1685 | 21.853 | 30.0162 | 1.477 | 0.15205 | 502.2342 | 23.81 | 47.18
2021-01-21 04:20 | 0.44362 | 0.77313 | 0.18536 | 1.3725 | 34.0296 | 30.8152 | 1.4697 | 0.16652 | 501.6623 | 23.85 | 46.84
2021-01-21 04:25 | 0.50693 | 0.71189 | 0.17909 | 1.2703 | 30.7907 | 25.5187 | 1.4767 | 0.18821 | 501.7643 | 23.83 | 46.44
2021-01-21 04:30 | 0.79843 | 0.68881 | 0.2145 | 1.2703 | 41.3964 | 23.7855 | 1.4695 | 0.18822 | 501.1659 | 23.86 | 46.42
2021-01-21 04:35 | 1.1534 | 1.0938 | 0.2166 | 1.8932 | 54.2275 | 51.3782 | 1.4624 | 0.20271 | 501.4166 | 24 | 46.37
2021-01-21 04:40 | 2.0914 | 1.1821 | 0.21244 | 2.0245 | 63.4566 | 57.2306 | 1.4842 | 0.29684 | 501.1984 | 24.12 | 46.14
2021-01-21 04:45 | 2.9914 | 1.1604 | 0.28535 | 2.0641 | 84.4087 | 90.057 | 1.4843 | 0.30409 | 501.1487 | 24.14 | 46.19
2021-01-21 04:50 | 3.1691 | 1.3671 | 0.35411 | 2.4496 | 94.667 | 48.0383 | 1.4699 | 0.33307 | 500.4096 | 24.24 | 46.13
2021-01-21 04:55 | 2.9534 | 1.5735 | 0.42491 | 2.8348 | 75.5167 | 61.685 | 1.477 | 0.36202 | 499.2263 | 24.32 | 45.74
2021-01-21 05:00 | 2.5478 | 1.8222 | 0.44365 | 3.2368 | 67.3834 | 41.4948 | 1.4625 | 0.34753 | 500.7922 | 24.35 | 45.63
2021-01-21 05:05 | 3.2577 | 1.9268 | 0.41658 | 3.3701 | 63.5211 | 49.1416 | 1.4698 | 0.38374 | 499.6576 | 24.38 | 45.61
2021-01-21 05:10 | 2.9281 | 2.0845 | 0.50823 | 3.7055 | 63.2176 | 62.2137 | 1.4843 | 0.39099 | 500.1216 | 24.42 | 45.54
2021-01-21 05:15 | 2.9409 | 2.4216 | 0.4895 | 4.2034 | 81.8992 | 96.5733 | 1.4988 | 0.40548 | 498.3625 | 24.5 | 45.41
2021-01-21 05:20 | 3.0679 | 2.7071 | 0.61451 | 4.7661 | 99.8041 | 70.515 | 1.4917 | 0.50688 | 498.1654 | 24.6 | 45.33
2021-01-21 05:25 | 3.2331 | 2.861 | 0.73751 | 5.1209 | 99.2087 | 103.205 | 1.4991 | 0.4997 | 497.6484 | 24.87 | 45.02
2021-01-21 05:30 | 4.653 | 3.6058 | 0.79167 | 6.3188 | 107.0682 | 88.1416 | 1.5063 | 0.47073 | 496.1989 | 25.1 | 44.37
2021-01-21 05:35 | 6.4278 | 4.1398 | 0.96664 | 7.3123 | 131.4369 | 116.6592 | 1.5135 | 0.55762 | 497.5333 | 25.25 | 43.91
2021-01-21 05:40 | 6.0722 | 3.8961 | 0.88322 | 6.8554 | 149.4348 | 158.3897 | 1.5134 | 0.61549 | 497.9866 | 25.33 | 43.39
2021-01-21 05:45 | 6.4017 | 3.7874 | 0.78531 | 6.5907 | 177.3928 | 157.9823 | 1.4989 | 0.70237 | 497.2063 | 25.48 | 42.97
2021-01-21 05:50 | 5.5145 | 4.3379 | 0.93322 | 7.5824 | 185.7133 | 137.6319 | 1.5062 | 0.6517 | 497.0611 | 25.56 | 42.84
2021-01-21 05:55 | 6.0213 | 4.8989 | 1.1269 | 8.6341 | 161.9957 | 123.307 | 1.4989 | 0.59375 | 497.3336 | 25.73 | 42.29
2021-01-21 06:00 | 6.0722 | 5.0716 | 1.0082 | 8.7801 | 164.2311 | 150.9965 | 1.4989 | 0.60825 | 495.4492 | 25.89 | 41.97
2021-01-21 06:05 | 5.337 | 4.4071 | 0.94572 | 7.7011 | 171.3721 | 126.0596 | 1.5713 | 0.58653 | 495.3623 | 25.94 | 41.87
2021-01-21 06:10 | 4.2594 | 3.483 | 0.70616 | 6.0451 | 169.0085 | 137.6104 | 1.5423 | 0.54308 | 494.763 | 25.98 | 41.76
2021-01-21 06:15 | 7.1752 | 3.8296 | 0.79574 | 6.6659 | 177.5897 | 167.9247 | 1.5641 | 0.69515 | 496.3138 | 26.01 | 41.71
2021-01-21 06:20 | 12.3729 | 3.5741 | 0.83116 | 6.3097 | 207.8639 | 170.8468 | 1.651 | 0.91963 | 496.6956 | 26.1 | 41.51
2021-01-21 06:25 | 6.6938 | 3.2862 | 0.76869 | 5.8058 | 184.1902 | 120.7718 | 1.6945 | 0.60828 | 495.5244 | 26.15 | 41.5
2021-01-21 06:30 | 4.8933 | 3.3879 | 0.727 | 5.9201 | 155.9577 | 128.6666 | 1.5786 | 0.47791 | 495.9822 | 26.21 | 41.22
2021-01-21 06:35 | 5.4261 | 3.524 | 0.63746 | 6.0413 | 161.1994 | 117.8518 | 1.5207 | 0.51415 | 496.9248 | 26.27 | 41.23
2021-01-21 06:40 | 5.1852 | 3.5213 | 0.69163 | 6.0872 | 155.3793 | 120.277 | 1.499 | 0.57208 | 496.2365 | 26.36 | 41.04
2021-01-21 06:45 | 6.5164 | 3.5404 | 0.74371 | 6.1726 | 149.1935 | 127.276 | 1.499 | 0.60105 | 494.5152 | 26.43 | 40.89
2021-01-21 06:50 | 5.9465 | 3.1316 | 0.67503 | 5.4773 | 151.1248 | 100.0128 | 1.5136 | 0.64457 | 495.9375 | 26.51 | 40.97
2021-01-21 06:55 | 6.175 | 3.057 | 0.61048 | 5.2963 | 131.8795 | 103.6594 | 1.5644 | 0.6446 | 495.8631 | 26.54 | 41.04
2021-01-21 07:00 | 8.1024 | 3.0394 | 0.65007 | 5.3068 | 132.9156 | 104.4823 | 1.5355 | 0.65909 | 494.7405 | 26.57 | 41
2021-01-21 07:05 | 7.3805 | 2.9133 | 0.63555 | 5.1011 | 142.2529 | 111.8789 | 1.5067 | 0.63019 | 495.1391 | 26.62 | 41.18
2021-01-21 07:10 | 6.0491 | 2.9147 | 0.72517 | 5.1929 | 134.6163 | 107.1128 | 1.5284 | 0.57949 | 494.5797 | 26.63 | 41.21
2021-01-21 07:15 | 5.7323 | 3.1894 | 0.65643 | 5.5453 | 128.4946 | 110.902 | 1.5864 | 0.60125 | 494.4416 | 26.7 | 41.17
2021-01-21 07:20 | 6.4561 | 3.6481 | 0.59817 | 6.1901 | 163.8663 | 145.6319 | 1.5722 | 0.62308 | 493.6867 | 26.79 | 41.37
2021-01-21 07:25 | 6.3803 | 3.1941 | 0.47105 | 5.3671 | 167.506 | 133.8667 | 1.5288 | 0.58687 | 492.5341 | 26.83 | 41.39
2021-01-21 07:30 | 7.738 | 2.7741 | 0.46691 | 4.7191 | 148.4773 | 112.2079 | 1.5216 | 0.60864 | 493.5893 | 26.82 | 41.57
2021-01-21 07:35 | 7.4222 | 2.5148 | 0.55247 | 4.4073 | 146.7485 | 107.2549 | 1.5074 | 0.70297 | 493.8513 | 26.93 | 41.81
2021-01-21 07:40 | 7.6128 | 2.6564 | 0.53165 | 4.6034 | 151.8804 | 114.9837 | 1.5147 | 0.61603 | 493.7818 | 26.96 | 41.85
2021-01-21 07:45 | 6.4956 | 2.7799 | 0.53785 | 4.7989 | 135.981 | 84.2396 | 1.4856 | 0.59422 | 493.7833 | 26.99 | 41.49
2021-01-21 07:50 | 6.191 | 2.9743 | 0.55451 | 5.1136 | 119.6791 | 97.1377 | 1.4855 | 0.6232 | 493.177 | 27.04 | 41.32
2021-01-21 07:55 | 5.1636 | 2.8166 | 0.61916 | 4.9366 | 121.8558 | 101.851 | 1.4856 | 0.51452 | 493.0425 | 27.11 | 41.26
2021-01-21 08:00 | 5.5441 | 3.007 | 0.56912 | 5.1805 | 134.3479 | 100.0429 | 1.4638 | 0.50727 | 492.9349 | 27.18 | 41.05
2021-01-21 08:05 | 5.6709 | 2.8887 | 0.39609 | 4.8239 | 121.843 | 110.4249 | 1.4493 | 0.46378 | 492.3242 | 27.23 | 40.91
2021-01-21 08:10 | 6.0646 | 2.9174 | 0.5212 | 4.9931 | 126.0837 | 113.2642 | 1.4857 | 0.44207 | 491.7426 | 27.24 | 41.07
2021-01-21 08:15 | 5.545 | 2.8225 | 0.64844 | 4.9749 | 133.9935 | 82.9136 | 1.4713 | 0.43487 | 493.2254 | 27.28 | 41.24
2021-01-21 08:20 | 4.7831 | 2.9105 | 0.63585 | 5.0952 | 116.2756 | 95.3874 | 1.4494 | 0.41307 | 493.2868 | 27.28 | 40.9
2021-01-21 08:25 | 3.6287 | 2.2863 | 0.48577 | 3.9904 | 122.4507 | 94.5786 | 1.4132 | 0.36961 | 492.7384 | 27.28 | 40.99
2021-01-21 08:30 | 4.0349 | 2.1355 | 0.43159 | 3.705 | 117.9512 | 78.6477 | 1.3988 | 0.36238 | 493.257 | 27.27 | 41.18
2021-01-21 08:35 | 3.6032 | 1.9299 | 0.49409 | 3.4544 | 93.8039 | 57.7419 | 1.3914 | 0.3551 | 492.2396 | 27.27 | 40.92
2021-01-21 08:40 | 4.1739 | 2.0917 | 0.54201 | 3.7461 | 81.58 | 46.7273 | 1.3913 | 0.34784 | 492.761 | 27.29 | 40.75
2021-01-21 08:45 | 4.2617 | 2.1062 | 0.55439 | 3.7849 | 84.2095 | 56.8331 | 1.3838 | 0.36949 | 492.8254 | 27.32 | 40.05
2021-01-21 08:50 | 3.1326 | 2.3303 | 0.5335 | 4.1075 | 93.4649 | 66.6795 | 1.3692 | 0.26804 | 492.8554 | 27.33 | 39.77
2021-01-21 08:55 | 3.3992 | 2.8553 | 0.59816 | 4.9728 | 97.9985 | 66.0359 | 1.3693 | 0.28979 | 492.2477 | 27.35 | 39.96
2021-01-21 09:00 | 4.9594 | 2.3537 | 0.5294 | 4.1351 | 86.3527 | 35.3427 | 1.3693 | 0.34052 | 492.7313 | 27.37 | 40
2021-01-21 09:05 | 4.3514 | 1.9801 | 0.60037 | 3.6356 | 69.4199 | 44.1588 | 1.3623 | 0.31884 | 493.1214 | 27.4 | 40.44
2021-01-21 09:10 | 3.6288 | 2.0593 | 0.50455 | 3.6632 | 61.096 | 60.5884 | 1.348 | 0.34788 | 492.4557 | 27.44 | 40.72
2021-01-21 09:15 | 3.2728 | 2.4097 | 0.47526 | 4.1689 | 74.2754 | 49.1178 | 1.3405 | 0.37679 | 493.0458 | 27.47 | 40.06
2021-01-21 09:20 | 3.07 | 2.0181 | 0.41065 | 3.5041 | 77.8199 | 48.6019 | 1.3333 | 0.39854 | 493.0123 | 27.48 | 40.13
2021-01-21 09:25 | 3.1085 | 1.7573 | 0.43781 | 3.1314 | 73.1209 | 42.955 | 1.3262 | 0.35511 | 493.427 | 27.51 | 40.43
2021-01-21 09:30 | 3.8823 | 2.2455 | 0.5066 | 3.9464 | 69.7996 | 42.9739 | 1.3334 | 0.61599 | 492.8947 | 27.52 | 40.32
2021-01-21 09:35 | 4.1338 | 2.1912 | 0.51882 | 3.8776 | 68.4129 | 54.0588 | 1.3327 | 0.58668 | 491.5412 | 27.56 | 38.74
2021-01-21 09:40 | 3.2703 | 1.9622 | 0.42907 | 3.4367 | 70.9027 | 62.7092 | 1.3395 | 0.38374 | 493.7816 | 27.6 | 37.67
2021-01-21 09:45 | 2.9285 | 1.8415 | 0.4083 | 3.231 | 69.0062 | 36.7647 | 1.3252 | 0.26069 | 494.2262 | 27.61 | 38.03
2021-01-21 09:50 | 3.6391 | 1.4503 | 0.44379 | 2.6669 | 58.3166 | 51.0131 | 1.3109 | 0.26074 | 492.5455 | 27.61 | 38.5
2021-01-21 09:55 | 3.5391 | 1.9609 | 0.54195 | 3.5498 | 73.1779 | 52.6382 | 1.3042 | 0.24636 | 492.2868 | 27.64 | 39.57
2021-01-21 10:00 | 3.6434 | 2.0182 | 0.57364 | 3.6671 | 74.0045 | 44.6241 | 1.3197 | 0.27554 | 492.384 | 27.68 | 41.47
2021-01-21 10:05 | 3.1587 | 1.791 | 0.47943 | 3.2268 | 69.2829 | 32.6778 | 1.297 | 0.26085 | 492.7389 | 27.68 | 39.55
2021-01-21 10:10 | 3.5255 | 1.8639 | 0.48137 | 3.3363 | 67.9945 | 48.5458 | 1.3039 | 0.30424 | 493.4142 | 27.68 | 38.77
2021-01-21 10:15 | 4.1077 | 1.8688 | 0.49791 | 3.3645 | 62.0828 | 47.9136 | 1.3108 | 0.34761 | 492.4234 | 27.72 | 37.94
2021-01-21 10:20 | 3.7906 | 2.4313 | 0.48955 | 4.2163 | 71.6231 | 45.2842 | 1.3035 | 0.34759 | 493.4465 | 27.76 | 37.71
2021-01-21 10:25 | 2.7757 | 2.6237 | 0.49359 | 4.5152 | 63.1089 | 41.2378 | 1.2742 | 0.27511 | 493.0008 | 27.78 | 37.03
2021-01-21 10:30 | 2.8381 | 2.491 | 0.45595 | 4.2743 | 60.5938 | 61.6987 | 1.2955 | 0.27501 | 492.0905 | 27.79 | 36.1
2021-01-21 10:35 | 2.8001 | 2.4502 | 0.4726 | 4.2284 | 69.5634 | 55.6163 | 1.2954 | 0.28948 | 492.5301 | 27.85 | 35.94
2021-01-21 10:40 | 2.9528 | 1.8653 | 0.4269 | 3.2861 | 82.7303 | 46.7791 | 1.2958 | 0.30403 | 493.9525 | 27.88 | 36.53
2021-01-21 10:45 | 3.9282 | 1.9602 | 0.44559 | 3.4502 | 80.2667 | 54.9642 | 1.3028 | 0.34019 | 492.4207 | 27.88 | 36.2
2021-01-21 10:50 | 3.5612 | 1.864 | 0.45398 | 3.3112 | 80.39 | 59.2508 | 1.303 | 0.28956 | 492.2668 | 27.93 | 36.48
2021-01-21 10:55 | 4.1689 | 1.789 | 0.50596 | 3.2482 | 106.3075 | 80.2146 | 1.3101 | 0.31847 | 492.8691 | 27.96 | 35.95
2021-01-21 11:00 | 3.651 | 1.7015 | 0.41871 | 3.0288 | 92.4115 | 67.8989 | 1.3107 | 0.37654 | 490.3585 | 28.06 | 36.94
2021-01-21 11:05 | 2.8771 | 1.7161 | 0.41029 | 3.0386 | 96.1643 | 58.7693 | 1.2959 | 0.31131 | 491.504 | 28.07 | 36.38
2021-01-21 11:10 | 2.5226 | 1.8372 | 0.4395 | 3.2557 | 86.8675 | 50.1167 | 1.2961 | 0.31135 | 491.4233 | 28.08 | 36.7
2021-01-21 11:15 | 2.6363 | 2.3152 | 0.55607 | 4.1049 | 82.9813 | 51.9444 | 1.2814 | 0.29682 | 490.4035 | 28.1 | 36.27
2021-01-21 11:20 | 2.7628 | 2.7511 | 0.606 | 4.823 | 75.0968 | 47.5704 | 1.2885 | 0.2968 | 490.8434 | 28.18 | 35.89
2021-01-21 11:25 | 3.3455 | 2.3189 | 0.48101 | 4.0355 | 64.8309 | 32.5016 | 1.2957 | 0.2461 | 491.3021 | 28.25 | 35.52
2021-01-21 11:30 | 2.9274 | 1.9658 | 0.46229 | 3.4734 | 71.7781 | 59.6528 | 1.2885 | 0.28231 | 491.2666 | 28.26 | 35.6
2021-01-21 11:35 | 3.0801 | 1.6537 | 0.4124 | 2.9472 | 68.3454 | 45.2661 | 1.3032 | 0.23892 | 491.1802 | 28.25 | 36.16
2021-01-21 11:40 | 2.9157 | 2.2478 | 0.47078 | 3.9162 | 83.7399 | 44.4307 | 1.2889 | 0.39102 | 489.5222 | 28.25 | 36.52
2021-01-21 11:45 | 3.032 | 2.4915 | 0.51281 | 4.3318 | 67.5621 | 63.8273 | 1.2754 | 0.44203 | 489.1438 | 28.29 | 38.26
2021-01-21 11:50 | 3.6034 | 1.8675 | 0.44616 | 3.3087 | 78.31 | 69.1138 | 1.2755 | 0.4131 | 490.5686 | 28.35 | 38.46
2021-01-21 11:55 | 4.263 | 2.168 | 0.42947 | 3.7506 | 75.8821 | 63.6004 | 1.2827 | 0.39135 | 490.5653 | 28.36 | 38.37
2021-01-21 12:00 | 4.975 | 1.9224 | 0.41918 | 3.3659 | 86.7181 | 56.7663 | 1.2904 | 0.40596 | 488.287 | 28.37 | 39.12
2021-01-21 12:05 | 2.9959 | 2.0617 | 0.47142 | 3.6316 | 78.9491 | 51.0823 | 1.2834 | 0.3408 | 489.7256 | 28.39 | 39.67
2021-01-21 12:10 | 2.9592 | 1.9469 | 0.48834 | 3.4727 | 93.5666 | 71.4171 | 1.284 | 0.27567 | 488.9652 | 28.39 | 40.88
2021-01-21 12:15 | 2.8566 | 1.8006 | 0.50904 | 3.267 | 79.1118 | 43.6745 | 1.2764 | 0.23206 | 490.2053 | 28.38 | 40.03
2021-01-21 12:20 | 3.3276 | 2.094 | 0.56349 | 3.7733 | 80.3198 | 39.22 | 1.2841 | 0.26117 | 488.9029 | 28.42 | 40.88
2021-01-21 12:25 | 2.68 | 2.4522 | 0.60316 | 4.3641 | 76.37 | 58.2022 | 1.2769 | 0.26843 | 489.3646 | 28.45 | 40.9
2021-01-21 12:30 | 2.7809 | 2.0391 | 0.50077 | 3.6264 | 89.8205 | 47.8867 | 1.2765 | 0.26111 | 490.5459 | 28.45 | 40.25
2021-01-21 12:35 | 2.413 | 1.8992 | 0.44658 | 3.3556 | 76.3819 | 54.9649 | 1.2695 | 0.21762 | 489.9145 | 28.47 | 40.57
2021-01-21 12:40 | 3.1885 | 1.995 | 0.44878 | 3.5068 | 76.4314 | 55.3647 | 1.2698 | 0.2467 | 488.6884 | 28.5 | 41.13
2021-01-21 12:45 | 3.6209 | 1.8427 | 0.46764 | 3.2922 | 81.0467 | 51.4394 | 1.27 | 0.23948 | 488.585 | 28.52 | 41.45
2021-01-21 12:50 | 4.5987 | 2.2661 | 0.48429 | 3.9578 | 88.5697 | 57.5424 | 1.2699 | 0.26123 | 488.0229 | 28.57 | 41.09
2021-01-21 12:55 | 3.7982 | 2.1543 | 0.50723 | 3.8095 | 89.1656 | 45.9344 | 1.2698 | 0.2975 | 488.5868 | 28.56 | 41.01
2021-01-21 13:00 | 2.4905 | 1.7926 | 0.55331 | 3.3032 | 100.993 | 72.5097 | 1.2774 | 0.26855 | 487.3604 | 28.58 | 41.68
2021-01-21 13:05 | 1.6516 | 1.5663 | 0.45511 | 2.8559 | 103.0424 | 37.4644 | 1.2845 | 0.23223 | 489.0494 | 28.58 | 41.29
2021-01-21 13:10 | 1.8422 | 1.712 | 0.50729 | 3.1293 | 89.542 | 40.0754 | 1.2845 | 0.20319 | 489.639 | 28.55 | 41.29
2021-01-21 13:15 | 2.4015 | 1.7026 | 0.47395 | 3.0838 | 101.8533 | 55.2976 | 1.2701 | 0.21773 | 491.173 | 28.54 | 41.64
2021-01-21 13:20 | 2.9733 | 1.5882 | 0.47395 | 2.9085 | 92.2277 | 51.8012 | 1.2774 | 0.31209 | 488.5021 | 28.56 | 41.61
2021-01-21 13:25 | 4.3587 | 1.7614 | 0.44895 | 3.1489 | 93.8232 | 46.4389 | 1.2775 | 0.37019 | 487.3488 | 28.59 | 41.8
2021-01-21 13:30 | 5.5151 | 1.9685 | 0.43224 | 3.4496 | 104.3858 | 60.3359 | 1.2848 | 0.38471 | 486.79 | 28.61 | 41.75
2021-01-21 13:35 | 5.0828 | 1.5556 | 0.42804 | 2.8125 | 104.7054 | 60.6681 | 1.2847 | 0.37017 | 488.9076 | 28.62 | 41.59
2021-01-21 13:40 | 4.1556 | 1.7165 | 0.53668 | 3.1679 | 102.7445 | 59.7293 | 1.2921 | 0.32666 | 489.3647 | 28.63 | 41.84
2021-01-21 13:45 | 3.3677 | 1.8228 | 0.48238 | 3.2764 | 103.8213 | 59.8609 | 1.2848 | 0.25406 | 489.3365 | 28.65 | 41.77
2021-01-21 13:50 | 3.2154 | 1.9891 | 0.56803 | 3.6191 | 110.9859 | 58.2788 | 1.2777 | 0.23956 | 487.1815 | 28.66 | 41.91
2021-01-21 13:55 | 2.7576 | 1.85 | 0.55546 | 3.3933 | 113.122 | 62.2288 | 1.2776 | 0.27584 | 489.2631 | 28.7 | 41.61
2021-01-21 14:00 | 2.7321 | 1.8976 | 0.49906 | 3.4057 | 108.868 | 52.6092 | 1.2775 | 0.24679 | 488.756 | 28.7 | 41.51
2021-01-21 14:05 | 3.1009 | 1.925 | 0.59307 | 3.5417 | 112.8113 | 56.0905 | 1.2849 | 0.27585 | 488.6358 | 28.75 | 41.59
2021-01-21 14:10 | 3.1773 | 1.8774 | 0.58056 | 3.4583 | 116.5267 | 77.1185 | 1.314 | 0.29038 | 487.4673 | 28.81 | 41.54
2021-01-21 14:15 | 4.2195 | 2.0001 | 0.55134 | 3.6171 | 111.4048 | 71.6196 | 1.3648 | 0.39928 | 487.3598 | 28.87 | 41.45
2021-01-21 14:20 | 5.668 | 2.1961 | 0.53668 | 3.903 | 149.2389 | 141.7053 | 1.372 | 0.45732 | 487.8839 | 28.89 | 41.25
2021-01-21 14:25 | 4.8037 | 1.7329 | 0.426 | 3.0822 | 191.0311 | 135.5009 | 1.2994 | 0.41376 | 486.3059 | 28.92 | 41.09
2021-01-21 14:30 | 5.0325 | 1.5776 | 0.44479 | 2.863 | 160.0847 | 88.5824 | 1.2848 | 0.43554 | 486.8129 | 28.93 | 41.08
2021-01-21 14:35 | 3.164 | 1.6264 | 0.48233 | 2.9754 | 117.7468 | 37.0329 | 1.3428 | 0.37742 | 486.8384 | 28.95 | 40.74
2021-01-21 14:40 | 3.7101 | 1.7189 | 0.45723 | 3.09 | 92.8545 | 41.9395 | 1.3209 | 0.37014 | 489.0278 | 28.92 | 40.62
2021-01-21 14:45 | 3.4816 | 1.7408 | 0.47396 | 3.1424 | 87.6349 | 50.7553 | 1.2992 | 0.35564 | 487.4544 | 28.9 | 40.81
2021-01-21 14:50 | 4.0535 | 1.7327 | 0.43639 | 3.0923 | 95.4132 | 67.4988 | 1.2847 | 0.38468 | 488.4643 | 28.92 | 40.81
2021-01-21 14:55 | 4.1935 | 1.978 | 0.4218 | 3.4538 | 89.7469 | 75.5244 | 1.3138 | 0.35567 | 488.8927 | 28.96 | 40.88
2021-01-21 15:00 | 4.2952 | 2.0216 | 0.51159 | 3.6103 | 108.3598 | 81.1148 | 1.3211 | 0.3847 | 487.7986 | 28.99 | 40.78
2021-01-21 15:05 | 4.5245 | 2.4796 | 0.63278 | 4.4336 | 134.6055 | 91.0181 | 1.2994 | 0.3412 | 487.6716 | 29.03 | 41
2021-01-21 15:10 | 4.6006 | 2.2602 | 0.52416 | 3.9866 | 131.0725 | 78.2856 | 1.2776 | 0.41378 | 487.6092 | 29.08 | 40.79
2021-01-21 15:15 | 3.5326 | 1.9153 | 0.53037 | 3.4662 | 125.2636 |  | 1.2775 | 0.33389 | 486.6436 | 29.06 | 40.57
2021-01-21 15:20 | 2.9353 | 1.715 | 0.47815 | 3.1069 | 111.1293 |  | 1.2702 | 0.29758 | 486.7247 | 29.02 | 40.58
2021-01-21 15:25 | 3.6093 | 1.6757 | 0.46778 | 3.0385 | 102.5335 | 35.9503 | 1.2776 | 0.34118 | 486.6404 | 29.03 | 40.9
2021-01-21 15:30 | 3.762 | 1.6595 | 0.40306 | 2.9467 | 102.1427 | 47.9296 | 1.2632 | 0.31216 | 486.5809 | 29.05 | 40.99
2021-01-21 15:35 | [9 empty] | 29.05 | 40.96
2021-01-21 15:40 | 4.7158 | 1.7387 | 0.47413 | 3.1414 | 88.1329 | 73.3373 | 1.2706 | 0.53002 | 487.0822 | 29.05 | 41.26
2021-01-21 15:45 | 5.7206 | 2.205 | 0.56818 | 3.948 | 85.4476 | 57.6838 | 1.307 | 0.5446 | 486.9479 | 29.1 | 41.41
2021-01-21 15:50 | 4.742 | 2.0279 | 0.5139 | 3.6224 | 100.007 | 82.2391 | 1.3434 | 0.41392 | 486.3446 | 29.13 | 41.49
2021-01-21 15:55 | 3.8906 | 1.9368 | 0.48052 | 3.4493 | 116.0962 | 72.8983 | 1.3363 | 0.37038 | 486.2241 | 29.18 | 41.57
2021-01-21 16:00 | 3.5731 | 2.3214 | 0.54953 | 4.1079 | 127.0464 | 90.2315 | 1.3001 | 0.40674 | 485.0179 | 29.24 | 41.73
2021-01-21 16:05 | 3.2933 | 2.1346 | 0.52236 | 3.7923 | 131.123 | 78.8569 | 1.2783 | 0.45031 | 486.028 | 29.27 | 41.61
2021-01-21 16:10 | 3.5604 | 1.8307 | 0.46804 | 3.2721 | 120.2399 | 80.4448 | 1.2711 | 0.40674 | 486.0706 | 29.24 | 41.71
2021-01-21 16:15 | 3.0772 | 1.6439 | 0.4534 | 2.9732 | 97.4314 | 51.5233 | 1.2565 | 0.30505 | 485.6347 | 29.19 | 41.79
2021-01-21 16:20 | 4.2599 | 1.6781 | 0.45761 | 3.0298 | 83.1949 | 53.6423 | 1.2566 | 0.3777 | 486.7192 | 29.15 | 42.03
2021-01-21 16:25 | 5.3538 | 1.8281 | 0.4033 | 3.2055 | 76.9629 | 53.9809 | 1.2639 | 0.37772 | 486.6613 | 29.17 | 42.11
2021-01-21 16:30 | 4.8709 | 2.0818 | 0.42841 | 3.6195 | 80.6408 | 57.6878 | 1.264 | 0.39228 | 486.0729 | 29.19 | 42.22
2021-01-21 16:35 | 4.6292 | 1.8269 | 0.41377 | 3.2141 | 77.9136 | 59.6205 | 1.264 | 0.37775 | 486.5523 | 29.22 | 42.13
2021-01-21 16:40 | 7.7073 | 1.5638 | 0.39916 | 2.7962 | 88.1528 | 55.8586 | 1.2858 | 0.42135 | 486.5621 | 29.2 | 42.29
2021-01-21 16:45 | 7.7968 | 1.5789 | 0.36784 | 2.7881 | 79.6728 | 54.6822 | 1.2932 | 0.42865 | 486.5279 | 29.2 | 42.46
2021-01-21 16:50 | 5.4428 | 1.6345 | 0.39494 | 2.8983 | 91.3071 | 59.5455 | 1.2784 | 0.37772 | 486.5994 | 29.21 | 42
2021-01-21 16:55 | 4.6286 | 1.5158 | 0.39282 | 2.7142 | 91.4724 | 78.5633 | 1.2711 | 0.32685 | 487.2129 | 29.18 | 41.87
2021-01-21 17:00 | 4.6919 | 1.284 | 0.33847 | 2.3066 | 105.5249 | 84.5908 | 1.2928 | 0.35588 | 487.3217 | 29.13 | 41.85
2021-01-21 17:05 | 4.6285 | 1.3904 | 0.32595 | 2.4572 | 94.9711 | 68.1359 | 1.2856 | 0.39221 | 487.8895 | 29.11 | 41.98
2021-01-21 17:10 | 4.0568 | 1.531 | 0.34271 | 2.6915 | 88.8577 | 60.5441 | 1.2712 | 0.30509 | 487.3564 | 29.08 | 42.34
2021-01-21 17:15 | 3.51 | 1.5146 | 0.35734 | 2.679 | 93.823 | 47.5423 | 1.2494 | 0.29056 | 486.2574 | 29.11 | 42.28
2021-01-21 17:20 | 3.6752 | 1.6809 | 0.36987 | 2.9464 | 59.2104 | 45.8016 | 1.2712 | 0.39952 | 487.3644 | 29.08 | 42.3
2021-01-21 17:25 | 4.9601 | 1.5733 | 0.34064 | 2.7523 | 54.1893 | 27.9799 | 1.2786 | 0.31964 | 487.4508 | 29 | 42.71
2021-01-21 17:30 | 4.2985 | 1.1806 | 0.26331 | 2.073 | 54.1356 | 44.7044 | 1.2712 | 0.27604 | 487.5732 | 28.94 | 42.73
2021-01-21 17:35 | 4.0566 | 0.92018 | 0.25284 | 1.6612 | 53.4912 | 51.2531 | 1.2494 | 0.23244 | 486.6205 | 28.9 | 42.67
2021-01-21 17:40 | 2.9758 | 0.89023 | 0.26121 | 1.6258 | 49.8109 | 40.1967 | 1.2494 | 0.23245 | 485.6443 | 28.84 | 42.94
2021-01-21 17:45 | 4.235 | 0.97206 | 0.25495 | 1.745 | 57.2197 | 38.4585 | 1.2713 | 0.25425 | 487.2796 | 28.79 | 43.16
2021-01-21 17:50 | 3.2305 | 1.0062 | 0.25497 | 1.7973 | 59.2483 | 43.6197 | 1.2786 | 0.21795 | 487.8202 | 28.76 | 43.4
2021-01-21 17:55 | 4.0322 | 1.069 | 0.2759 | 1.9167 | 58.2676 | 56.9244 | 1.2788 | 0.2325 | 486.8153 | 28.7 | 43.82
2021-01-21 18:00 | 2.6205 | 0.8441 | 0.25292 | 1.5468 | 59.6343 | 41.9476 | 1.257 | 0.18165 | 487.9194 | 28.65 | 44.08
2021-01-21 18:05 | 2.7608 | 0.84013 | 0.22996 | 1.5178 | 64.0096 | 35.3076 | 1.2499 | 0.15988 | 486.959 | 28.55 | 44.71
2021-01-21 18:10 | 2.7229 | 0.77884 | 0.27598 | 1.4698 | 50.9969 | 38.7719 | 1.2501 | 0.17443 | 488.0738 | 28.48 | 45.14
2021-01-21 18:15 | 2.6593 | 0.6629 | 0.23208 | 1.2482 | 33.7843 | 27.1068 | 1.2501 | 0.15989 | 488.2014 | 28.4 | 45.36
2021-01-21 18:20 | 2.4178 | 1.0163 | 0.26974 | 1.8275 | 27.3844 | 25.8574 | 1.2575 | 0.23259 | 488.7752 | 28.34 | 45.77
2021-01-21 18:25 | 2.367 | 1.135 | 0.29485 | 2.0347 | 24.9632 | 36.5896 | 1.2503 | 0.20353 | 487.7411 | 28.31 | 46.02
2021-01-21 18:30 | 2.3923 | 1.0845 | 0.24046 | 1.9028 | 18.4866 | 21.7237 | 1.2502 | 0.18171 | 488.4406 | 28.23 | 46
2021-01-21 18:35 | 2.9394 | 0.78708 | 0.19237 | 1.3988 | 8.2049 | 21.8763 | 1.2502 | 0.16717 | 488.5887 | 28.14 | 46.23
2021-01-21 18:40 | 2.6469 | 0.79668 | 0.23211 | 1.4554 | 13.4585 | 29.8592 | 1.2575 | 0.14538 | 488.6385 | 28.09 | 46.53
2021-01-21 18:45 | 2.3159 | 0.76253 | 0.23 | 1.3988 | 17.5196 | 23.9838 | 1.2429 | 0.1381 | 488.2197 | 28.04 | 46.53
2021-01-21 18:50 | 1.705 | 0.60288 | 0.19862 | 1.1227 | 32.064 | 50.4779 | 1.2428 | 0.15989 | 490.0455 | 27.89 | 46.77
2021-01-21 18:55 | 2.3411 | 0.54285 | 0.18398 | 1.0161 | 29.6199 | 41.8954 | 1.2428 | 0.29797 | 489.2061 | 27.77 | 47
2021-01-21 19:00 | 2.0614 | 0.5361 | 0.17564 | 0.99739 | 32.9932 | 26.4373 | 1.2502 | 0.2544 | 489.7365 | 27.73 | 47.44
2021-01-21 19:05 | 1.7051 | 0.68613 | 0.21745 | 1.2692 | 25.3271 | 44.3223 | 1.2429 | 0.32707 | 489.7002 | 27.76 | 47.29
2021-01-21 19:10 | 1.8957 | 0.69696 | 0.2237 | 1.292 | 20.8455 | 20.5605 | 1.25 | 0.22529 | 490.9593 | 27.67 | 47.22
2021-01-21 19:15 | 1.8067 | 0.63015 | 0.19862 | 1.1645 | 18.6067 | 24.3577 | 1.2573 | 0.14535 | 491.1249 | 27.56 | 47.6
2021-01-21 19:20 | 2.3413 | 0.61929 | 0.17145 | 1.1186 | 26.7929 | 47.9056 | 1.2574 | 0.15263 | 491.2263 | 27.47 | 48.1
2021-01-21 19:25 | 1.6288 | 0.61521 | 0.17564 | 1.1187 | 37.5843 | 36.0166 | 1.2502 | 0.1381 | 490.7363 | 27.44 | 48.25
2021-01-21 19:30 | 1.2726 | 0.65074 | 0.18611 | 1.1836 | 23.925 | 21.4409 | 1.2503 | 0.12358 | 491.2866 | 27.42 | 48.5
2021-01-21 19:35 | 0.78898 | 0.6016 | 0.18819 | 1.1124 | 29.8388 | 25.9498 | 1.2357 | 0.087226 | 490.8284 | 27.37 | 48.57
2021-01-21 19:40 | 0.97993 | 0.56344 | 0.15266 | 1.0184 | 15.6381 | 32.5387 | 1.2285 | 0.094501 | 490.9777 | 27.28 | 48.96
2021-01-21 19:45 | 1.031 | 0.71223 | 0.16522 | 1.257 | 29.5285 | 30.0987 | 1.2505 | 0.094512 | 491.9243 | 27.29 | 49.29
2021-01-21 19:50 | 0.7255 | 0.58944 | 0.14013 | 1.0457 | 40.5566 | 48.5193 | 1.2432 | 0.079973 | 490.9594 | 27.23 | 49.51
2021-01-21 19:55 | 0.92919 | 0.55945 | 0.13804 | 0.99559 | 46.648 | 53.1651 | 1.236 | 0.087247 | 491.0493 | 27.16 | 49.85
2021-01-21 20:00 | 1.6676 | 0.64272 | 0.14433 | 1.1295 | 54.319 | 58.0767 | 1.2361 | 0.087253 | 490.5093 | 27.15 | 50.04
2021-01-21 20:05 | 2.113 | 0.56083 | 0.15269 | 1.0124 | 33.9815 | 32.9021 | 1.2288 | 0.10179 | 491.6599 | 27.1 | 50.11
2021-01-21 20:10 | 0.92924 | 0.48579 | 0.13387 | 0.87851 | 48.229 | 157.8033 | 1.2361 | 0.07271 | 435.2908 | 27.04 | 50.35
2021-01-21 20:15 | 2.4191 | 0.73432 | 0.17365 | 1.3013 | 277.0951 | 287.9532 | 1.2291 | 0.19636 | 327.0526 | 27.04 | 50.98
2021-01-21 20:20 | 3.4252 | 0.68931 | 0.16738 | 1.224 | 177.2021 | 59.1726 | 1.2437 | 0.20365 | 326.3661 | 27.17 | 50.74
2021-01-21 20:25 | 3.578 | 0.65656 | 0.16111 | 1.1675 | 85.4957 | 22.8484 | 1.2437 | 0.2182 | 325.7463 | 27.25 | 50.55
2021-01-21 20:30 | 2.3939 | 0.64703 | 0.15902 | 1.1508 | 46.4215 | 20.9849 | 1.2438 | 0.16729 | 325.1773 | 27.28 | 50.54
2021-01-21 20:35 | 2.0628 | 0.58424 | 0.14437 | 1.0399 | 21.2906 | 25.6506 | 1.2438 | 0.17456 | 326.1977 | 27.31 | 50.46
2021-01-21 20:40 | 1.9864 | 0.4996 | 0.14228 | 0.90809 | 18.7029 | 20.2513 | 1.2437 | 0.16729 | 325.7067 | 27.28 | 50.52
2021-01-21 20:45 | 2.2412 | 0.50919 | 0.16949 | 0.94999 | 27.5468 | 23.8284 | 1.2365 | 0.1382 | 325.6862 | 27.28 | 50.69
2021-01-21 20:50 | 1.8591 | 0.37538 | 0.13182 | 0.70721 | 16.7062 | 20.3632 | 1.2365 | 0.10183 | 326.2903 | 27.23 | 50.65
2021-01-21 20:55 | 1.1332 | 0.29893 | 0.11298 | 0.57328 | 14.2405 | 25.3131 | 1.2364 | 0.080003 | 326.4106 | 27.13 | 50.85
2021-01-21 21:00 | 1.146 | 0.30577 | 0.12136 | 0.59005 | 22.411 | 10.9814 | 1.2365 | 0.094554 | 326.4821 | 27.05 | 51.22
2021-01-21 21:05 | 1.7065 | 0.42048 | 0.1423 | 0.78683 | 26.5094 | 30.3605 | 1.2366 | 0.072743 | 325.936 | 27.03 | 51.62
2021-01-21 21:10 | 0.98049 | 0.33853 | 0.12345 | 0.64445 | 22.1259 | 28.6556 | 1.2292 | 0.058187 | 325.9643 | 27.04 | 51.26
2021-01-21 21:15 | 2.6995 | 0.30031 | 0.12136 | 0.57958 | 4.3599 | 25.3752 | 1.2365 | 0.080007 | 325.5491 | 26.94 | 51.53
2021-01-21 21:20 | 1.8083 | 0.44366 | 0.1109 | 0.79096 | 10.6764 | 15.7701 | 1.222 | 0.087286 | 327.1325 | 26.92 | 51.77
2021-01-21 21:25 | 2.5086 | 0.37676 | 0.087883 | 0.66749 | 12.5404 | 14.9344 | 1.2292 | 0.050916 | 326.1389 | 26.87 | 51.86
2021-01-21 21:30 | 0.92966 | 0.41366 | 0.10882 | 0.74288 | 13.7437 | 31.0837 | 1.2366 | 0.058194 | 326.1435 | 26.84 | 52.19
2021-01-21 21:35 | 2.1394 | 0.31808 | 0.075331 | 0.56289 | 23.2889 | 23.5334 | 1.2366 | 0.043644 | 326.7171 | 26.81 | 52.17
2021-01-21 21:40 | 0.98066 | 0.33995 | 0.077432 | 0.59853 | 27.7539 | 3.2196 | 1.2367 | 0.050923 | 326.2223 | 26.75 | 52.63
2021-01-21 21:45 | 0.90434 | 0.28401 | 0.094183 | 0.52952 | 23.365 | 33.4019 | 1.2368 | 0.043653 | 326.1774 | 26.76 | 52.89
2021-01-21 21:50 | 0.36939 | 0.32089 | 0.10256 | 0.59442 | 19.0758 | 17.4454 | 1.2296 | 0.065481 | 326.7155 | 26.74 | 53.05
2021-01-21 21:55 | 0.59865 | 0.30176 | 0.079533 | 0.54208 | 19.1669 | 12.9919 | 1.2223 | 0.065479 | 326.2203 | 26.72 | 53.02
2021-01-21 22:00 | 1.6304 | 0.24578 | 0.079533 | 0.45627 | 20.0637 | 8.1009 | 1.2296 | 0.050928 | 326.2841 | 26.66 | 53.22
2021-01-21 22:05 | 1.2228 | 0.20755 | 0.075347 | 0.39348 | 9.2829 | 21.3273 | 1.2368 | 0.036378 | 326.8983 | 26.58 | 53.48
2021-01-21 22:10 | 1.0701 | 0.38511 | 0.092106 | 0.68242 | 18.844 | 22.2785 | 1.237 | 0.050937 | 325.8332 | 26.54 | 54.06
2021-01-21 22:15 | 0.86628 | 0.50803 | 0.11513 | 0.89595 | 25.1526 | 9.366 | 1.237 | 0.065491 | 326.3158 | 26.58 | 53.95
2021-01-21 22:20 | 0.66238 | 0.29905 | 0.085818 | 0.54421 | 14.8169 | -1.8445 | 1.2369 | 0.058208 | 327.4599 | 26.53 | 53.82
2021-01-21 22:25 | 0.71337 | 0.35369 | 0.090009 | 0.63215 | 5.6152 | 10.7617 | 1.2297 | 0.050935 | 327.0134 | 26.44 | 54.25
2021-01-21 22:30 | 0.48409 | 0.41925 | 0.094198 | 0.73684 | 6.8995 | 9.3251 | 1.237 | 0.04366 | 325.9676 | 26.42 | 54.41
2021-01-21 22:35 | 0.42042 | 0.28134 | 0.07955 | 0.51079 | 13.6062 | 17.367 | 1.2298 | 0.050939 | 326.9724 | 26.45 | 54.48
2021-01-21 22:40 | 0.81531 | 0.16388 | 0.071172 | 0.32027 | 5.9314 | -7.3174 | 1.237 | 0.029106 | 326.011 | 26.38 | 54.54
2021-01-21 22:45 | 1.0191 | 0.18846 | 0.073266 | 0.36214 | 2.0994 | 1.0599 | 1.237 | 0.02183 | 326.0956 | 26.3 | 54.82
2021-01-21 22:50 | 0.63704 | 0.18848 | 0.085836 | 0.37475 | 8.47 | 7.6852 | 1.2372 | 0.043665 | 327.6658 | 26.28 | 55.21
2021-01-21 22:55 | 1.1976 | 0.14204 | 0.075367 | 0.29309 | 12.9444 | 4.2808 | 1.2299 | 0.050942 | 327.1419 | 26.28 | 55.17
2021-01-21 23:00 | 0.50959 | 0.18983 | 0.085828 | 0.37681 | 8.4693 | 8.6629 | 1.2298 | 0.043661 | 326.1624 | 26.23 | 55.13
2021-01-21 23:05 | 0.39491 | 0.27995 | 0.087918 | 0.51704 | 7.7046 | 15.4295 | 1.237 | 0.050936 | 326.717 | 26.22 | 55.03
2021-01-21 23:10 | 0.44581 | 0.20345 | 0.083721 | 0.39767 | 17.486 | 12.1159 | 1.2369 | 0.043654 | 326.2604 | 26.19 | 54.78
2021-01-21 23:15 | 1.3883 | 0.27854 | 0.077439 | 0.5023 | 23.8333 | 26.7577 | 1.2441 | 0.050927 | 326.8475 | 26.15 | 54.78
2021-01-21 23:20 | 0.26748 | 0.2567 | 0.069068 | 0.46255 | 21.6838 | 21.4698 | 1.2368 | 0.043653 | 326.8519 | 26.14 | 54.87
2021-01-21 23:25 | 0.80251 | 0.18981 | 0.071167 | 0.36211 | 24.8549 | 23.0104 | 1.2442 | 0.043657 | 326.3721 | 26.07 | 55.34
2021-01-21 23:30 | 1.0829 | 0.24446 | 0.085831 | 0.46055 | 30.6268 | 19.9966 | 1.2371 | 0.043662 | 326.8684 | 26.06 | 55.76
2021-01-21 23:35 | 0.30576 | 0.18301 | 0.069084 | 0.34751 | 20.1396 | 14.0855 | 1.2371 | 0.029109 | 326.9067 | 26.02 | 55.94
2021-01-21 23:40 | 0.076445 | 0.15297 | 0.054433 | 0.28891 | 8.093 | -1.3352 | 1.2372 | 0.043665 | 327.506 | 25.94 | 56.36
2021-01-21 23:45 | 0.49692 | 0.20079 | 0.066998 | 0.37477 | 13.8832 | 22.313 | 1.2445 | 0.043668 | 326.9477 | 25.95 | 56.49
2021-01-21 23:50 |  | 0.24177 | 0.058626 | 0.42923 | 26.4832 | 15.209 | 1.2446 | 0.036391 | 326.3714 | 25.98 | 56.52
2021-01-21 23:55 | -0.3823 | 0.29371 | 0.10051 | 0.55071 | 22.2038 | 23.9063 | 1.2447 | 0.050952 | 326.2778 | 26.04 | 56.57
2021-01-22 | 0.85374 | 0.18031 | 0.08794 | 0.36432 | 16.6771 | 10.8972 | 1.2373 | 0.036392 | 327.0635 | 26.01 | 56.41
2021-01-22 00:05 | -0.025484 | 0.099713 | 0.067 | 0.22194 | 18.5829 | 15.7796 | 1.2446 | -0.021835 | 326.6537 | 25.91 | 56.66
2021-01-22 00:10 | 0.025484 | 0.095615 | 0.052344 | 0.19891 | 16.3096 | 2.5892 | 1.2373 | 0.036391 | 326.2792 | 25.77 | 57.12
2021-01-22 00:15 | 0.82819 | 0.095611 | 0.052341 | 0.1989 | 1.529 | 1.6411 | 1.2518 | 0.050945 | 326.9431 | 25.66 | 57.36
2021-01-22 00:20 | 1.0702 | 0.079214 | 0.04815 | 0.17167 | -1.0396 | -6.9001 | 1.259 | 0.036386 | 327.5876 | 25.58 | 57.38
2021-01-22 00:25 | 0.24206 | 0.076482 | 0.046056 | 0.16538 | 7.7053 | 6.3395 | 1.259 | 0.014554 | 327.1463 | 25.5 | 57.65
2021-01-22 00:30 | 0.24207 | 0.066923 | 0.039777 | 0.14236 | 8.48 | 2.2423 | 1.2517 | 0 | 327.692 | 25.48 | 57.77
2021-01-22 00:35 | 0.38221 | 0.058727 | 0.039776 | 0.1277 | -4.984 | 1.2231 | 1.2444 | 0.065495 | 327.2459 | 25.41 | 57.95
2021-01-22 00:40 | 0.25479 | 0.12018 | 0.054428 | 0.24074 | -3.5569 | -11.3129 | 1.2589 | 0.043662 | 328.3065 | 25.42 | 57.8
2021-01-22 00:45 | 0.48406 | 0.047794 | 0.043957 | 0.11931 | 4.9527 | 1.6407 | 1.2661 | 0.029105 | 326.7961 | 25.38 | 57.62
2021-01-22 00:50 | 1.2738 | 0.060085 | 0.048143 | 0.14024 | 5.6864 | 10.6595 | 1.2661 | 0.029105 | 326.8385 | 25.34 | 57.77
2021-01-22 00:55 | 2.3058 | 0.40014 | 0.085826 | 0.70126 | -1.7529 | -1.6306 | 1.2589 | 0.029107 | 327.8752 | 25.34 | 57.98
2021-01-22 01:00 | 0.10191 | 0.26902 | 0.069076 | 0.48144 | -2.1197 | -12.2087 | 1.2661 | 0.014553 | 327.9144 | 25.32 | 57.89
2021-01-22 01:05 |  |  |  |  | 3.3121 | 3.1592 |  |  | 327.9778 | 25.26 | 58.12
2021-01-22 01:10 |  |  |  |  | 0.50959 | 8.7956 |  |  | 327.9706 | 25.24 | 58.46
2021-01-22 01:15 |  |  |  |  | -0.46882 | 11.1905 |  |  | 327.4566 | 25.23 | 58.45
2021-01-22 01:20 |  |  |  |  | 10.0691 | -4.4638 |  |  | 326.4408 | 25.2 | 58.45
2021-01-22 01:25
2021-01-22 01:30 | 0.24203 | 0.091494 | 0.041864 | 0.18211 | -1.1006 | 4.9528 | 1.3679 | -0.043658 | 328.0468 | 25.2 | 58.3
2021-01-22 01:35 | 0.49681 | 0.073742 | 0.043958 | 0.15699 | -5.1363 | 5.0649 | 1.3461 | -0.036382 | 327.5563 | 25.16 | 58.48
2021-01-22 01:40 | 0.076436 | 0.12428 | 0.064893 | 0.25539 | 5.5238 | -7.0016 | 1.3171 | 0.0072767 | 326.9894 | 25.18 | 58.55
2021-01-22 01:45 | -0.22932 | 0.1516 | 0.069085 | 0.30146 | 5.3407 | -3.3634 | 1.3026 | 0.036386 | 326.5728 | 25.24 | 58.5
2021-01-22 01:50 | 0.59879 | 0.066921 | 0.052337 | 0.15492 | -4.2909 | -1.6817 | 1.3026 | 0.058217 | 326.5979 | 25.22 | 58.54
2021-01-22 01:55 | 0.76433 | 0.066915 | 0.054424 | 0.15699 | -6.9605 | 0.17325 | 1.2952 | 0.050935 | 327.7671 | 25.15 | 58.47
2021-01-22 02:00 | 1.1592 | 0.099687 | 0.054423 | 0.20723 | 4.3923 | -5.5846 | 1.2952 | 0.043658 | 327.267 | 25.13 | 58.47
2021-01-22 02:05 | 0.61142 | 0.076469 | 0.056514 | 0.17582 | 3.0367 | -8.6516 | 1.3024 | 0.043656 | 326.8065 | 25.08 | 58.51
2021-01-22 02:10 | 0.2675 | 0.096952 | 0.062794 | 0.20931 | -3.3527 | 7.276 | 1.3097 | 0.058208 | 328.4373 | 25.04 | 58.67
2021-01-22 02:15 | 0.1019 | 0.1147 | 0.058607 | 0.23443 | 5.5232 | 10.0376 | 1.3097 | 0.050932 | 327.3685 | 25.05 | 58.62
2021-01-22 02:20 | 0.22928 | 0.10104 | 0.066977 | 0.22186 | 12.3707 | -2.2214 | 1.3169 | 0.05093 | 326.8286 | 25.07 | 58.44
2021-01-22 02:25 | 0.20379 | 0.095579 | 0.060696 | 0.2072 | 11.1067 | 4.9522 | 1.3387 | 0.050928 | 326.8413 | 25.07 | 58.32
2021-01-22 02:30 | 0.43306 | 0.099675 | 0.064882 | 0.21767 | 2.6085 | 11.8913 | 1.3387 | 0.050928 | 326.8195 | 25.09 | 58.25
2021-01-22 02:35 | 0.6496 | 0.15566 | 0.07744 | 0.31395 | 1.9666 | -1.1413 | 1.3387 | 0.050928 | 327.3241 | 25.11 | 58.21
2021-01-22 02:40 | 0.72597 | 0.09967 | 0.04395 | 0.19673 | 6.0421 | -3.0058 | 1.3241 | 0.04365 | 327.3892 | 25.07 | 58.15
2021-01-22 02:45 | 1.5284 | 0.1024 | 0.066972 | 0.22394 | 6.7861 | 3.3421 | 1.3241 | 0.043651 | 326.9083 | 25.02 | 58.38
2021-01-22 02:50 | 0.8916 | 0.1775 | 0.12139 | 0.39348 | 1.6304 | 9.7108 | 1.3314 | 0.058204 | 326.8945 | 25.02 | 58.51
2021-01-22 02:55 | 1.8087 | 0.15975 | 0.094183 | 0.33906 | 5.4922 | 14.1636 | 1.3387 | 0.065478 | 327.4159 | 25.03 | 58.45
2021-01-22 03:00 | 0.66231 | 0.12971 | 0.073251 | 0.27208 | 13.7148 | 3.016 | 1.3532 | 0.087302 | 327.9773 | 25.01 | 58.43
2021-01-22 03:05 | 0.84065 | 0.13108 | 0.07116 | 0.27208 | 11.7283 | 0.58081 | 1.346 | 0.065479 | 326.3772 | 25.01 | 58.53
2021-01-22 03:10 | 0.52225 | 0.13518 | 0.066978 | 0.2721 | 4.8301 | 8.4069 | 1.346 | 0.058206 | 328.4585 | 25.03 | 58.61
2021-01-22 03:15 | 0.31843 | 0.15703 | 0.058604 | 0.2993 | 5.5127 | 7.5507 | 1.346 | 0.072756 | 326.91 | 25 | 58.64
2021-01-22 03:20 | 0.43308 | 0.21028 | 0.077443 | 0.39977 | 10.4041 | 1.2432 | 1.3533 | 0.058206 | 327.399 | 25.03 | 58.61
2021-01-22 03:25 | 0.95525 | 0.18159 | 0.075344 | 0.3537 | 7.9375 | 3.5866 | 1.3386 | 0.050926 | 327.9554 | 25.03 | 58.36
2021-01-22 03:30 | 0.94253 | 0.19115 | 0.071159 | 0.36417 | -3.3727 | -10.1487 | 1.3314 | 0.043652 | 327.4421 | 25.01 | 58.48
2021-01-22 03:35 | 1.3756 | 0.31405 | 0.083718 | 0.56719 | -4.6363 | 2.792 | 1.3314 | 0.058203 | 328.4075 | 25.09 | 58.26
2021-01-22 03:40 | 1.6302 | 0.31811 | 0.11929 | 0.6069 | 4.1162 | 7.1117 | 1.3167 | 0.080022 | 327.3146 | 25.15 | 57.75
2021-01-22 03:45 | 0.3948 | 0.24984 | 0.0858 | 0.46667 | 7.2541 | -9.4548 | 1.324 | 0.072745 | 326.7946 | 25.15 | 57.66
2021-01-22 03:50 | 0.57313 | 0.39048 | 0.10673 | 0.70527 | -1.4468 | 3.6069 | 1.3386 | 0.10185 | 326.7671 | 25.16 | 57.78
2021-01-22 03:55 | 0.43301 | 0.80686 | 0.17369 | 1.4105 | 6.1436 | 16.1996 | 1.3749 | 0.14549 | 326.1542 | 25.25 | 57.33
2021-01-22 04:00 | 0.6112 | 0.80399 | 0.13809 | 1.3705 | 20.2104 | 21.0864 | 1.3674 | 0.12365 | 327.7109 | 25.33 | 56.54
2021-01-22 04:05 | 0.50932 | 0.61014 | 0.14018 | 1.0733 | 28.481 | 18.4678 | 1.3528 | 0.09455 | 327.1264 | 25.39 | 56.24
2021-01-22 04:10 | 0.36929 | 0.65252 | 0.1674 | 1.1697 | 24.3986 | 20.5071 | 1.3456 | 0.094559 | 327.5912 | 25.42 | 56.43
2021-01-22 04:15 | 0.42022 | 0.61701 | 0.17158 | 1.1174 | 18.6016 | 17.8172 | 1.3529 | 0.087283 | 327.0254 | 25.46 | 56.23
2021-01-22 04:20 | 1.6554 | 0.58563 | 0.16531 | 1.0609 | 25.8758 | 27.4344 | 1.3675 | 0.11638 | 327.5038 | 25.5 | 56.16
2021-01-22 04:25 | 2.1649 | 0.6539 | 0.16113 | 1.1635 | 37.2052 | 34.6074 | 1.3748 | 0.15275 | 326.3917 | 25.54 | 56.12
2021-01-22 04:30 | 2.8273 | 0.98435 | 0.17579 | 1.6846 | 44.2895 | 32.3791 | 1.3822 | 0.18187 | 326.7824 | 25.64 | 56.05
2021-01-22 04:35 | 3.1451 | 1.32 | 0.19249 | 2.2179 | 50.0774 | 51.9823 | 1.3965 | 0.26184 | 326.2275 | 25.72 | 55.23
2021-01-22 04:40 | 2.5722 | 1.4879 | 0.32014 | 2.6009 | 79.1329 | 88.0669 | 1.4038 | 0.24003 | 327.1839 | 25.8 | 55.09
2021-01-22 04:45 | 2.6487 | 1.3719 | 0.31597 | 2.4189 | 41.0246 |  | 1.3966 | 0.26913 | 404.287 | 25.84 | 55.06
2021-01-22 04:50 | 2.0377 | 1.1755 | 0.29716 | 2.101 |  |  | 1.3967 | 0.21096 | 486.5246 | 25.94 | 54.99
2021-01-22 04:55 | 2.0499 | 1.5028 | 0.35986 | 2.6655 |  | 1.9353 | 1.4109 | 0.21818 | 486.6529 | 25.93 | 54.35
2021-01-22 05:00 | 2.1391 | 1.8059 | 0.37661 | 3.1426 | 20.5256 | 83.2638 | 1.411 | 0.21819 | 486.6296 | 25.93 | 54.49
2021-01-22 05:05 | 1.9228 | 1.8046 | 0.40593 | 3.1721 | 82.5657 | 104.9161 | 1.4111 | 0.29094 | 485.5445 | 25.93 | 54.66
2021-01-22 05:10 | 2.6351 | 2.0401 | 0.41417 | 3.5414 | 109.5272 | 99.2415 | 1.4034 | 0.29812 | 486.2243 | 25.93 | 53.75
2021-01-22 05:15 | 3.0681 | 2.4907 | 0.46232 | 4.2801 | 121.3195 | 85.6936 | 1.4107 | 0.36359 | 485.0481 | 25.98 | 53.82
2021-01-22 05:20 | 3.9341 | 2.5959 | 0.55021 | 4.5293 | 118.0884 | 96.8215 | 1.4399 | 0.45088 | 484.31 | 26.09 | 53.66
2021-01-22 05:25 | 3.8191 | 2.8017 | 0.58363 | 4.8782 | 115.5107 | 98.7269 | 1.4398 | 0.42902 | 484.7551 | 26.17 | 53.13
2021-01-22 05:30 | 5.9712 | 3.0122 | 0.63809 | 5.2553 | 122.531 | 95.122 | 1.4254 | 0.53816 | 484.6043 | 26.23 | 53.26
2021-01-22 05:35 | 4.7868 | 2.81 | 0.61084 | 4.9181 | 129.1106 | 116.1354 | 1.418 | 0.50903 | 484.0022 | 26.3 | 52.81
2021-01-22 05:40 | 5.1942 | 4.1161 | 0.80121 | 7.1104 | 135.4352 | 123.4785 | 1.4253 | 0.50903 | 486.5116 | 26.38 | 52.56
2021-01-22 05:45 | 6.8118 | 3.9651 | 0.77411 | 6.8519 | 181.9403 | 185.5257 | 1.44 | 0.53818 | 486.1271 | 26.58 | 52.29
2021-01-22 05:50 | 6.2133 | 3.389 | 0.66112 | 5.8559 | 206.3329 | 166.802 | 1.4254 | 0.54545 | 483.8948 | 26.66 | 52.01
2021-01-22 05:55 | 6.0612 | 3.7047 | 0.67374 | 6.3545 | 201.2205 | 187.2849 | 1.4401 | 0.61824 | 482.677 | 26.73 | 52.09
2021-01-22 06:00 | 5.8192 | 3.7784 | 0.74488 | 6.5386 | 184.6647 | 143.001 | 1.4547 | 0.56732 | 484.5967 | 26.85 | 51.69
2021-01-22 06:05 | 6.4933 | 3.1706 | 0.67156 | 5.5315 | 173.8053 | 124.5279 | 1.4981 | 0.62543 | 481.9883 | 26.87 | 51.3
2021-01-22 06:10 | 6.902 | 3.3159 | 0.59427 | 5.677 | 150.2145 | 127.9854 | 1.4548 | 0.61828 | 483.4419 | 26.89 | 51.78
2021-01-22 06:15 | 5.6796 | 2.976 | 0.60056 | 5.1602 | 134.1906 | 107.4585 | 1.4111 | 0.49463 | 484.4429 | 26.92 | 51.71
2021-01-22 06:20 | 3.4508 | 2.6946 | 0.57331 | 4.7036 | 126.4788 | 96.0509 | 1.4401 | 0.4364 | 483.9065 | 26.95 | 51.4
2021-01-22 06:25 | 4.4443 | 3.1002 | 0.60892 | 5.361 | 124.5421 | 86.6752 | 1.5202 | 0.42188 | 483.3286 | 26.96 | 51.57
2021-01-22 06:30 | 6.6213 | 2.7327 | 0.60468 | 4.7935 | 127.6484 | 118.5721 | 1.5056 | 0.46549 | 483.2902 | 27.01 | 51.18
2021-01-22 06:35 | 5.1574 | 2.6729 | 0.59845 | 4.6955 | 142.0122 | 110.2378 | 1.4693 | 0.45098 | 482.6624 | 27.05 | 51.27
2021-01-22 06:40 | 3.782 | 2.6701 | 0.56497 | 4.6557 | 121.4528 | 104.8271 | 1.4184 | 0.40005 | 484.7246 | 27.08 | 51.15
2021-01-22 06:45 | 4.4696 | 2.4435 | 0.46243 | 4.21 | 125.9435 | 105.5285 | 1.4838 | 0.43642 | 484.1087 | 27.14 | 50.93
2021-01-22 06:50 | 6.1253 | 2.9624 | 0.51477 | 5.0556 | 129.7602 | 101.8052 | 1.5275 | 0.61829 | 483.5255 | 27.16 | 51.01
2021-01-22 06:55 | 7.3481 | 2.912 | 0.56919 | 5.0328 | 117.8148 | 83.8172 | 1.484 | 0.68378 | 484.4453 | 27.23 | 50.91
2021-01-22 07:00 | 5.5916 | 2.7431 | 0.60068 | 4.8055 | 128.5943 | 112.9734 | 1.3823 | 0.48746 | 483.1057 | 27.36 | 50.96
2021-01-22 07:05 | 4.5975 | 2.5735 | 0.59642 | 4.5412 | 122.2105 | 100.4888 | 1.3458 | 0.32736 | 483.5947 | 27.42 | 50.45
2021-01-22 07:10 | 5.1326 | 2.8753 | 0.58807 | 4.9954 | 120.8892 | 112.0352 | 1.3458 | 0.43648 | 481.9573 | 27.45 | 50.43
2021-01-22 07:15 | 5.6042 | 2.8099 | 0.51485 | 4.822 | 135.8858 | 157.2835 | 1.3459 | 0.64022 | 483.3895 | 27.52 | 50.4
2021-01-22 07:20 | 6.101 | 2.6257 | 0.5023 | 4.5249 | 189.943 | 179.6311 | 1.3823 | 0.72753 | 482.1881 | 27.61 | 50.17
2021-01-22 07:25 | 5.9092 | 2.6308 | 0.47085 | 4.5034 | 170.4297 | 112.7334 | 1.4185 | 0.41464 | 481.6893 | 27.63 | 49.79
2021-01-22 07:30 | 7.5906 | 3.0091 | 0.55459 | 5.165 | 138.8528 | 112.4435 | 1.404 | 0.40739 | 482.1909 | 27.63 | 49.92
2021-01-22 07:35 | 7.9858 | 2.8413 | 0.54833 | 4.9036 | 170.6796 | 165.9824 | 1.375 | 0.45833 | 480.976 | 27.72 | 49.77
2021-01-22 07:40 | 8.0883 | 2.7022 | 0.52744 | 4.6674 | 180.2 | 131.7262 | 1.3533 | 0.45109 | 481.3202 | 27.81 | 49.71
2021-01-22 07:45 | 5.1586 | 2.3922 | 0.46883 | 4.1357 | 142.5858 | 88.9977 | 1.3532 | 0.40743 | 481.2819 | 27.84 | 49.57
2021-01-22 07:50 | 6.0124 | 2.3146 | 0.48561 | 4.0335 | 108.7738 | 76.4188 | 1.3315 | 0.41473 | 480.7221 | 27.84 | 49.76
2021-01-22 07:55 | 5.9489 | 2.5946 | 0.50446 | 4.4816 | 108.2373 | 94.7344 | 1.3679 | 0.50206 | 481.1671 | 27.88 | 49.73
2021-01-22 08:00 | 8.9169 | 2.4689 | 0.5212 | 4.3057 | 117.9887 | 84.2878 | 1.3825 | 0.47295 | 483.1588 | 27.95 | 49.5
2021-01-22 08:05 | 7.6691 | 2.1741 | 0.51705 | 3.8496 | 132.3969 | 111.2497 | 1.3535 | 0.42932 | 481.4096 | 28.04 | 49.41
2021-01-22 08:10 | 5.8091 | 1.9556 | 0.43541 | 3.433 | 124.5282 | 93.5872 | 1.3171 | 0.47298 | 480.7612 | 28.12 | 49.16
2021-01-22 08:15 | 6.3556 | 1.932 | 0.44369 | 3.4051 | 113.3969 | 72.7619 | 1.3241 | 0.62566 | 481.874 | 28.14 | 48.59
2021-01-22 08:20 | 5.9615 | 2.0579 | 0.46259 | 3.617 | 98.9305 | 77.0513 | 1.3315 | 0.54571 | 481.7964 | 28.15 | 48.89
2021-01-22 08:25 | 5.3121 | 1.9624 | 0.41028 | 3.4183 | 88.8057 | 73.1215 | 1.3243 | 0.40748 | 479.6106 | 28.19 | 48.91
2021-01-22 08:30 | 5.1729 | 1.848 | 0.43547 | 3.2681 | 88.7597 | 67.5177 | 1.31 | 0.33478 | 479.4811 | 28.22 | 49.26
2021-01-22 08:35 | 7.0218 | 2.3497 | 0.42928 | 4.0289 | 86.9629 | 59.5589 | 1.3103 | 0.37124 | 480.3943 | 28.27 | 49.58
2021-01-22 08:40 | 6.3742 | 2.2864 | 0.43781 | 3.9424 | 90.6864 | 54.9911 | 1.3034 | 0.37866 | 478.539 | 28.34 | 50.3
2021-01-22 08:45 | 5.228 | 2.6573 | 0.46725 | 4.5384 | 84.8929 | 63.1137 | 1.2892 | 0.32776 | 479.917 | 28.39 | 50.74
2021-01-22 08:50 | 5.5453 | 2.2084 | 0.4357 | 3.8166 | 89.7848 | 84.2064 | 1.2888 | 0.34223 | 480.0186 | 28.41 | 49.98
2021-01-22 08:55 | 4.3466 | 2.036 | 0.42729 | 3.5482 | 94.6522 | 67.2926 | 1.2742 | 0.33492 | 479.9606 | 28.47 | 49.61
2021-01-22 09:00 | 3.1982 | 2.3248 | 0.54646 | 4.1121 | 86.6537 | 69.7633 | 1.2664 | 0.32023 | 478.5339 | 28.5 | 48.53
2021-01-22 09:05 | 3.732 | 2.1861 | 0.52325 | 3.8741 | 95.112 | 67.9255 | 1.2659 | 0.28375 | 478.6035 | 28.56 | 47.5
2021-01-22 09:10 | 4.6099 | 1.9058 | 0.4792 | 3.4004 | 92.5045 | 47.5563 | 1.2657 | 0.30551 | 478.6397 | 28.6 | 46.87
2021-01-22 09:15 | 5.1948 | 2.1579 | 0.49794 | 3.8078 | 85.9692 | 60.6165 | 1.28 | 0.34182 | 479.1995 | 28.63 | 46.35
2021-01-22 09:20 | 4.6736 | 1.9385 | 0.46454 | 3.4359 | 103.8422 | 88.4284 | 1.2584 | 0.3346 | 479.5805 | 28.67 | 46.65
2021-01-22 09:25 | 4.7372 | 1.589 | 0.36409 | 2.7998 | 100.0711 | 62.3674 | 1.2729 | 0.3055 | 479.5729 | 28.68 | 46.58
2021-01-22 09:30 | 4.6625 | 1.6032 | 0.45006 | 2.9055 | 95.818 | 60.2404 | 1.2588 | 0.33472 | 479.33 | 28.72 | 47.4
2021-01-22 09:35 | 4.0777 | 1.6679 | 0.48159 | 3.0382 | 81.9203 | 49.3805 | 1.2592 | 0.3421 | 478.0839 | 28.76 | 48
2021-01-22 09:40 | 3.2487 | 1.7071 | 0.51289 | 3.1318 | 84.8479 | 50.6947 | 1.2517 | 0.29836 | 478.6475 | 28.8 | 47.35
2021-01-22 09:45 | 2.9685 | 1.6444 | 0.4501 | 2.9706 | 89.1407 | 60.409 | 1.2517 | 0.29837 | 475.9449 | 28.85 | 47.27
2021-01-22 09:50 | 2.7778 | 2.0476 | 0.54647 | 3.685 | 100.6315 | 76.7377 | 1.2519 | 0.35663 | 479.4222 | 28.92 | 47.43
2021-01-22 09:55 | 3.3643 | 2.1051 | 0.557 | 3.7838 | 106.9935 | 71.6994 | 1.2593 | 0.66967 | 480.2885 | 29 | 47.47
2021-01-22 10:00 | 2.931 | 1.6366 | 0.48999 | 2.9986 | 100.9881 | 66.8666 | 1.252 | 0.42946 | 478.0931 | 29.07 | 47.26
2021-01-22 10:05 | 4.8041 | 2.3496 | 0.46695 | 4.0706 | 86.9894 | 61.7479 | 1.252 | 0.33483 | 479.0816 | 29.11 | 47.11
2021-01-22 10:10 | 4.1036 | 2.2474 | 0.51516 | 3.9579 | 88.3736 | 58.1749 | 1.2521 | 0.37125 | 477.8683 | 29.19 | 47.11
2021-01-22 10:15 | 3.3518 | 1.761 | 0.5403 | 3.2397 | 92.7904 | 68.5452 | 1.2448 | 0.30575 | 478.2998 | 29.24 | 47.03
2021-01-22 10:20 | 3.1593 | 1.509 | 0.47936 | 2.7924 | 84.0264 | 40.4998 | 1.2443 | 0.28378 | 478.501 | 29.27 | 45.86
2021-01-22 10:25 | 2.8145 | 1.5195 | 0.48759 | 2.8167 | 65.6017 | 27.8443 | 1.2366 | 0.26915 | 478.5635 | 29.32 | 45.02
2021-01-22 10:30 | 3.3489 | 1.8619 | 0.52936 | 3.3854 | 75.0144 | 51.4527 | 1.2365 | 0.25456 | 477.5141 | 29.37 | 44.53
2021-01-22 10:35 | 3.3869 | 1.9955 | 0.50841 | 3.5672 | 81.4886 | 47.3856 | 1.2291 | 0.24 | 477.9828 | 29.42 | 44.27
2021-01-22 10:40 | 3.8202 | 2.0394 | 0.59007 | 3.7162 | 99.9875 | 73.9999 | 1.2438 | 0.34186 | 477.2822 | 29.5 | 44.33
2021-01-22 10:45 | 4.4577 | 1.7899 | 0.56506 | 3.3067 | 99.8214 | 39.8491 | 1.244 | 0.42922 | 477.0574 | 29.59 | 44.51
2021-01-22 10:50 | 3.8082 | 1.6179 | 0.48973 | 2.9677 | 98.081 | 73.199 | 1.244 | 0.47288 | 477.9637 | 29.67 | 44.35
2021-01-22 10:55 | 4.3949 | 1.4025 | 0.4333 | 2.5831 | 90.4559 | 43.7095 | 1.237 | 0.42203 | 478.2691 | 29.75 | 44.58
2021-01-22 11:00 | 5.3487 | 1.4089 | 0.4834 | 2.6451 | 86.5781 | 47.0586 | 1.2294 | 0.34917 | 477.3062 | 29.79 | 43.79
2021-01-22 11:05 | 4.8128 | 1.5969 | 0.47911 | 2.927 | 81.4056 | 37.7795 | 1.2291 | 0.35636 | 477.8495 | 29.84 | 43.17
2021-01-22 11:10 | 4.7614 | 1.7605 | 0.53554 | 3.2363 | 83.21 | 50.201 | 1.229 | 0.39269 | 478.3252 | 29.9 | 42.78
2021-01-22 11:15 | 3.6284 | 1.751 | 0.5209 | 3.2049 | 85.6956 | 49.4883 | 1.2217 | 0.37814 | 477.7233 | 29.95 | 42.67
2021-01-22 11:20 | 4.9426 | 2.1972 | 0.6761 | 4.0441 | 90.5152 | 48.7632 | 1.2224 | 0.40747 | 475.7577 | 30.03 | 43.82
2021-01-22 11:25 | 3.459 | 1.9854 | 0.60823 | 3.6515 | 97.9038 | 75.7866 | 1.2394 | 0.3937 | 475.1777 | 30.13 | 48.09
2021-01-22 11:30 | 3.064 | 1.8791 | 0.5769 | 3.4593 | 119.5268 | 61.7295 | 1.2543 | 0.2844 | 476.612 | 30.14 | 48.57
2021-01-22 11:35 | 3.1533 | 1.7408 | 0.54333 | 3.2117 | 120.4439 | 74.4846 | 1.2616 | 0.29169 | 475.0645 | 30.14 | 48.53
2021-01-22 11:40 | 3.4846 | 2.0196 | 0.59986 | 3.6977 | 116.7353 | 66.6592 | 1.2613 | 0.3208 | 476.1744 | 30.15 | 48.08
2021-01-22 11:45 | 3.7397 | 1.9908 | 0.51803 | 3.5717 | 110.4696 | 58.7626 | 1.2685 | 0.31349 | 476.6727 | 30.18 | 47.87
2021-01-22 11:50 | 3.5087 | 2.3128 | 0.62267 | 4.1679 | 95.0273 | 45.4212 | 1.2754 | 0.32066 | 477.8199 | 30.22 | 46.94
2021-01-22 11:55 | 3.1132 | 1.9805 | 0.61009 | 3.6459 | 91.2613 | 51.1578 | 1.2827 | 0.34253 | 478.2892 | 30.25 | 46.87
2021-01-22 12:00 | 3.1771 | 2.1228 | 0.66463 | 3.9186 | 98.1855 | 64.95 | 1.2754 | 0.35712 | 474.6808 | 30.25 | 46.91
2021-01-22 12:05 | 4.2493 | 2.1586 | 0.6626 | 3.9714 | 103.5862 | 67.499 | 1.2756 | 0.42276 | 476.1054 | 30.3 | 47.02
2021-01-22 12:10 | 4.1239 | 1.6588 | 0.6147 | 3.1553 | 106.634 | 71.2221 | 1.2908 | 0.4011 | 475.774 | 30.35 | 48.08
2021-01-22 12:15 | 3.1043 | 1.3147 | 0.47231 | 2.4875 | 93.8597 | 31.6919 | 1.2843 | 0.35026 | 475.5294 | 30.33 | 49.44
2021-01-22 12:20 | 2.7839 | 1.484 | 0.51201 | 2.7867 | 75.6608 | 43.296 | 1.2765 | 0.34283 | 476.8187 | 30.28 | 48.75
2021-01-22 12:25 | 4.0343 | 1.9489 | 0.55173 | 3.5411 | 87.5691 | 47.8495 | 1.2907 | 0.45942 | 477.4046 | 30.32 | 48.02
2021-01-22 12:30 | 3.4603 | 1.6535 | 0.51404 | 3.0486 | 100.5034 | 71.3095 | 1.2982 | 0.48136 | 475.2183 | 30.35 | 48.26
2021-01-22 12:35 | 3.1938 | 1.8803 | 0.58148 | 3.4637 | 106.9632 | 72.3989 | 1.2916 | 0.37215 | 475.3812 | 30.42 | 49.22
2021-01-22 12:40 | 3.0678 | 1.991 | 0.57131 | 3.6211 | 104.0377 | 59.4633 | 1.285 | 0.32856 | 476.0526 | 30.48 | 50.31
2021-01-22 12:45 | 3.9764 | 2.056 | 0.52524 | 3.6767 | 118.8361 | 80.1003 | 1.3 | 0.33595 | 473.7629 | 30.54 | 50.74
2021-01-22 12:50 | 4.5136 | 2.2562 | 0.55048 | 4.0088 | 125.1944 | 78.7337 | 1.3 | 0.35057 | 473.6295 | 30.61 | 50.65
2021-01-22 12:55 | 4.296 | 2.4287 | 0.55255 | 4.2754 | 127.6827 | 72.5202 | 1.3 | 0.38707 | 473.1102 | 30.63 | 50.46
2021-01-22 13:00 | 3.5549 | 2.3907 | 0.65979 | 4.3244 | 134.4129 | 70.6488 | 1.2856 | 0.37982 | 473.9626 | 30.7 | 50.59
2021-01-22 13:05 | 3.6964 | 2.1348 | 0.65573 | 3.9281 | 148.3271 | 102.5888 | 1.3004 | 0.38721 | 473.7821 | 30.75 | 50.92
2021-01-22 13:10 | 2.8526 | 1.7237 | 0.59907 | 3.2413 | 135.2692 | 71.3802 | 1.3006 | 0.34342 | 475.2168 | 30.78 | 51.14
2021-01-22 13:15 | 3.2874 | 1.688 | 0.57803 | 3.1655 | 133.524 | 82.9306 | 1.2933 | 0.35072 | 474.7203 | 30.78 | 51.05
2021-01-22 13:20 | 3.2749 | 1.5551 | 0.52973 | 2.9135 | 146.0821 | 81.6582 | 1.2934 | 0.35074 | 474.6812 | 30.78 | 51.23
2021-01-22 13:25 | 3.6846 | 1.4195 | 0.46039 | 2.6362 | 141.2722 | 69.454 | 1.2935 | 0.42385 | 473.6533 | 30.78 | 51.34
2021-01-22 13:30 | 5.0026 | 1.5403 | 0.48355 | 2.8487 | 136.6445 | 77.9641 | 1.2862 | 0.43118 | 472.5614 | 30.8 | 51.42
2021-01-22 13:35 | 5.7574 | 1.9791 | 0.6286 | 3.6644 | 137.3167 | 62.8652 | 1.2862 | 0.43117 | 473.5258 | 30.85 | 51.22
2021-01-22 13:40 | 6.4228 | 1.639 | 0.59498 | 3.1073 | 151.5176 | 98.8861 | 1.2862 | 0.48965 | 472.4033 | 30.9 | 51.14
2021-01-22 13:45 | 5.963 | 1.7792 | 0.59085 | 3.3159 | 147.217 | 70 | 1.2791 | 0.50433 | 472.7959 | 30.94 | 51.3
2021-01-22 13:50 | 5.1186 | 1.6791 | 0.59507 | 3.1688 | 148.0084 | 93.7311 | 1.2718 | 0.44587 | 472.7081 | 30.99 | 51.2
2021-01-22 13:55 | 5.0927 | 1.7146 | 0.53406 | 3.1623 | 146.7525 | 87.1343 | 1.2645 | 0.36545 | 472.684 | 31.02 | 51.01
2021-01-22 14:00 | 4.0433 | 1.5582 | 0.53193 | 2.9183 | 145.8237 | 78.5519 | 1.2644 | 0.35812 | 472.6927 | 31.03 | 50.87
2021-01-22 14:05 | 5.6172 | 1.8956 | 0.58871 | 3.4944 | 149.8086 | 85.2685 | 1.2644 | 0.40929 | 472.0751 | 31.09 | 50.74
2021-01-22 14:10 | 6.3083 | 1.8491 | 0.58032 | 3.4146 | 132.1542 | 68.1449 | 1.2791 | 0.39468 | 473.5144 | 31.15 | 50.62
2021-01-22 14:15 | 5.9874 | 1.7596 | 0.54869 | 3.2459 | 118.9402 | 99.2175 | 1.3081 | 0.35808 | 472.0302 | 31.16 | 50.25
2021-01-22 14:20 | 6.2435 | 1.8584 | 0.5466 | 3.3952 | 135.7602 | 78.1461 | 1.3008 | 0.42386 | 473.0768 | 31.14 | 50.37
2021-01-22 14:25 | 5.7702 | 1.7213 | 0.59497 | 3.2334 | 141.3825 | 82.6616 | 1.2789 | 0.42387 | 472.0058 | 31.16 | 50.36
2021-01-22 14:30 | 4.6446 | 1.8243 | 0.58869 | 3.3829 | 140.1306 | 60.8631 | 1.279 | 0.43851 | 472.4658 | 31.18 | 50.41
2021-01-22 14:35 | 4.7859 | 2.0028 | 0.56564 | 3.6356 | 141.3158 | 86.495 | 1.2865 | 0.43857 | 470.8144 | 31.21 | 50.6
2021-01-22 14:40 | 3.7751 | 2.1689 | 0.64136 | 3.9659 | 154.8031 | 75.052 | 1.323 | 0.49706 | 471.7823 | 31.24 | 50.58
2021-01-22 14:45 | 4.3128 | 2.121 | 0.66662 | 3.9177 | 157.0106 | 103.8445 | 1.3816 | 0.50439 | 471.7167 | 31.27 | 50.58
2021-01-22 14:50 | 5.2087 | 2.1978 | 0.60144 | 3.9703 | 165.1012 | 107.6854 | 1.3962 | 0.51171 | 472.6604 | 31.32 | 50.47
2021-01-22 14:55 | 4.402 | 1.9809 | 0.60769 | 3.6461 | 171.8726 | 100.3042 | 1.3449 | 0.45318 | 471.6308 | 31.35 | 50.18
2021-01-22 15:00 | 4.8489 | 1.8721 | 0.57393 | 3.4436 | 148.4306 | 91.8096 | 1.3154 | 0.48963 | 472.2389 | 31.35 | 49.76
2021-01-22 15:05 | 4.4388 | 1.6675 | 0.55702 | 3.1109 | 131.1113 | 76.1269 | 1.3152 | 0.46763 | 473.9233 | 31.31 | 49.52
2021-01-22 15:10 | 4.2591 | 1.7495 | 0.57375 | 3.2555 | 130.4383 | 84.261 | 1.3077 | 0.43104 | 472.4916 | 31.28 | 49.31
2021-01-22 15:15 | 4.2845 | 1.8207 | 0.55481 | 3.3436 | 139.7836 | 72.7259 | 1.3003 | 0.39449 | 473.5909 | 31.25 | 49.29
2021-01-22 15:20 | 3.1713 | 1.449 | 0.498 | 2.719 | 127.2002 | 106.0854 | 1.2855 | 0.36521 | 473.6771 | 31.24 | 49
2021-01-22 15:25 | 3.1836 | 1.3953 | 0.50002 | 2.6388 | 126.281 | 83.0145 | 1.2781 | 0.33594 | 472.7184 | 31.24 | 48.68
2021-01-22 15:30 | 3.0173 | 1.4323 | 0.4748 | 2.6702 | 132.3634 | 71.7203 | 1.2853 | 0.33594 | 472.7468 | 31.23 | 48.65
2021-01-22 15:35 | [9 empty] | 31.22 | 48.79
2021-01-22 15:40 | 5.7291 | 2.1591 | 0.58838 | 3.898 | 121.0369 | 82.202 | 1.3075 | 0.38714 | 474.6544 | 31.26 | 49.04
2021-01-22 15:45 | 4.2454 | 1.6121 | 0.46647 | 2.9375 | 126.2158 | 101.2652 | 1.3293 | 0.33599 | 474.1383 | 31.28 | 48.85
2021-01-22 15:50 | 5.2041 | 1.7833 | 0.51477 | 3.2462 | 131.6092 | 82.3964 | 1.3366 | 0.42361 | 472.1853 | 31.23 | 48.86
2021-01-22 15:55 | 6.5471 | 1.9712 | 0.58413 | 3.6057 | 129.7241 | 120.9367 | 1.3659 | 0.52589 | 473.7033 | 31.23 | 48.98
2021-01-22 16:00 | 4.6159 | 1.7339 | 0.52316 | 3.181 | 109.4516 | 48.3121 | 1.3512 | 0.47473 | 474.2343 | 31.24 | 48.81
2021-01-22 16:05 | 4.2832 | 1.8133 | 0.55465 | 3.3342 | 101.5495 | 99.0128 | 1.3073 | 0.43819 | 475.2886 | 31.24 | 48.7
2021-01-22 16:10 | 4.6277 | 1.698 | 0.53356 | 3.1362 | 96.0931 | 84.015 | 1.2779 | 0.39431 | 472.2872 | 31.23 | 48.4
2021-01-22 16:15 | 5.1254 | 1.5017 | 0.45156 | 2.7535 | 78.3054 | 46.5251 | 1.2777 | 0.40155 | 472.897 | 31.22 | 48.07
2021-01-22 16:20 | 5.3672 | 1.437 | 0.41157 | 2.6143 | 62.2796 | 61.3289 | 1.2774 | 0.37957 | 472.5655 | 31.19 | 47.66
2021-01-22 16:25 | 6.2231 | 1.4959 | 0.46195 | 2.7549 | 58.6075 | 57.9941 | 1.27 | 0.40145 | 472.566 | 31.2 | 47.56
2021-01-22 16:30 | 6.8598 | 2.0993 | 0.49958 | 3.7154 | 50.8417 | 88.5515 | 1.2696 | 0.51077 | 472.645 | 31.25 | 46.72
2021-01-22 16:35 | 4.7006 | 2.0266 | 0.51004 | 3.6164 | 81.545 | 79.256 | 1.2695 | 0.48154 | 473.1024 | 31.31 | 46.4
2021-01-22 16:40 | 4.9811 | 1.6498 | 0.43233 | 2.9592 | 114.3358 | 74.0986 | 1.2621 | 0.41584 | 472.088 | 31.33 | 46.14
2021-01-22 16:45 | 3.473 | 1.4098 | 0.48466 | 2.6478 | 121.7484 | 67.8252 | 1.2544 | 0.37925 | 473.2267 | 31.35 | 45.46
2021-01-22 16:50 | 5.337 | 1.8806 | 0.51611 | 3.3988 | 124.5939 | 77.2711 | 1.269 | 0.43029 | 474.2577 | 31.36 | 45.36
2021-01-22 16:55 | 6.8428 | 1.8394 | 0.51396 | 3.3355 | 138.2255 | 80.0613 | 1.2761 | 0.48129 | 472.693 | 31.38 | 45.13
2021-01-22 17:00 | 6.307 | 1.9928 | 0.55385 | 3.6084 | 131.7072 | 82.1191 | 1.2689 | 0.4959 | 472.1576 | 31.4 | 45.16
2021-01-22 17:05 | 6.2188 | 1.6728 | 0.4994 | 3.0635 | 129.6781 | 71.3465 | 1.2692 | 0.4887 | 474.0767 | 31.41 | 45.57
2021-01-22 17:10 | 4.9167 | 1.6606 | 0.50993 | 3.0554 | 123.2114 | 66.8979 | 1.2693 | 0.43768 | 474.0848 | 31.38 | 45.82
2021-01-22 17:15 | 4.9171 | 1.4773 | 0.49948 | 2.7639 | 113.894 | 75.3026 | 1.2621 | 0.43772 | 473.527 | 31.38 | 46.01
2021-01-22 17:20 | 5.9651 | 1.3912 | 0.42608 | 2.5586 | 98.7732 | 50.296 | 1.2622 | 0.46695 | 474.0349 | 31.35 | 46.33
2021-01-22 17:25 | 4.7773 | 1.1749 | 0.38621 | 2.1871 | 94.5651 | 75.6194 | 1.2623 | 0.53263 | 473.0567 | 31.31 | 46.48
2021-01-22 17:30 | 4.0244 | 1.108 | 0.40308 | 2.1035 | 99.9593 | 65.8628 | 1.2625 | 0.45245 | 474.5429 | 31.29 | 46.94
2021-01-22 17:35 | 3.8727 | 1.1893 | 0.44104 | 2.2661 | 117.9139 | 101.7074 | 1.263 | 0.38693 | 475.4432 | 31.25 | 47.91
2021-01-22 17:40 | 3.5802 | 1.0376 | 0.41181 | 2.0023 | 125.2253 | 66.5918 | 1.2635 | 0.37979 | 474.7945 | 31.21 | 48.9
2021-01-22 17:45 | 3.0949 | 0.98297 | 0.36985 | 1.8787 | 100.6931 | 70.7778 | 1.2637 | 0.32872 | 473.743 | 31.17 | 49.39
2021-01-22 17:50 | 2.4302 | 0.92416 | 0.3573 | 1.7739 | 39.6611 | 49.0136 | 1.2639 | 0.28493 | 473.7351 | 31.13 | 49.82
2021-01-22 17:55 | 3.1342 | 1.045 | 0.27748 | 1.8793 | 40.2615 | 68.0986 | 1.2642 | 0.27037 | 473.7318 | 31.08 | 50.33
2021-01-22 18:00 | 2.8144 | 1.0025 | 0.31531 | 1.8519 | 53.3908 | 62.0181 | 1.2568 | 0.23383 | 473.7887 | 31.05 | 50.37
2021-01-22 18:05 | 3.1727 | 0.8873 | 0.27748 | 1.6376 | 52.0728 | 37.7957 | 1.2569 | 0.23384 | 472.8329 | 30.99 | 50.63
2021-01-22 18:10 | 2.5586 | 1.0244 | 0.2943 | 1.8646 | 48.7456 | 45.9107 | 1.2495 | 0.27767 | 474.981 | 30.94 | 50.73
2021-01-22 18:15 | 2.5199 | 0.82824 | 0.26484 | 1.5365 | 42.5499 | 29.0931 | 1.264 | 0.28496 | 473.558 | 30.89 | 50.67
2021-01-22 18:20 | 3.9777 | 0.82265 | 0.29633 | 1.5573 | 32.548 | 37.1115 | 1.2639 | 0.29953 | 474.2242 | 30.83 | 50.58
2021-01-22 18:25 | 4.0668 | 0.64023 | 0.24167 | 1.223 | 25.4956 | 27.6031 | 1.2564 | 0.23376 | 474.351 | 30.78 | 50.5
2021-01-22 18:30 | 4.3732 | 0.60314 | 0.24374 | 1.1704 | 24.0601 | 31.7937 | 1.249 | 0.19721 | 473.459 | 30.73 | 50.36
2021-01-22 18:35 | 2.7995 | 0.59884 | 0.25206 | 1.17 | 19.8392 | 34.8925 | 1.2413 | 0.18984 | 474.2176 | 30.67 | 49.84
2021-01-22 18:40 | 2.8372 | 0.60007 | 0.2667 | 1.1886 | 14.508 | 29.0263 | 1.2483 | 0.2117 | 474.9024 | 30.63 | 49.46
2021-01-22 18:45 | 2.9008 | 0.64796 | 0.26458 | 1.2557 | 14.8439 | 29.1254 | 1.2482 | 0.24088 | 476.5487 | 30.6 | 49.31
2021-01-22 18:50 | 2.926 | 0.56296 | 0.23305 | 1.096 | 16.171 | 22.0282 | 1.2407 | 0.24815 | 476.6964 | 30.54 | 49.23
2021-01-22 18:55 | 3.2965 | 0.82732 | 0.24565 | 1.5138 | 15.343 | 34.4783 | 1.2407 | 0.23355 | 475.2429 | 30.48 | 49.39
2021-01-22 19:00 | 3.5006 | 0.63274 | 0.27081 | 1.2407 | 15.8625 | 18.4483 | 1.2406 | 0.22622 | 476.9095 | 30.44 | 49.25
2021-01-22 19:05 | 2.4654 | 0.56146 | 0.27498 | 1.1356 | 7.174 | 24.6288 | 1.2404 | 0.18242 | 477.0787 | 30.37 | 49.17
2021-01-22 19:10 | 1.3667 | 0.55456 | 0.24557 | 1.0956 | 9.7791 | 24.3405 | 1.233 | 0.15322 | 476.7464 | 30.28 | 49.22
2021-01-22 19:15 | 0.86846 | 0.35871 | 0.19937 | 0.74921 | 10.064 | 14.345 | 1.2402 | 0.13131 | 476.3923 | 30.19 | 49.24
2021-01-22 19:20 | 1.9539 | 0.25053 | 0.16788 | 0.554 | 3.2591 | 17.3377 | 1.2328 | 0.11672 | 478.1292 | 30.09 | 49.4
2021-01-22 19:25 | 1.8902 | 0.3149 | 0.17629 | 0.65898 | 5.7218 | -0.8787 | 1.2402 | 0.16779 | 477.1655 | 30.02 | 49.78
2021-01-22 19:30 | 1.2645 | 0.34231 | 0.1826 | 0.7073 | 3.1165 | 30.5421 | 1.2403 | 0.14592 | 477.7298 | 29.97 | 50.08
2021-01-22 19:35 | 1.5584 | 0.43957 | 0.18471 | 0.8585 | 11.8031 | 9.7593 | 1.2331 | 0.13863 | 477.7462 | 29.93 | 50.42
2021-01-22 19:40 | 1.073 | 0.43136 | 0.19102 | 0.85432 | 178.687 | 417.6893 | 1.2331 | 0.11675 | 345.6394 | 29.9 | 50.57
2021-01-22 19:45 | 0.95815 | 0.50535 | 0.21202 | 0.98664 | 224.5493 | 125.2186 | 1.2332 | 0.12405 | 329.5925 | 29.86 | 50.87
2021-01-22 19:50 | 0.90711 | 0.47525 | 0.20364 | 0.93212 | 100.5944 | 36.5705 | 1.226 | 0.11676 | 328.5777 | 29.82 | 51.14
2021-01-22 19:55 | 1.1755 | 0.49037 | 0.23096 | 0.98261 | 32.6593 | 35.225 | 1.2334 | 0.10218 | 329.6233 | 29.78 | 51.5
2021-01-22 20:00 | 1.4951 | 0.41233 | 0.19318 | 0.82521 | 19.8119 | 20.7421 | 1.2335 | 0.11679 | 330.6437 | 29.77 | 51.72
2021-01-22 20:05 | 1.3545 | 0.43287 | 0.17848 | 0.84409 | 6.3278 | 26.9467 | 1.2335 | 0.11678 | 329.1732 | 29.7 | 51.87
2021-01-22 20:10 | 1.3801 | 0.41234 | 0.18058 | 0.81263 | 3.6496 | 26.5594 | 1.2336 | 0.13139 | 328.6842 | 29.66 | 52.09
2021-01-22 20:15 | 1.4825 | 0.6316 | 0.19321 | 1.1613 | 8.7009 | 27.6671 | 1.2337 | 0.1679 | 329.1821 | 29.64 | 52.45
2021-01-22 20:20 | 1.5721 | 0.57957 | 0.18272 | 1.069 | 9.4683 | 26.9631 | 1.2411 | 0.12411 | 328.6563 | 29.63 | 52.61
2021-01-22 20:25 | 1.3548 | 0.47133 | 0.16382 | 0.88629 | 5.2966 | 26.401 | 1.2192 | 0.10951 | 329.1814 | 29.62 | 52.67
2021-01-22 20:30 | 1.2909 | 0.43982 | 0.14912 | 0.82329 | 5.1535 | 45.9108 | 1.2119 | 0.13141 | 329.7517 | 29.57 | 52.84
2021-01-22 20:35 | 1.3422 | 0.51112 | 0.15543 | 0.93889 | 12.0667 | 28.367 | 1.2193 | 0.16793 | 329.2366 | 29.54 | 53.14
2021-01-22 20:40 | 1.2783 | 0.48783 | 0.14913 | 0.8969 | 14.4701 | 32.5091 | 1.2267 | 0.15333 | 329.7605 | 29.53 | 53.21
2021-01-22 20:45 | 1.4955 | 0.59467 | 0.16803 | 1.0796 | 21.044 | 39.7464 | 1.2339 | 0.15332 | 328.8006 | 29.48 | 53.2
2021-01-22 20:50 | 1.5723 | 0.68928 | 0.17644 | 1.233 | 13.6522 | 18.8063 | 1.234 | 0.16064 | 328.7823 | 29.47 | 53.44
2021-01-22 20:55 | 2.1859 | 0.67558 | 0.19325 | 1.2288 | 14.7159 | 31.2418 | 1.234 | 0.19715 | 330.1821 | 29.44 | 53.6
2021-01-22 21:00 | 1.9176 | 0.68798 | 0.19327 | 1.2478 | 21.9174 | 41.4313 | 1.2414 | 0.18256 | 330.1611 | 29.43 | 53.86
2021-01-22 21:05 | 1.6491 | 0.51527 | 0.15124 | 0.94107 | 25.0764 | 19.7788 | 1.234 | 0.16064 | 328.6644 | 29.39 | 53.86
2021-01-22 21:10 | 1.2144 | 0.52758 | 0.14073 | 0.94942 | 21.056 | 32.5914 | 1.2413 | 0.16064 | 329.8079 | 29.31 | 53.98
2021-01-22 21:15 | 1.777 | 0.58655 | 0.11764 | 1.0188 | 16.926 | 18.9408 | 1.2414 | 0.18256 | 329.2831 | 29.29 | 54.24
2021-01-22 21:20 | 1.662 | 0.43719 | 0.10924 | 0.77938 | 18.2972 | 19.5143 | 1.2487 | 0.16066 | 329.2803 | 29.28 | 54.37
2021-01-22 21:25 | 1.5724 | 0.33439 | 0.11764 | 0.63021 | 13.1625 | 16.2614 | 1.256 | 0.12414 | 329.8315 | 29.26 | 54.36
2021-01-22 21:30 | 0.57528 | 0.26998 | 0.11974 | 0.53357 | 7.7113 | 10.7078 | 1.2633 | 0.10223 | 330.4218 | 29.2 | 54.51
2021-01-22 21:35 | 1.956 | 0.28917 | 0.12814 | 0.5714 | 9.6547 | 15.5048 | 1.2706 | 0.10223 | 329.9135 | 29.18 | 54.65
2021-01-22 21:40 | 2.4543 | 0.25076 | 0.12603 | 0.51041 | 11.2385 | 24.6858 | 1.2777 | 0.11682 | 328.9626 | 29.14 | 54.45
2021-01-22 21:45 | 1.3291 | 0.23154 | 0.1176 | 0.47251 | 8.2815 | 6.6661 | 1.2921 | 0.2628 | 329.5673 | 29.12 | 54.05
2021-01-22 21:50 | 1.8016 | 0.20135 | 0.10708 | 0.41572 | 10.9069 | 3.7924 | 1.2918 | 0.27735 | 329.6771 | 29.08 | 53.69
2021-01-22 21:55 | 0.90716 | 0.32735 | 0.094477 | 0.59626 | 5.8058 | 15.4242 | 1.2918 | 0.27733 | 330.2591 | 29.04 | 53.68
2021-01-22 22:00 | 1.8274 | 0.39453 | 0.11129 | 0.71605 | 11.5829 | 5.5819 | 1.292 | 0.21898 | 329.6832 | 29.04 | 54.09
2021-01-22 22:05 | 1.1117 | 0.21643 | 0.098685 | 0.43044 | 7.9939 | 11.6842 | 1.2846 | 0.18977 | 330.2943 | 28.98 | 54.09
2021-01-22 22:10 | 1.444 | 0.36851 | 0.11339 | 0.67825 | 5.9192 | 11.6851 | 1.2774 | 0.19708 | 330.313 | 28.94 | 54.4
2021-01-22 22:15 | 1.3295 | 0.5276 | 0.11973 | 0.92846 | 12.763 | 4.6634 | 1.2778 | 0.16794 | 330.7066 | 28.95 | 55.22
2021-01-22 22:20 | 0.85655 | 0.33851 | 0.10504 | 0.62392 | 8.6115 | 20.8743 | 1.2706 | 0.16065 | 330.1748 | 28.94 | 55.42
2021-01-22 22:25 | 0.88204 | 0.27818 | 0.10503 | 0.53144 | 11.6276 | 13.2332 | 1.2705 | 0.11683 | 331.3318 | 28.86 | 55.46
2021-01-22 22:30 | 1.1249 | 0.36451 | 0.094522 | 0.65325 | 19.2972 | 14.5828 | 1.2778 | 0.08762 | 330.2983 | 28.86 | 55.41
2021-01-22 22:35 | 0.43458 | 0.40832 | 0.10081 | 0.7267 | 13.7429 | 24.0194 | 1.2558 | 0.08031 | 330.8397 | 28.87 | 55.14
2021-01-22 22:40 | 1.6487 | 0.30005 | 0.10921 | 0.56913 | 16.7171 | -4.5601 | 1.2483 | 0.15331 | 329.8388 | 28.86 | 54.96
2021-01-22 22:45 | 0.75406 | 0.37952 | 0.10291 | 0.68464 | 15.5005 | 21.7989 | 1.263 | 0.15331 | 329.8571 | 28.84 | 55.05
2021-01-22 22:50 | 0.94575 | 0.34799 | 0.088203 | 0.62162 | 15.2751 | 27.3296 | 1.2702 | 0.1533 | 330.398 | 28.83 | 55.01
2021-01-22 22:55 | 1.1758 | 0.33841 | 0.10501 | 0.62584 | 25.0809 | 9.1817 | 1.2776 | 0.16791 | 330.4109 | 28.81 | 55.14
2021-01-22 23:00 | 1.3804 | 0.3535 | 0.090311 | 0.63008 | 20.164 | 27.5671 | 1.2922 | 0.16792 | 328.8745 | 28.77 | 55.41
2021-01-22 23:05 | 1.0736 | 0.32471 | 0.094505 | 0.59223 | 16.4409 | 18.0053 | 1.2921 | 0.16791 | 331.5655 | 28.71 | 55.43
2021-01-22 23:10 | 0.49848 | 0.20827 | 0.081911 | 0.40115 | 11.299 | -3.2823 | 1.2923 | 0.12411 | 330.5739 | 28.64 | 55.86
2021-01-22 23:15 | 0.79246 | 0.21238 | 0.079811 | 0.40326 | 5.0309 | 15.8902 | 1.285 | 0.12412 | 331.1696 | 28.57 | 56.1
2021-01-22 23:20 | 0.57516 | 0.24252 | 0.079809 | 0.44945 | 11.8407 | 8.9674 | 1.2776 | 0.065707 | 330.18 | 28.53 | 56.17
2021-01-22 23:25 | 0.56241 | 0.17676 | 0.079814 | 0.35076 | 4.3357 | -3.1904 | 1.2485 | 0.10222 | 330.3929 | 28.49 | 56.39
2021-01-22 23:30 | 0.21727 | 0.14523 | 0.084005 | 0.30872 | 0.7055 | 7.4639 | 1.2484 | 0.13141 | 329.4542 | 28.43 | 56.31
2021-01-22 23:35 | 1.0864 | 0.1466 | 0.084007 | 0.30872 | 1.9325 | -1.8711 | 1.2557 | 0.12411 | 330.5438 | 28.38 | 56.52
2021-01-22 23:40 | 1.0608 | 0.13975 | 0.084005 | 0.29822 | 0.16359 | 7.5764 | 1.2703 | 0.1022 | 331.1251 | 28.33 | 56.64
2021-01-22 23:45 | 0.46012 | 0.15756 | 0.090308 | 0.32973 | 1.4315 | 4.3967 | 1.2703 | 0.10221 | 330.1301 | 28.28 | 56.87
2021-01-22 23:50 |  | 0.20415 | 0.081908 | 0.39484 | 5.6033 | 4.4683 | 1.2849 | 0.18251 | 329.6068 | 28.28 | 56.89
2021-01-22 23:55 | 1.8148 | 0.22331 | 0.090301 | 0.43261 | 4.1408 | 5.4188 | 1.2848 | 0.1533 | 331.2179 | 28.26 | 56.75
2021-01-23 | 0.56215 | 0.17531 | 0.083974 | 0.35059 | 3.5977 | 4.7016 | 1.2844 | 0.14595 | 330.3471 | 28.2 | 56.14
2021-01-23 00:05 | 0.35762 | 0.16293 | 0.077652 | 0.3253 | 5.7628 | 0.18392 | 1.284 | 0.1532 | 332.5786 | 28.16 | 55.48
2021-01-23 00:10 | 0.62576 | 0.26696 | 0.090235 | 0.49944 | 5.4761 | 14.3543 | 1.2839 | 0.16778 | 331.0724 | 28.14 | 55.27
2021-01-23 00:15 | 0.43417 | 0.16837 | 0.075539 | 0.33153 | 12.1873 | 12.3201 | 1.291 | 0.15317 | 331.6336 | 28.13 | 55.08
2021-01-23 00:20 | 0.58737 | 0.13551 | 0.067142 | 0.27486 | 11.819 | 0.2656 | 1.2983 | 0.13129 | 331.7043 | 28.08 | 55.12
2021-01-23 00:25 | 0.28085 | 0.13959 | 0.07342 | 0.28739 | 10.1311 | 13.5728 | 1.3053 | 0.10938 | 331.892 | 27.98 | 54.84
2021-01-23 00:30 | 0.89353 | 0.11357 | 0.071315 | 0.24541 | 10.7223 | 5.4939 | 1.3051 | 0.087494 | 331.4936 | 27.9 | 54.82
2021-01-23 00:35 | 0.26801 | 0.11492 | 0.058718 | 0.23487 | 9.6278 | 2.287 | 1.2976 | 0.094767 | 332.6582 | 27.85 | 54.47
2021-01-23 00:40 | 0.19139 | 0.13678 | 0.062898 | 0.27046 | 5.6345 | 12.9838 | 1.29 | 0.10932 | 331.1891 | 27.83 | 53.94
2021-01-23 00:45 | 0.77822 | 0.091631 | 0.058697 | 0.20125 | 4.1233 | 2.4699 | 1.2971 | 0.10931 | 331.2634 | 27.8 | 53.71
2021-01-23 00:50 | -0.19133 | 0.095714 | 0.060781 | 0.20749 | 1.1224 | -2.2551 | 1.2823 | 0.10929 | 331.3754 | 27.76 | 53.3
2021-01-23 00:55 | -0.35714 | 0.10939 | 0.058685 | 0.22426 | 1.7449 | 5.5407 | 1.2823 | 0.12386 | 331.3556 | 27.78 | 53.22
2021-01-23 01:00 | 0.038257 | 0.086125 | 0.071246 | 0.20326 | 2.7137 | -4.244 | 1.2747 | 0.10926 | 331.9332 | 27.79 | 52.67
2021-01-23 01:05 |  |  |  |  | -3.2743 | 3.7231 |  |  | 331.9829 | 27.79 | 52.28
2021-01-23 01:10 |  |  |  |  | 1.7336 | 12.4921 |  |  | 332.6405 | 27.75 | 51.69
2021-01-23 01:15 |  |  |  |  | -0.76469 | -12.1433 |  |  | 331.7066 | 27.7 | 51.39
2021-01-23 01:20 |  |  |  |  | 0.27527 | -9.655 |  |  | 333.337 | 27.66 | 51.38
2021-01-23 01:25 |  |  |  |  | -2.2034 | -2.8767 |  |  | 333.1705 | 27.64 | 52.93
2021-01-23 01:30 |  |  |  |  | -4.5611 | 0.44896 |  |  | 332.0847 | 27.6 | 53.72
2021-01-23 01:35 |  |  |  |  | -7.2845 | -12.4061 |  |  | 332.1723 | 27.56 | 53.5
2021-01-23 01:40 |  |  |  |  | 5.249 | 17.6428 |  |  | 333.0804 | 27.51 | 51.03
2021-01-23 01:45 |  |  |  |  | 10.9404 | 20.6788 |  |  | 333.2443 | 27.53 | 49.49
2021-01-23 01:50 |  |  |  |  | 20.9191 | 6.5551 |  |  | 331.872 | 27.59 | 51.37
2021-01-23 01:55 |  |  |  |  | 30.7864 | 22.0282 |  |  | 332.9892 | 27.61 | 54.72
2021-01-23 02:00 |  |  |  |  | 27.3039 | 19.4897 |  |  | 331.2161 | 27.59 | 56.59
2021-01-23 02:05 |  |  |  |  | 27.0058 | 10.2319 |  |  | 332.0662 | 27.56 | 58.5
2021-01-23 02:10 | 0.025564 | 0.075362 | 0.054608 | 0.16803 | 29.02 | 15.3383 | 1.4018 | 0.043806 | 331.9869 | 27.52 | 59.62
2021-01-23 02:15 | -0.2174 | 0.079512 | 0.052534 | 0.17231 | 14.2 | 10.8853 | 1.3806 | 0.065741 | 332.4017 | 27.47 | 61.09
2021-01-23 02:20 | 0.1279 | 0.068553 | 0.05254 | 0.15762 | 8.7687 | 3.1105 | 1.3734 | 0.10958 | 330.8383 | 27.43 | 61.57
2021-01-23 02:25 | 0.012792 | 0.064453 | 0.056755 | 0.15555 | 12.1988 | 18.5132 | 1.3664 | 0.11691 | 331.8357 | 27.41 | 62.19
2021-01-23 02:30 | 0.076763 | 0.061717 | 0.054659 | 0.14926 | 11.2995 | 21.6369 | 1.3812 | 0.13154 | 331.299 | 27.39 | 62.56
2021-01-23 02:35 | 0.063964 | 0.093254 | 0.065165 | 0.20811 | 9.2313 | 8.4125 | 1.3884 | 0.16807 | 331.8588 | 27.38 | 62.38
2021-01-23 02:40 | 0.52451 | 0.08777 | 0.065166 | 0.1997 | 13.7448 | -0.14328 | 1.3884 | 0.15345 | 332.3425 | 27.41 | 62.31
2021-01-23 02:45 | 0.65253 | 0.064465 | 0.054663 | 0.15348 | 13.3781 | 25.3641 | 1.3813 | 0.16809 | 331.2448 | 27.42 | 62.62
2021-01-23 02:50 | 0.76762 | 0.087775 | 0.069374 | 0.20392 | 8.5666 | 14.7076 | 1.3812 | 0.19 | 332.1255 | 27.42 | 62.48
2021-01-23 02:55 | 1.1384 | 0.067189 | 0.065157 | 0.16815 | 14.0805 | 11.993 | 1.3809 | 0.17535 | 331.7011 | 27.39 | 62.07
2021-01-23 03:00 | 0.65231 | 0.056217 | 0.056747 | 0.14292 | 17.395 | 25.7651 | 1.3662 | 0.16073 | 333.3307 | 27.35 | 62.07
2021-01-23 03:05 | 0.6779 | 0.056217 | 0.056747 | 0.14082 | 13.4762 | 21.7543 | 1.3516 | 0.14612 | 332.3483 | 27.29 | 62.32
2021-01-23 03:10 | -0.076721 | 0.061684 | 0.056731 | 0.15128 | 15.6102 | 4.5112 | 1.3366 | 0.15338 | 331.9907 | 27.23 | 61.74
2021-01-23 03:15 | -0.025578 | 0.15081 | 0.060943 | 0.2921 | 19.3163 | 20.9942 | 1.3295 | 0.13149 | 332.4603 | 27.23 | 62.17
2021-01-23 03:20 | -0.11513 | 0.13027 | 0.084077 | 0.28376 | 20.2826 | 22.0939 | 1.3225 | 0.13883 | 331.3516 | 27.22 | 62.81
2021-01-23 03:25 | 0.23023 | 0.10832 | 0.084071 | 0.25011 | 16.8122 | 8.2782 | 1.3151 | 0.10229 | 332.4323 | 27.21 | 62.65
2021-01-23 03:30 | -0.24304 | 0.075418 | 0.07777 | 0.19337 | 18.0104 | 6.5697 | 1.3006 | 0.094984 | 332.9602 | 27.19 | 62.86
2021-01-23 03:35 | 0.1919 | 0.12069 | 0.08619 | 0.27118 | 21.8815 | 37.0287 | 1.308 | 0.1023 | 331.8573 | 27.2 | 63.2
2021-01-23 03:40 | 0.33267 | 0.18791 | 0.075689 | 0.36373 | 20.2059 | 17.5855 | 1.3082 | 0.095011 | 331.7772 | 27.23 | 63.47
2021-01-23 03:45 | -0.038388 | 0.15226 | 0.096722 | 0.33012 | 24.0465 | -0.30711 | 1.2937 | 0.080401 | 331.7381 | 27.24 | 63.66
2021-01-23 03:50 | 0.38394 | 0.17149 | 0.11566 | 0.38063 | 22.1147 | 25.3295 | 1.2939 | 0.087721 | 331.683 | 27.25 | 63.98
2021-01-23 03:55 | 0.31997 | 0.15092 | 0.10305 | 0.33229 | 14.3141 | 21.1537 | 1.2867 | 0.073106 | 331.1264 | 27.26 | 64.13
2021-01-23 04:00 | 0.56318 | 0.12623 | 0.094645 | 0.28814 | 18.9536 | 24.5854 | 1.2941 | 0.0658 | 332.1715 | 27.24 | 64.38
2021-01-23 04:05 | 0.40956 | 0.14406 | 0.084124 | 0.30495 | 20.6726 | 3.4813 | 1.3013 | 0.073107 | 331.7132 | 27.2 | 64.37
2021-01-23 04:10 | 0.256 | 0.16328 | 0.094647 | 0.34494 | 12.6155 | 19.169 | 1.3014 | 0.080424 | 332.5646 | 27.18 | 64.73
2021-01-23 04:15 | 0.5376 | 0.27031 | 0.082028 | 0.49638 | 14.7456 | 18.0019 | 1.3087 | 0.11698 | 332.0272 | 27.19 | 64.72
2021-01-23 04:20 | 1.8941 | 0.31692 | 0.086221 | 0.5699 | 23.9372 | 13.9958 | 1.3012 | 0.095032 | 332.0358 | 27.23 | 64.14
2021-01-23 04:25 | 1.1007 | 0.25656 | 0.11356 | 0.50683 | 20.7128 | 30.4703 | 1.3013 | 0.10966 | 331.4804 | 27.25 | 64.15
2021-01-23 04:30 | 0.66558 | 0.23052 | 0.10937 | 0.46482 | 18.9026 | 23.4592 | 1.3014 | 0.095045 | 332.4914 | 27.25 | 64.43
2021-01-23 04:35 | 0.14077 | 0.31142 | 0.1451 | 0.62245 | 25.5541 | 29.9769 | 1.3158 | 0.13889 | 333.0592 | 27.26 | 63.94
2021-01-23 04:40 | 0.14078 | 0.2785 | 0.14721 | 0.57411 | 40.1343 | 18.7362 | 1.3012 | 0.087722 | 331.9367 | 27.32 | 63.8
2021-01-23 04:45 | 0.35836 | 0.21815 | 0.12829 | 0.46267 | 31.9759 | 31.7814 | 1.3013 | 0.095037 | 332.9875 | 27.3 | 64.01
2021-01-23 04:50 | 0.23033 | 0.33059 | 0.15349 | 0.66233 | 33.0341 | 35.0508 | 1.3083 | 0.10964 | 332.053 | 27.26 | 63.62
2021-01-23 04:55 | 1.1132 | 0.40876 | 0.1661 | 0.79477 | 36.1242 | 30.9037 | 1.3156 | 0.16079 | 332.044 | 27.28 | 63.44
2021-01-23 05:00 | 1.587 | 0.64895 | 0.14511 | 1.1399 | 29.9689 | 13.2695 | 1.3305 | 0.19007 | 331.3884 | 27.33 | 63.88
2021-01-23 05:05 | 1.958 | 0.79844 | 0.15772 | 1.3795 | 32.5977 | 36.1708 | 1.3377 | 0.20468 | 331.8931 | 27.37 | 63.52
2021-01-23 05:10 | 1.8171 | 0.78055 | 0.18504 | 1.3815 | 42.3824 | 37.2843 | 1.3303 | 0.19005 | 332.3822 | 27.42 | 63.16
2021-01-23 05:15 | 1.5229 | 0.87803 | 0.22712 | 1.5751 | 36.8882 | 19.8109 | 1.3158 | 0.19006 | 331.7977 | 27.45 | 63.28
2021-01-23 05:20 | 1.9067 | 0.70509 | 0.21448 | 1.2953 | 39.3207 | 39.9247 | 1.323 | 0.18273 | 331.822 | 27.46 | 62.96
2021-01-23 05:25 | 1.6251 | 0.70095 | 0.17872 | 1.2532 | 47.0073 | 44.1308 | 1.3229 | 0.21196 | 332.8332 | 27.5 | 62.73
2021-01-23 05:30 | 2.9687 | 0.98902 | 0.21237 | 1.7284 | 56.0365 | 70.6138 | 1.3229 | 0.27775 | 332.6091 | 27.53 | 62.7
2021-01-23 05:35 | 1.9705 | 1.5144 | 0.24811 | 2.5694 | 72.2603 | 78.6786 | 1.3302 | 0.29236 | 331.5045 | 27.59 | 62.42
2021-01-23 05:40 | 2.4823 | 1.2866 | 0.28594 | 2.2581 | 97.121 | 90.447 | 1.3375 | 0.29965 | 331.9858 | 27.64 | 62.13
2021-01-23 05:45 | 2.2775 | 1.0575 | 0.30486 | 1.9259 | 95.5523 | 83.7708 | 1.3374 | 0.24849 | 331.439 | 27.67 | 61.95
2021-01-23 05:50 | 2.0472 | 0.94092 | 0.33429 | 1.7766 | 82.654 | 60.5652 | 1.3374 | 0.2631 | 330.8872 | 27.7 | 61.81
2021-01-23 05:55 | 1.676 | 0.98474 | 0.31744 | 1.8248 | 82.5151 | 66.0673 | 1.33 | 0.21924 | 333.5026 | 27.72 | 61.55
2021-01-23 06:00 | 1.6249 | 1.1343 | 0.36371 | 2.1024 | 84.3399 | 67.9734 | 1.3301 | 0.21924 | 331.9007 | 27.74 | 61.57
2021-01-23 06:05 | 1.6376 | 1.1452 | 0.34057 | 2.096 | 83.1398 | 78.0632 | 1.3446 | 0.21924 | 330.3206 | 27.76 | 61.42
2021-01-23 06:10 | 2.3542 | 1.026 | 0.32588 | 1.8985 | 84.1587 | 64.7107 | 1.352 | 0.20463 | 331.8224 | 27.8 | 61.45
2021-01-23 06:15 | 2.751 | 1.0589 | 0.31538 | 1.9385 | 91.2253 | 69.4631 | 1.3521 | 0.24119 | 331.7861 | 27.82 | 61.49
2021-01-23 06:20 | 1.9063 | 0.86956 | 0.267 | 1.5978 | 78.7514 | 66.3358 | 1.3301 | 0.24848 | 331.6111 | 27.83 | 61.31
2021-01-23 06:25 | 2.5972 | 0.82017 | 0.25648 | 1.5158 | 68.9038 | 46.8366 | 1.3301 | 0.2777 | 332.1615 | 27.81 | 61.34
2021-01-23 06:30 | 1.8937 | 0.89022 | 0.27333 | 1.6379 | 71.6549 | 66.9973 | 1.3229 | 0.25581 | 331.5792 | 27.83 | 61.56
2021-01-23 06:35 | 3.5062 | 1.1056 | 0.29648 | 1.9912 | 77.4119 | 81.7626 | 1.3157 | 0.3143 | 332.062 | 27.85 | 61.63
2021-01-23 06:40 | 3.1602 | 1.0684 | 0.30274 | 1.9405 | 93.0103 | 66.2444 | 1.3301 | 0.38002 | 332.0753 | 27.88 | 61.16
2021-01-23 06:45 | 4.12 | 1.1741 | 0.33009 | 2.1298 | 100.4573 | 91.5518 | 1.3448 | 0.4239 | 334.1148 | 27.91 | 61.2
2021-01-23 06:50 | 4.4533 | 1.1702 | 0.29859 | 2.0943 | 92.8836 | 82.8715 | 1.3449 | 0.45319 | 332.4173 | 27.99 | 61.23
2021-01-23 06:55 | 4.3249 | 1.0082 | 0.31539 | 1.8608 | 88.2186 | 52.9434 | 1.3448 | 0.52624 | 331.833 | 28.07 | 60.74
2021-01-23 07:00 | 3.4679 | 0.915 | 0.27967 | 1.6843 | 83.578 | 60.6974 | 1.3376 | 0.65785 | 332.2293 | 28.16 | 60.63
2021-01-23 07:05 | 3.5065 | 1.0852 | 0.35118 | 2.0146 | 79.672 | 68.7276 | 1.3304 | 0.70906 | 331.6212 | 28.22 | 60.57
2021-01-23 07:10 | 3.3526 | 1.1536 | 0.35955 | 2.1279 | 84.8435 | 75.794 | 1.323 | 0.53357 | 331.6124 | 28.26 | 60.16
2021-01-23 07:15 | 3.5448 | 1.151 | 0.33855 | 2.1028 | 85.8422 | 52.4369 | 1.3011 | 0.39472 | 332.5904 | 28.3 | 60.19
2021-01-23 07:20 | 4.0574 | 1.0332 | 0.28183 | 1.8655 | 74.8913 | 55.4978 | 1.2794 | 0.35093 | 331.4639 | 28.32 | 60.58
2021-01-23 07:25 | 4.9268 | 1.0988 | 0.28598 | 1.9703 | 61.5892 | 52.3037 | 1.2865 | 0.38741 | 331.5138 | 28.33 | 60.08
2021-01-23 07:30 | 3.4169 | 1.1016 | 0.31122 | 1.9998 | 72.4016 | 48.4862 | 1.2938 | 0.33625 | 331.4517 | 28.38 | 59.96
2021-01-23 07:35 | 3.2639 | 1.095 | 0.32811 | 2.0065 | 80.5666 | 69.2209 | 1.2941 | 0.29976 | 331.8651 | 28.42 | 60.31
2021-01-23 07:40 | 2.4708 | 1.076 | 0.31975 | 1.9669 | 77.7347 | 71.4258 | 1.309 | 0.24863 | 331.7473 | 28.47 | 60.61
2021-01-23 07:45 | 4.1084 | 1.0633 | 0.28602 | 1.9159 | 83.3248 | 59.8776 | 1.3159 | 0.33629 | 332.3357 | 28.49 | 59.87
2021-01-23 07:50 | 4.7744 | 0.89602 | 0.28184 | 1.6574 | 95.8159 | 80.2511 | 1.316 | 0.43137 | 330.704 | 28.52 | 60.02
2021-01-23 07:55 | 5.5542 | 1.007 | 0.34277 | 1.8863 | 86.8399 | 81.3727 | 1.3158 | 0.48246 | 331.2647 | 28.54 | 59.49
2021-01-23 08:00 | 5.0806 | 0.9905 | 0.30071 | 1.819 | 94.117 | 65.3792 | 1.2938 | 0.39473 | 331.7391 | 28.59 | 59.26
2021-01-23 08:05 | 5.1963 | 0.97688 | 0.31757 | 1.8171 | 89.1609 | 64.1164 | 1.2867 | 0.30705 | 331.1393 | 28.63 | 59.38
2021-01-23 08:10 | 6.9607 | 0.96154 | 0.31959 | 1.7935 | 72.5549 | 56.7193 | 1.279 | 0.32889 | 331.736 | 28.64 | 58.7
2021-01-23 08:15 | 4.7981 | 1.0342 | 0.33009 | 1.9153 | 48.0989 | 41.5581 | 1.2717 | 0.40928 | 331.1919 | 28.67 | 58.52
2021-01-23 08:20 | 5.297 | 1.1247 | 0.35531 | 2.0793 | 42.8877 | 48.3536 | 1.2716 | 0.45312 | 331.1667 | 28.7 | 58.36
2021-01-23 08:25 | 4.068 | 1.2013 | 0.33422 | 2.1756 | 52.3974 | 49.1021 | 1.2787 | 0.38727 | 331.504 | 28.75 | 57.8
2021-01-23 08:30 | 4.5416 | 1.2754 | 0.35527 | 2.3082 | 62.3801 | 33.4979 | 1.2788 | 0.37999 | 330.5496 | 28.82 | 57.69
2021-01-23 08:35 | 5.7696 | 1.3714 | 0.40361 | 2.5078 | 65.5709 | 69.5827 | 1.2861 | 0.35806 | 331.5715 | 28.85 | 57.5
2021-01-23 08:40 | 5.0139 | 1.3615 | 0.31526 | 2.4023 | 85.4304 | 81.9821 | 1.2785 | 0.34338 | 330.8648 | 28.9 | 56.95
2021-01-23 08:45 | 4.7197 | 1.5851 | 0.37201 | 2.8037 | 91.6015 | 60.7607 | 1.2639 | 0.34338 | 330.8394 | 28.92 | 56.91
2021-01-23 08:50 | 5.7806 | 1.4834 | 0.34674 | 2.6205 | 83.9156 | 70.0422 | 1.2492 | 0.40178 | 330.874 | 28.93 | 56.54
2021-01-23 08:55 | 4.8863 | 1.2533 | 0.37203 | 2.2932 | 87.0228 | 66.6383 | 1.2494 | 0.38724 | 329.868 | 29.01 | 56.71
2021-01-23 09:00 | 5.2441 | 1.2231 | 0.3657 | 2.2404 | 91.8252 | 58.5496 | 1.2493 | 0.35068 | 330.8922 | 29.05 | 56.39
2021-01-23 09:05 | 4.4116 | 1.2351 | 0.38242 | 2.2756 | 83.0867 | 68.1819 | 1.2417 | 0.39442 | 329.7076 | 29.08 | 55.75
2021-01-23 09:10 | 3.9382 | 1.1171 | 0.33827 | 2.0506 | 83.4485 | 71.1225 | 1.2416 | 0.32866 | 331.455 | 29.11 | 55.41
2021-01-23 09:15 | 4.8078 | 1.198 | 0.35509 | 2.1915 | 81.9985 | 58.7881 | 1.2562 | 0.37249 | 331.4342 | 29.12 | 55.45
2021-01-23 09:20 | 5.1268 | 1.2116 | 0.35294 | 2.2101 | 84.3308 | 61.9619 | 1.2707 | 0.38705 | 329.6976 | 29.14 | 55.15
2021-01-23 09:25 | 5.5489 | 1.2198 | 0.36136 | 2.2312 | 87.5548 | 69.6143 | 1.2707 | 0.46009 | 332.2429 | 29.19 | 55.05
2021-01-23 09:30 | 5.4964 | 1.2881 | 0.30876 | 2.2831 | 81.7562 | 60.4249 | 1.2412 | 0.51109 | 330.2249 | 29.2 | 54.44
2021-01-23 09:35 | 4.716 | 1.2015 | 0.29611 | 2.1379 | 74.74 | 54.6491 | 1.2337 | 0.45991 | 330.2645 | 29.21 | 54.04
2021-01-23 09:40 | 4.1914 | 1.0808 | 0.30027 | 1.957 | 64.0166 | 32.8671 | 1.2263 | 0.38686 | 331.8614 | 29.22 | 53.7
2021-01-23 09:45 | 3.1431 | 0.98479 | 0.32332 | 1.8349 | 52.1393 | 40.2314 | 1.2042 | 0.29922 | 331.893 | 29.24 | 53.25
2021-01-23 09:50 | 4.2539 | 1.2311 | 0.35685 | 2.244 | 59.9692 | 51.0269 | 1.2113 | 0.35025 | 330.8823 | 29.26 | 52.79
2021-01-23 09:55 | 5.6079 | 1.1626 | 0.36524 | 2.1473 | 63.6771 | 41.4499 | 1.2185 | 0.38672 | 330.3261 | 29.3 | 52.6
2021-01-23 10:00 | 6.4639 | 1.2818 | 0.38413 | 2.3489 | 66.3657 | 55.5432 | 1.2404 | 0.4378 | 332.8759 | 29.35 | 52.48
2021-01-23 10:05 | 4.5858 | 1.1955 | 0.34634 | 2.1788 | 77.6755 | 60.303 | 1.2404 | 0.43779 | 330.7589 | 29.39 | 52.26
2021-01-23 10:10 | 4.1641 | 1.2255 | 0.37151 | 2.2501 | 69.0789 | 38.9029 | 1.2549 | 0.39399 | 331.7805 | 29.42 | 52.09
2021-01-23 10:15 | 3.7301 | 1.227 | 0.43451 | 2.3174 | 71.3108 | 65.9149 | 1.2477 | 0.35024 | 331.2065 | 29.45 | 52.14
2021-01-23 10:20 | 3.5005 | 1.4298 | 0.34429 | 2.536 | 76.7565 | 66.2498 | 1.2479 | 0.32109 | 331.1126 | 29.5 | 52.27
2021-01-23 10:25 | 3.3088 | 1.2394 | 0.36946 | 2.2693 | 78.1334 | 41.1056 | 1.2478 | 0.34297 | 331.1033 | 29.52 | 52.12
2021-01-23 10:30 | 5.263 | 1.3393 | 0.40931 | 2.4622 | 81.2948 | 74.0799 | 1.2696 | 0.48158 | 331.2768 | 29.56 | 51.75
2021-01-23 10:35 | 4.0749 | 0.99827 | 0.35683 | 1.887 | 81.8248 | 46.5993 | 1.2623 | 0.50346 | 329.6763 | 29.6 | 51.59
2021-01-23 10:40 | 4.2291 | 1.1683 | 0.36741 | 2.1583 | 68.7188 | 44.8722 | 1.2626 | 0.47438 | 329.526 | 29.67 | 51.91
2021-01-23 10:45 | 4.4747 | 1.5131 | 0.44117 | 2.7605 | 65.8682 | 64.2726 | 1.2561 | 0.43086 | 329.2507 | 29.73 | 53.22
2021-01-23 10:50 | 3.72 | 1.6609 | 0.50623 | 3.0521 | 87.2949 | 59.2942 | 1.2632 | 0.37239 | 330.2677 | 29.79 | 52.74
2021-01-23 10:55 | 4.5143 | 1.5683 | 0.48752 | 2.8894 | 92.393 | 74.1313 | 1.2637 | 0.40176 | 328.4926 | 29.87 | 53.4
2021-01-23 11:00 | 5.7188 | 1.318 | 0.49614 | 2.5164 | 96.3627 | 72.3821 | 1.2569 | 0.43116 | 329.3264 | 29.93 | 54.2
2021-01-23 11:05 | 5.3482 | 1.2372 | 0.41207 | 2.3085 | 79.0813 | 35.4668 | 1.257 | 0.43119 | 329.8009 | 29.95 | 54.3
2021-01-23 11:10 | 4.9884 | 1.3314 | 0.4729 | 2.5137 | 75.9972 | 67.6167 | 1.2566 | 0.40914 | 329.871 | 29.98 | 53.49
2021-01-23 11:15 | 4.9247 | 1.3328 | 0.47503 | 2.516 | 77.3114 | 50.9611 | 1.2567 | 0.43839 | 328.7696 | 30.02 | 53.5
2021-01-23 11:20 | 6.1787 | 1.2013 | 0.39939 | 2.2408 | 73.1005 | 44.3843 | 1.2568 | 0.51149 | 329.2332 | 30.05 | 53.57
2021-01-23 11:25 | 6.5256 | 1.288 | 0.46676 | 2.441 | 80.14 | 71.5824 | 1.2717 | 0.55546 | 329.1115 | 30.09 | 53.99
2021-01-23 11:30 | 6.7942 | 1.2893 | 0.44783 | 2.4242 | 89.4229 | 49.5736 | 1.279 | 0.50429 | 329.5924 | 30.13 | 53.83
2021-01-23 11:35 | 5.976 | 1.2072 | 0.4605 | 2.3109 | 88.5323 | 72.8795 | 1.2718 | 0.3874 | 330.0297 | 30.17 | 53.97
2021-01-23 11:40 | 7.3587 | 1.5077 | 0.429 | 2.7401 | 103.2629 | 71.9441 | 1.2793 | 0.48247 | 328.919 | 30.21 | 54.05
2021-01-23 11:45 | 6.207 | 1.7286 | 0.38484 | 3.0325 | 94.2541 | 63.0374 | 1.272 | 0.46054 | 328.3753 | 30.23 | 54.01
2021-01-23 11:50 | 4.6837 | 1.5557 | 0.3722 | 2.7568 | 85.9858 | 67.3533 | 1.25 | 0.38741 | 328.3876 | 30.24 | 53.82
2021-01-23 11:55 | 4.9291 | 1.2558 | 0.38499 | 2.3099 | 86.6292 | 48.3948 | 1.2578 | 0.3949 | 328.7568 | 30.24 | 54.85
2021-01-23 12:00 | 5.5167 | 1.497 | 0.47744 | 2.7721 | 91.2775 | 81.7852 | 1.2648 | 0.41674 | 328.8257 | 30.25 | 54.27
2021-01-23 12:05 | 4.7366 | 1.5041 | 0.49223 | 2.7977 | 90.2976 | 47.407 | 1.265 | 0.39486 | 330.3002 | 30.28 | 54.51
2021-01-23 12:10 | 4.5985 | 1.5242 | 0.50094 | 2.8373 | 83.1882 | 55.7047 | 1.2658 | 0.44631 | 329.0248 | 30.32 | 55.72
2021-01-23 12:15 | 4.6489 | 1.3537 | 0.43772 | 2.5127 | 75.3866 | 63.3276 | 1.2655 | 0.35113 | 329.0625 | 30.34 | 55.25
2021-01-23 12:20 | 6.3786 | 1.4719 | 0.45882 | 2.7171 | 76.0714 | 55.0247 | 1.2511 | 0.38776 | 328.4746 | 30.37 | 55.41
2021-01-23 12:25 | 4.69 | 1.2885 | 0.41271 | 2.3878 | 81.7141 | 14.1777 | 1.2224 | 0.3367 | 328.8083 | 30.4 | 56.35
2021-01-23 12:30 | 5.0876 | 1.2213 | 0.42326 | 2.2953 | 63.5628 |  | 1.2151 | 0.39528 | 328.7878 | 30.4 | 56.49
2021-01-23 12:35 | 5.7542 | 1.3876 | 0.45697 | 2.5839 | 45.8802 | 49.6531 | 1.2152 | 0.44654 | 327.9143 | 30.41 | 56.51
2021-01-23 12:40 | 6.9719 | 1.5044 | 0.44014 | 2.7461 | 67.1965 | 79.2333 | 1.2079 | 0.46119 | 328.4145 | 30.42 | 56.52
2021-01-23 12:45 | 7.1266 | 1.4441 | 0.42545 | 2.6391 | 88.4627 | 50.1429 | 1.2154 | 0.4759 | 328.3257 | 30.46 | 56.7
2021-01-23 12:50 | 7.3831 | 1.2532 | 0.40019 | 2.3211 | 89.3566 | 59.0652 | 1.2081 | 0.48323 | 327.7916 | 30.47 | 56.71
2021-01-23 12:55 | 6.0893 | 1.3152 | 0.40234 | 2.4183 | 76.4556 | 36.7766 | 1.2009 | 0.454 | 327.235 | 30.47 | 56.98
2021-01-23 13:00 | 5.9877 | 1.4872 | 0.45929 | 2.7389 | 82.9301 | 64.5491 | 1.2011 | 0.48336 | 326.6541 | 30.48 | 57.31
2021-01-23 13:05 | 6.8991 | 1.2826 | 0.47201 | 2.438 | 86.8513 | 55.3362 | 1.2013 | 0.60063 | 327.6056 | 30.51 | 57.55
2021-01-23 13:10 | 6.6563 | 1.236 | 0.42992 | 2.3245 | 90.2895 | 53.5581 | 1.2014 | 0.59339 | 327.014 | 30.54 | 57.74
2021-01-23 13:15 | 6.2205 | 1.0271 | 0.37303 | 1.9474 | 82.1772 | 44.6747 | 1.2015 | 0.57143 | 327.5061 | 30.55 | 57.8
2021-01-23 13:20 | 4.2838 | 0.88269 | 0.37303 | 1.726 | 77.6925 | 36.9891 | 1.1941 | 0.60073 | 328.0369 | 30.54 | 57.81
2021-01-23 13:25 | 4.5664 | 1.0492 | 0.4363 | 2.0445 | 72.5697 | 42.5033 | 1.2236 | 0.56416 | 328.5307 | 30.53 | 58.07
2021-01-23 13:30 | 4.3871 | 1.1964 | 0.46584 | 2.2997 | 76.3207 | 40.2385 | 1.2456 | 0.51291 | 327.4627 | 30.54 | 58.2
2021-01-23 13:35 | 4.8236 | 1.2473 | 0.47852 | 2.3905 | 82.1143 | 62.0707 | 1.2531 | 0.46898 | 327.4293 | 30.55 | 58.32
2021-01-23 13:40 | 3.8744 |  | 0.39421 | 1.9352 | 83.79 | 34.1256 |  |  | 328.4406 | 30.56 | 58.36
2021-01-23 13:45 | 4.2465 | 0.99159 | 0.3626 | 1.8825 | 85.9565 | 59.4357 | 1.2531 | 0.39572 | 327.3935 | 30.57 | 58.35
2021-01-23 13:50 | 4.8621 | 1.1222 | 0.39631 | 2.1165 | 79.7849 | 41.5345 | 1.2457 | 0.46898 | 326.8904 | 30.57 | 58.26
2021-01-23 13:55 | 6.0553 | 1.0947 | 0.40897 | 2.0849 | 86.4883 | 49.8588 | 1.2531 | 0.60089 | 326.8732 | 30.58 | 58.27
2021-01-23 14:00 | 6.8 | 1.2998 | 0.46382 | 2.4582 | 94.3893 | 64.4898 | 1.2679 | 0.63759 | 327.36 | 30.58 | 58.47
2021-01-23 14:05 | 6.4411 | 1.403 | 0.4554 | 2.6059 | 95.5843 | 58.6316 | 1.2752 | 0.6083 | 327.3128 | 30.61 | 58.47
2021-01-23 14:10 | 5.2088 | 1.2268 | 0.41531 | 2.2958 | 96.4994 | 66.9809 | 1.2605 | 0.4397 | 327.8588 | 30.61 | 58.27
2021-01-23 14:15 | 3.4638 | 1.0342 | 0.38156 | 1.9647 | 89.659 | 35.0487 | 1.2457 | 0.35907 | 327.8653 | 30.62 | 58.12
2021-01-23 14:20 | 3.3995 | 1.0355 | 0.34992 | 1.9372 | 82.7992 | 46.4796 | 1.2384 | 0.32241 | 328.3867 | 30.63 | 57.98
2021-01-23 14:25 | 3.1812 | 0.96121 | 0.37098 | 1.8422 | 74.2563 | 35.8762 | 1.231 | 0.30041 | 327.3733 | 30.63 | 57.85
2021-01-23 14:30 | 3.3736 | 0.94469 | 0.4047 | 1.8528 | 62.5466 | 47.677 | 1.2309 | 0.30041 | 327.3875 | 30.62 | 57.86
2021-01-23 14:35 | 3.3863 | 0.99692 | 0.40258 | 1.9307 | 65.818 | 37.4549 | 1.2382 | 0.35169 | 327.9255 | 30.61 | 57.82
2021-01-23 14:40 | 3.9381 | 1.1551 | 0.47005 | 2.2428 | 78.0239 | 44.179 | 1.2456 | 0.41765 | 328.4001 | 30.63 | 57.89
2021-01-23 14:45 | 3.9123 | 1.1234 | 0.46582 | 2.1879 | 85.2342 | 71.3193 | 1.2529 | 0.36634 | 327.8776 | 30.65 | 57.72
2021-01-23 14:50 | 3.6296 | 0.9363 | 0.39831 | 1.8335 | 90.3732 | 49.9577 | 1.2454 | 0.34432 | 327.9334 | 30.64 | 57.45
2021-01-23 14:55 | 2.9239 | 0.8922 | 0.40038 | 1.768 | 81.8072 | 51.4809 | 1.2306 | 0.28568 | 326.9361 | 30.64 | 57.21
2021-01-23 15:00 | 3.2446 | 0.92249 | 0.373 | 1.787 | 77.5938 | 25.5773 | 1.238 | 0.33697 | 328.1319 | 30.65 | 57.21
2021-01-23 15:05 | 3.5779 | 0.89357 | 0.37087 | 1.7406 | 76.0103 | 49.3364 | 1.2233 | 0.27835 | 328.674 | 30.64 | 57.14
2021-01-23 15:10 | 3.0776 | 0.82892 | 0.37507 | 1.6436 | 78.8074 | 44.5228 | 1.2013 | 0.29299 | 327.6569 | 30.64 | 57.04
2021-01-23 15:15 | 2.911 | 0.81245 | 0.3498 | 1.5952 | 79.5587 | 53.7983 | 1.1866 | 0.28567 | 327.6688 | 30.62 | 57.17
2021-01-23 15:20 | 2.7958 | 0.85789 | 0.35193 | 1.6648 | 80.0271 | 41.2447 | 1.1794 | 0.27837 | 327.6197 | 30.64 | 57.29
2021-01-23 15:25 | 2.5136 | 0.86063 | 0.34771 | 1.6669 | 79.9439 | 32.5644 | 1.1794 | 0.26372 | 327.6242 | 30.64 | 57.26
2021-01-23 15:30 | 3.1038 | 0.94042 | 0.38778 | 1.8314 | 78.8201 | 52.3791 | 1.1795 | 0.26373 | 328.1096 | 30.65 | 57.36
2021-01-23 15:35 | 3.668 | 1.0009 | 0.35616 | 1.8925 | 82.3175 | 38.0242 | 1.1794 | 0.28571 | 328.1043 | 30.66 | 57.29
2021-01-23 15:40 | 3.8732 | 1.1618 | 0.37302 | 2.1538 | 67.7685 | 51.1881 | 1.1868 | 0.32233 | 327.0725 | 30.66 | 57.29
2021-01-23 15:45 | 3.9889 | 1.1494 | 0.36039 | 2.1223 | 58.5271 | 24.164 | 1.1795 | 0.34433 | 328.5926 | 30.67 | 57.37
2021-01-23 15:50 | 4.7071 | 1.0587 | 0.36461 | 1.9874 | 55.7568 | 56.2082 | 1.1868 | 0.35898 | 328.5813 | 30.68 | 57.34
2021-01-23 15:55 | 4.1807 | 0.83861 | 0.33506 | 1.6205 | 61.3308 | 46.9164 | 1.1867 | 0.30766 | 328.1393 | 30.65 | 57.16
2021-01-23 16:00 | 3.783 | 0.80145 | 0.29501 | 1.5235 | 58.6914 | 57.7168 | 1.1866 | 0.30765 | 328.1654 | 30.64 | 57.09
2021-01-23 16:05 | 3.4493 | 0.72441 | 0.29498 | 1.4054 | 53.1785 | 30.2309 | 1.1939 | 0.41016 | 326.6412 | 30.64 | 56.93
2021-01-23 16:10 | 3.6286 | 0.82057 | 0.29707 | 1.557 | 39.1422 | 37.4805 | 1.2231 | 0.38816 | 327.1936 | 30.63 | 56.79
2021-01-23 16:15 | 3.7048 | 0.88638 | 0.36863 | 1.7273 | 27.4846 | 30.8894 | 1.2521 | 0.33683 | 327.7609 | 30.64 | 56.34
2021-01-23 16:20 | 4.6403 | 1.0526 | 0.37493 | 1.9884 | 33.0412 | 36.5278 | 1.2521 | 0.3661 | 327.253 | 30.65 | 56.18
2021-01-23 16:25 | 4.5759 | 1.0539 | 0.31803 | 1.9356 | 46.8404 | 65.0105 | 1.252 | 0.38071 | 327.7959 | 30.65 | 56
2021-01-23 16:30 | 4.2295 | 1.047 | 0.3496 | 1.9544 | 62.351 | 48.4883 | 1.2592 | 0.41729 | 326.8048 | 30.63 | 55.93
2021-01-23 16:35 | 5.0883 | 1.0593 | 0.35382 | 1.9776 | 61.7469 | 68.5143 | 1.2592 | 0.37337 | 326.7893 | 30.64 | 55.93
2021-01-23 16:40 | 5.2934 | 1.036 | 0.34118 | 1.9271 | 56.8045 | 32.6985 | 1.2519 | 0.29284 | 327.8122 | 30.65 | 55.89
2021-01-23 16:45 | 4.9855 | 1.0428 | 0.3917 | 1.9901 | 46.6711 | 42.775 | 1.2445 | 0.30746 | 328.3383 | 30.66 | 55.72
2021-01-23 16:50 | 4.383 | 1.0208 | 0.39591 | 1.9606 | 35.5765 | 33.1671 | 1.2445 | 0.30013 | 327.3147 | 30.66 | 55.66
2021-01-23 16:55 | 3.5372 | 1.1362 | 0.38959 | 2.1312 | 36.9609 | 42.2718 | 1.2518 | 0.26354 | 328.3442 | 30.66 | 55.68
2021-01-23 17:00 | 4.0374 | 1.0662 | 0.36015 | 1.9945 | 45.0858 | 64.4552 | 1.3105 | 0.46856 | 327.2554 | 30.68 | 55.85
2021-01-23 17:05 | 4.1396 | 0.94798 | 0.36222 | 1.8153 | 95.7107 | 125.0955 | 1.3836 | 0.71742 | 327.6338 | 30.66 | 55.78
2021-01-23 17:10 | 3.4476 | 0.82159 | 0.3896 | 1.649 | 142.4547 | 134.1088 | 1.3397 | 0.44656 | 327.1361 | 30.64 | 55.86
2021-01-23 17:15 | 3.2554 | 0.83672 | 0.37908 | 1.6616 | 95.5393 | 32.2258 | 1.2738 | 0.32211 | 329.4145 | 30.61 | 55.95
2021-01-23 17:20 | 3.5633 | 0.95221 | 0.42123 | 1.8787 | 80.1658 | 64.7232 | 1.2812 | 0.32214 | 328.3454 | 30.62 | 56.09
2021-01-23 17:25 | 2.1147 | 0.72407 | 0.37698 | 1.4869 | 78.7456 | 45.5555 | 1.2519 | 0.22695 | 328.3885 | 30.6 | 56.01
2021-01-23 17:30 | 2.6012 | 0.70879 | 0.37268 | 1.4613 | 61.3317 | 29.5331 | 1.2589 | 0.27081 | 328.3303 | 30.55 | 55.72
2021-01-23 17:35 | 4.6643 | 0.75277 | 0.33269 | 1.4887 | 42.4299 | 31.2253 | 1.2736 | 0.35133 | 329.0258 | 30.55 | 55.72
2021-01-23 17:40 | 5.8812 | 0.78293 | 0.31792 | 1.518 | 41.0328 | 31.0591 | 1.2735 | 0.38058 | 328.0053 | 30.56 | 55.53
2021-01-23 17:45 | 4.0225 | 0.77179 | 0.30944 | 1.4925 | 28.6033 | 23.3459 | 1.2586 | 0.27806 | 328.6217 | 30.53 | 55.17
2021-01-23 17:50 | 3.702 | 0.72506 | 0.2989 | 1.4103 | 30.4361 | 25.5171 | 1.2512 | 0.24878 | 328.6726 | 30.5 | 55.14
2021-01-23 17:55 | 3.4327 | 0.67007 | 0.29466 | 1.3218 | 28.5276 | 35.5161 | 1.2511 | 0.23412 | 328.2154 | 30.47 | 55.05
2021-01-23 18:00 | 3.1507 | 0.67415 | 0.29043 | 1.3238 | 28.8946 | 23.1465 | 1.2583 | 0.22679 | 327.7522 | 30.44 | 55
2021-01-23 18:05 | 3.7013 | 0.5986 | 0.27148 | 1.189 | 34.3949 | 24.436 | 1.2583 | 0.23409 | 328.8383 | 30.41 | 54.96
2021-01-23 18:10 | 4.1875 | 0.56696 | 0.26724 | 1.1363 | 42.2897 | 49.9322 | 1.2654 | 0.25601 | 328.3896 | 30.38 | 54.81
2021-01-23 18:15 | 3.7393 | 0.60127 | 0.26092 | 1.1826 | 35.8047 | 21.9233 | 1.2581 | 0.27064 | 328.402 | 30.37 | 54.83
2021-01-23 18:20 | 3.4194 | 0.67408 | 0.26094 | 1.2942 | 42.7333 | 46.4114 | 1.2655 | 0.29261 | 328.926 | 30.34 | 55.1
2021-01-23 18:25 | 3.3041 | 0.64387 | 0.27567 | 1.2626 | 43.9825 | 31.6678 | 1.2728 | 0.31455 | 327.8975 | 30.34 | 55.06
2021-01-23 18:30 | 2.766 | 0.59715 | 0.27144 | 1.1889 | 39.6051 | 21.8412 | 1.2727 | 0.27795 | 327.9525 | 30.31 | 55
2021-01-23 18:35 | 3.1501 | 0.51752 | 0.23356 | 1.0268 | 36.9304 | 35.0249 | 1.28 | 0.32183 | 329.5448 | 30.28 | 55.04
2021-01-23 18:40 | 3.534 | 0.42688 | 0.2125 | 0.86684 | 31.5189 | 24.7582 | 1.2799 | 0.34375 | 328.0521 | 30.25 | 54.95
2021-01-23 18:45 | 2.9322 | 0.42414 | 0.20619 | 0.85633 | 34.2131 | 40.0519 | 1.2799 | 0.25598 | 330.1411 | 30.23 | 55.03
2021-01-23 18:50 | 3.9306 | 0.49273 | 0.23353 | 0.9888 | 28.1673 | 15.2308 | 1.2871 | 0.2779 | 327.1049 | 30.19 | 54.98
2021-01-23 18:55 | 4.1737 | 0.46114 | 0.23141 | 0.93827 | 28.0634 | 28.8623 | 1.2871 | 0.26326 | 328.1891 | 30.16 | 54.96
2021-01-23 19:00 | 3.7511 | 0.51603 | 0.24613 | 1.0392 | 28.0426 | 38.7455 | 1.287 | 0.26326 | 329.2398 | 30.15 | 54.96
2021-01-23 19:05 | 2.4707 | 0.52148 | 0.25873 | 1.0581 | 25.777 | 12.0026 | 1.2869 | 0.24861 | 329.288 | 30.13 | 54.84
2021-01-23 19:10 | 2.0221 | 0.49938 | 0.2839 | 1.0494 | 23.5994 | 29.855 | 1.2793 | 0.19737 | 330.2718 | 30.09 | 54.39
2021-01-23 19:15 | 1.5739 | 0.47188 | 0.27545 | 0.99877 | 24.0467 | 28.2848 | 1.2791 | 0.18273 | 329.8297 | 30.06 | 54.18
2021-01-23 19:20 | 1.4458 | 0.40737 | 0.24388 | 0.86831 | 25.6306 | 18.9261 | 1.279 | 0.16809 | 330.4065 | 30.04 | 53.99
2021-01-23 19:25 | 1.1001 | 0.3963 | 0.23752 | 0.84499 | 22.9845 | 27.9682 | 1.2787 | 0.15344 | 329.4879 | 30 | 53.59
2021-01-23 19:30 | 1.8801 | 0.34414 | 0.20806 | 0.73557 | 21.6302 | 14.3246 | 1.2858 | 0.15342 | 329.5943 | 29.95 | 53.38
2021-01-23 19:35 | 1.7903 | 0.34821 | 0.19543 | 0.72917 | 24.277 | 16.5223 | 1.2783 | 0.1534 | 330.2017 | 29.91 | 53.19
2021-01-23 19:40 | 1.9437 | 0.46335 | 0.18912 | 0.89935 | 22.8133 | 34.4655 | 1.2856 | 0.1607 | 330.2556 | 29.87 | 53.24
2021-01-23 19:45 | 1.6623 | 0.41672 | 0.16809 | 0.80685 | 19.9479 | 9.6977 | 1.2782 | 0.15338 | 330.2933 | 29.85 | 53.19
2021-01-23 19:50 | 1.7263 | 0.46058 | 0.18911 | 0.8951 | 28.4897 | 16.7665 | 1.2709 | 0.1826 | 330.3263 | 29.82 | 53.28
2021-01-23 19:55 | 1.3669 | 0.41085 | 0.21202 | 0.84179 | 23.9458 | 33.2972 | 1.2697 | 0.16054 | 330.1478 | 29.79 | 51.2
2021-01-23 20:00 | 1.1747 | 0.4079 | 0.18673 | 0.81197 | 28.7649 | 8.846 | 1.269 | 0.15316 | 329.8101 | 29.78 | 50.02
2021-01-23 20:05 | 1.0466 | 0.3229 | 0.16568 | 0.65854 | 23.75 | 23.7704 | 1.2612 | 0.11665 | 329.9887 | 29.74 | 49.18
2021-01-23 20:10 | 1.4037 | 0.26265 | 0.15307 | 0.55566 | 19.5596 | 9.2081 | 1.261 | 0.12391 | 330.6211 | 29.7 | 48.81
2021-01-23 20:15 | 1.493 | 0.24212 | 0.15516 | 0.5263 | 20.7026 | 15.5474 | 1.261 | 0.1312 | 331.1901 | 29.66 | 48.89
2021-01-23 20:20 | 2.0417 | 0.31052 | 0.15726 | 0.63324 | 19.6615 | 21.2234 | 1.261 | 0.15307 | 330.6999 | 29.63 | 48.99
2021-01-23 20:25 | 1.8122 | 0.24899 | 0.15937 | 0.54312 | 21.7867 | 6.4421 | 1.2611 | 0.14579 | 331.7347 | 29.61 | 49.25
2021-01-23 20:30 | 1.7614 | 0.24219 | 0.18037 | 0.55161 | 26.3449 | 30.4702 | 1.2613 | 0.13853 | 331.53 | 29.57 | 49.84
2021-01-23 20:35 | 1.8002 | 0.37638 | 0.18252 | 0.75735 | 32.4904 | 30.468 | 1.2689 | 0.16044 | 332.5069 | 29.55 | 50.52
2021-01-23 20:40 | 1.06 | 0.25327 | 0.16578 | 0.554 | 28.3611 | 7.1516 | 1.262 | 0.1313 | 330.8904 | 29.52 | 51.22
2021-01-23 20:45 | 1.4049 | 0.32449 | 0.1637 | 0.6611 | 30.2648 | 30.7348 | 1.2621 | 0.12402 | 331.9603 | 29.46 | 51.67
2021-01-23 20:50 | 1.2389 | 0.29849 | 0.15951 | 0.61495 | 34.3227 | 20.988 | 1.2476 | 0.12403 | 330.9259 | 29.44 | 51.83
2021-01-23 20:55 | 0.74062 | 0.27514 | 0.15107 | 0.57282 | 30.391 | 21.7181 | 1.24 | 0.10941 | 331.5554 | 29.42 | 51.27
2021-01-23 21:00 | 1.3152 | 0.27513 | 0.14058 | 0.5623 | 20.6851 | 16.1191 | 1.2472 | 0.12399 | 332.1289 | 29.39 | 51.22
2021-01-23 21:05 | 1.7498 | 0.30807 | 0.14272 | 0.61494 | 25.5449 | 9.094 | 1.2403 | 0.13862 | 332.0177 | 29.4 | 51.91
2021-01-23 21:10 | 1.6094 | 0.29986 | 0.12593 | 0.58557 | 14.5916 | 8.8285 | 1.2403 | 0.16051 | 330.9997 | 29.37 | 52.06
2021-01-23 21:15 | 1.5594 | 0.24527 | 0.13232 | 0.50828 | 13.191 | 18.9173 | 1.2412 | 0.19713 | 331.3264 | 29.33 | 53.9
2021-01-23 21:20 | 1.5983 | 0.2577 | 0.12396 | 0.51897 | 13.0014 | -0.2455 | 1.2489 | 0.13147 | 332.8242 | 29.28 | 54.92
2021-01-23 21:25 | 1.2913 | 0.24396 | 0.10294 | 0.47899 | 21.0904 | 18.4617 | 1.2342 | 0.12415 | 330.3226 | 29.22 | 54.84
2021-01-23 21:30 | 1.4314 | 0.33293 | 0.13021 | 0.64054 | 26.8497 | 30.5101 | 1.2338 | 0.16061 | 331.0134 | 29.17 | 54.16
2021-01-23 21:35 | 1.1116 | 0.28079 | 0.14277 | 0.57318 | 17.9802 | 3.2812 | 1.2334 | 0.19706 | 331.6116 | 29.18 | 53.49
2021-01-23 21:40 | 1.4692 | 0.24105 | 0.13646 | 0.50594 | 11.3349 | 21.0242 | 1.2552 | 0.17514 | 332.1993 | 29.15 | 53.34
2021-01-23 21:45 | 1.0733 | 0.25477 | 0.11967 | 0.51019 | 12.1434 | 10.0173 | 1.2626 | 0.16786 | 331.1483 | 29.13 | 53.62
2021-01-23 21:50 | 0.76672 | 0.3137 | 0.13859 | 0.61943 | 12.3595 | 15.2525 | 1.2773 | 0.16058 | 330.601 | 29.12 | 53.92
2021-01-23 21:55 | 0.75405 | 0.27401 | 0.13231 | 0.55232 | 20.3465 | 20.7963 | 1.2921 | 0.1533 | 331.0857 | 29.11 | 54.3
2021-01-23 22:00 | 0.88205 | 0.30697 | 0.13444 | 0.60286 | 31.8051 | 27.7144 | 1.2924 | 0.15334 | 331.5304 | 29.11 | 54.86
2021-01-23 22:05 | 0.57531 | 0.27684 | 0.12395 | 0.5504 | 27.1443 | 13.6335 | 1.2926 | 0.15335 | 331.5101 | 29.1 | 55.12
2021-01-23 22:10 | 1.9438 | 0.24813 | 0.12818 | 0.50852 | 25.5351 | 22.2613 | 1.2856 | 0.1607 | 331.4662 | 29.06 | 55.89
2021-01-23 22:15 | 2.136 | 0.22075 | 0.1219 | 0.45817 | 22.0401 | 0.061393 | 1.2785 | 0.16803 | 330.9415 | 29.01 | 56.48
2021-01-23 22:20 | 1.2151 | 0.30577 | 0.1156 | 0.58639 | 19.6975 | 15.1031 | 1.2785 | 0.16804 | 331.5199 | 28.95 | 56.74
2021-01-23 22:25 | 2.0086 | 0.29213 | 0.12404 | 0.57183 | 21.6985 | 22.5992 | 1.2789 | 0.14616 | 330.9118 | 28.95 | 57.38
2021-01-23 22:30 | 0.74199 | 0.25371 | 0.11982 | 0.50872 | 15.505 | 22.5257 | 1.2861 | 0.14615 | 330.9932 | 28.9 | 57.35
2021-01-23 22:35 | 0.65247 | 0.24549 | 0.11562 | 0.49192 | 21.9536 | 1.484 | 1.2935 | 0.13154 | 332.0422 | 28.88 | 57.53
2021-01-23 22:40 | 0.53742 | 0.15226 | 0.10303 | 0.33641 | 17.4225 | 23.7589 | 1.2937 | 0.13887 | 331.0218 | 28.81 | 58.17
2021-01-23 22:45 | 0.56297 | 0.19888 | 0.11774 | 0.42259 | 10.9114 | 11.6689 | 1.3082 | 0.14617 | 331.1195 | 28.74 | 58.25
2021-01-23 22:50 | 0.40948 | 0.19342 | 0.11144 | 0.40582 | 13.4618 | 7.3195 | 1.3084 | 0.13888 | 331.6339 | 28.71 | 58.65
2021-01-23 22:55 | 0.31998 | 0.17014 | 0.088332 | 0.34912 | 15.6251 | 9.9833 | 1.3159 | 0.13159 | 332.6505 | 28.67 | 59.31
2021-01-23 23:00 | 0.47359 | 0.25247 | 0.10306 | 0.48795 | 8.0485 | 4.4338 | 1.3306 | 0.1316 | 331.1024 | 28.64 | 59.54
2021-01-23 23:05 | 0.61444 | 0.24701 | 0.098862 | 0.47748 | 11.6847 | 10.1076 | 1.3235 | 0.13161 | 332.1131 | 28.64 | 59.78
2021-01-23 23:10 | 0.42243 | 0.24426 | 0.098863 | 0.47328 | 19.8262 | 21.2906 | 1.3088 | 0.13161 | 332.6551 | 28.62 | 59.86
2021-01-23 23:15 | 0.46077 | 0.23737 | 0.084127 | 0.44798 | 16.1373 | 12.9221 | 1.3013 | 0.20471 | 332.2113 | 28.59 | 59.63
2021-01-23 23:20 | 0.42239 | 0.28952 | 0.092543 | 0.53423 | 17.9196 | 17.9401 | 1.3087 | 0.2632 | 332.7545 | 28.56 | 59.82
2021-01-23 23:25 | 0.47363 | 0.22093 | 0.094655 | 0.43331 | 15.5659 | 4.1373 | 1.3015 | 0.20473 | 331.713 | 28.53 | 60.16
2021-01-23 23:30 | 0.46083 | 0.21956 | 0.09255 | 0.4291 | 11.7766 | 14.3061 | 1.3088 | 0.20473 | 332.8173 | 28.48 | 60.29
2021-01-23 23:35 | 0.47363 | 0.17976 | 0.07993 | 0.35548 | 10.681 | 11.1418 | 1.3015 | 0.19742 | 332.8705 | 28.43 | 60.48
2021-01-23 23:40 | 0.58887 | 0.20722 | 0.10097 | 0.41861 | 12.8016 | 0 | 1.2943 | 0.22668 | 332.3614 | 28.4 | 60.74
2021-01-23 23:45 | 0.78079 | 0.22229 | 0.094647 | 0.43327 | 4.9049 | 11.1102 | 1.2941 | 0.16816 | 331.9065 | 28.38 | 60.47
2021-01-23 23:50 |  | 0.21817 | 0.08413 | 0.41855 | 7.7413 | 4.311 | 1.2868 | 0.20471 | 333.4956 | 28.36 | 60.53
2021-01-23 23:55 | 0.62722 | 0.20034 | 0.092548 | 0.40174 | 13.4148 | 7.1477 | 1.2941 | 0.19741 | 332.9696 | 28.35 | 60.68
2021-01-24 | 0.55036 | 0.11663 | 0.071507 | 0.25027 | 15.1746 | 14.8674 | 1.294 | 0.13159 | 332.0145 | 28.3 | 60.6
2021-01-24 00:05 | 0.67838 | 0.17426 | 0.07782 | 0.34493 | 14.9398 | 11.3456 | 1.2941 | 0.12429 | 332.5429 | 28.28 | 60.79
2021-01-24 00:10 | 0.4224 | 0.14408 | 0.082028 | 0.30287 | 10.8543 | 7.0041 | 1.3014 | 0.11698 | 330.9937 | 28.26 | 60.9
2021-01-24 00:15 | 0.2816 | 0.086446 | 0.069409 | 0.20192 | 10.6087 | 21.6474 | 1.3014 | 0.11698 | 332.0887 | 28.21 | 61.11
2021-01-24 00:20 | 0.2816 | 0.090562 | 0.060995 | 0.19981 | 19.6709 | 16.1689 | 1.3014 | 0.10967 | 332.6906 | 28.14 | 61.34
2021-01-24 00:25 | 0.256 | 0.13036 | 0.084132 | 0.28605 | 7.3421 | -4.7207 | 1.3014 | 0.10236 | 333.7641 | 28.11 | 61.48
2021-01-24 00:30 | 0.26882 | 0.10155 | 0.084137 | 0.23979 | 3.2565 | -2.0891 | 1.2942 | 0.10237 | 332.7354 | 28.08 | 61.72
2021-01-24 00:35 | 0.30722 | 0.11664 | 0.092552 | 0.27135 | 9.0221 | 14.419 | 1.3015 | 0.10237 | 332.2289 | 28.06 | 61.84
2021-01-24 00:40 | 0.29443 | 0.11116 | 0.088348 | 0.25873 | 7.4863 | 2.6627 | 1.3016 | 0.087746 | 331.7067 | 28.05 | 61.96
2021-01-24 00:45 | 0.15362 | 0.078222 | 0.077831 | 0.19773 | 8.92 | -9.3707 | 1.2943 | 0.087746 | 332.2725 | 28.01 | 62.11
2021-01-24 00:50 | 0.6657 | 0.12077 | 0.073627 | 0.25875 | 9.4018 | 7.292 | 1.2943 | 0.095062 | 331.8018 | 27.95 | 62.44
2021-01-24 00:55 | 0.23045 | 0.11391 | 0.069424 | 0.24614 | 7.6305 | 18.8047 | 1.3017 | 0.10969 | 332.3368 | 27.92 | 62.71
2021-01-24 01:00 | 1.4465 | 0.13997 | 0.084139 | 0.29869 | 6.3903 | 1.0753 | 1.3235 | 0.16818 | 333.4694 | 27.88 | 62.52
2021-01-24 01:05 |  |  |  |  | 15.6185 | 13.9184 |  |  | 332.9223 | 27.88 | 62.71
2021-01-24 01:10 |  |  |  |  | 12.9156 | 18.5693 |  |  | 331.8553 | 27.88 | 62.88
2021-01-24 01:15 |  |  |  |  | 12.0944 | -4.9975 |  |  | 331.9488 | 27.84 | 62.64
2021-01-24 01:20 |  |  |  |  | 14.7678 | 12.74 |  |  | 331.981 | 27.8 | 62.88
2021-01-24 01:25 |  |  |  |  | 9.4628 | 13.5183 |  |  | 332.0591 | 27.73 | 63.13
2021-01-24 01:30 |  |  |  |  | 10.9372 | -4.8541 |  |  | 332.6148 | 27.71 | 63.12
2021-01-24 01:35 |  |  |  |  | 10.7231 | 12.3208 |  |  | 333.1073 | 27.71 | 63.36
2021-01-24 01:40 |  |  |  |  | 7.752 | 10.691 |  |  | 332.662 | 27.68 | 63.12
2021-01-24 01:45 |  |  |  |  | 10.8328 | -5.4369 |  |  | 331.7051 | 27.64 | 62.91
2021-01-24 01:50 |  |  |  |  | 8.5405 | -2.2836 |  |  | 332.1922 | 27.63 | 63.32
2021-01-24 01:55 |  |  |  |  | -0.11265 | 4.5161 |  |  | 332.6984 | 27.64 | 63.33
2021-01-24 02:00 |  |  |  |  | 8.9289 | 8.2941 |  |  | 332.7325 | 27.64 | 63.06
2021-01-24 02:05 |  |  |  |  | 8.0896 | -9.687 |  |  | 333.4766 | 27.6 | 63.24
2021-01-24 02:10 | -0.1792 | 0.079585 | 0.069409 | 0.1935 | -1.9046 | 12.3904 | 1.3818 | 0.043868 | 332.974 | 27.58 | 63.33
2021-01-24 02:15 | -0.051199 | 0.067235 | 0.063098 | 0.16616 | 6.3692 | 0.95231 | 1.3672 | 0.065801 | 332.9898 | 27.57 | 63.33
2021-01-24 02:20 | -0.051202 | 0.050772 | 0.058894 | 0.13462 | 8.1923 | 0.83971 | 1.3526 | 0.080428 | 331.9506 | 27.55 | 63.53
2021-01-24 02:25 | -0.038403 | 0.039796 | 0.05469 | 0.11569 | 2.7855 | 6.206 | 1.3527 | 0.080432 | 331.9782 | 27.51 | 63.81
2021-01-24 02:30 | -0.1152 | 0.03842 | 0.054686 | 0.11358 | 4.6182 | 10.4243 | 1.3453 | 0.073114 | 334.1308 | 27.48 | 63.7
2021-01-24 02:35 | 0.17921 | 0.03705 | 0.052584 | 0.10938 | 9.9741 | -8.6019 | 1.3453 | 0.080428 | 333.6288 | 27.45 | 63.91
2021-01-24 02:40 | -0.012801 | 0.035679 | 0.050484 | 0.10517 | 8.2747 | 14.1939 | 1.3527 | 0.087744 | 332.599 | 27.42 | 64.16
2021-01-24 02:45 | 0.2176 | 0.038421 | 0.048376 | 0.10727 | 13.7728 | 10.6599 | 1.3453 | 0.087736 | 332.6612 | 27.39 | 64.04
2021-01-24 02:50 | 0.012801 | 0.04254 | 0.048379 | 0.11359 | 13.999 | 8.0492 | 1.3527 | 0.095054 | 332.6508 | 27.38 | 64.25
2021-01-24 02:55 | -0.064012 | 0.1194 | 0.054696 | 0.23982 | 10.8564 | 6.0017 | 1.3529 | 0.117 | 332.0664 | 27.4 | 64.49
2021-01-24 03:00 | -0.25608 | 0.10432 | 0.056807 | 0.21881 | 21.3367 | 18.4583 | 1.353 | 0.10239 | 333.0457 | 27.42 | 64.77
2021-01-24 03:05 | -0.076834 | 0.06452 | 0.056814 | 0.15571 | 17.098 | 9.6503 | 1.3605 | 0.10972 | 332.5274 | 27.38 | 65.24
2021-01-24 03:10 | -0.24334 | 0.074139 | 0.050508 | 0.16415 | 13.9446 | 8.8934 | 1.368 | 0.12436 | 333.573 | 27.34 | 65.75
2021-01-24 03:15 | -0.10246 | 0.094732 | 0.048403 | 0.19361 | 16.7722 | 26.1676 | 1.3826 | 0.16094 | 332.5867 | 27.29 | 65.91
2021-01-24 03:20 | -0.076851 | 0.12358 | 0.056827 | 0.24625 | 18.6698 | 12.3782 | 1.3901 | 0.13901 | 332.5277 | 27.31 | 66.13
2021-01-24 03:25 | -0.051233 | 0.11671 | 0.063139 | 0.24203 | 14.5296 | 4.7237 | 1.3827 | 0.12437 | 333.5943 | 27.3 | 66.09
2021-01-24 03:30 | -0.10246 | 0.061785 | 0.063137 | 0.15784 | 18.3408 | 10.5024 | 1.3681 | 0.139 | 332.5912 | 27.27 | 66.13
2021-01-24 03:35 | -0.012809 | 0.063162 | 0.061036 | 0.15785 | 11.4662 | 11.3023 | 1.3755 | 0.15364 | 333.6843 | 27.21 | 66.52
2021-01-24 03:40 | -0.14091 | 0.06729 | 0.052625 | 0.15787 | 9.7769 | 5.1036 | 1.383 | 0.1683 | 332.6475 | 27.16 | 67.09
2021-01-24 03:45 | 0 | 0.078285 | 0.050526 | 0.17052 | 19.2792 | -1.0557 | 1.3904 | 0.16832 | 332.1194 | 27.13 | 67.52
2021-01-24 03:50 | 0.15376 | 0.081041 | 0.056848 | 0.18318 | 10.5171 | 9.1025 | 1.3979 | 0.16833 | 333.1408 | 27.12 | 67.85
2021-01-24 03:55 | 0.25629 | 0.10028 | 0.069488 | 0.2232 | 9.0932 | 19.9599 | 1.4054 | 0.16835 | 332.0605 | 27.12 | 68.13
2021-01-24 04:00 | 0.38449 | 0.10304 | 0.063179 | 0.21902 | 13.4315 | 4.5934 | 1.4129 | 0.16838 | 331.4689 | 27.14 | 68.43
2021-01-24 04:05 | 0.43576 | 0.11816 | 0.067392 | 0.24851 | 10.5607 | 10.6017 | 1.4202 | 0.16838 | 333.0472 | 27.13 | 68.48
2021-01-24 04:10 | 0.1538 | 0.12365 | 0.056862 | 0.2464 | 2.6863 | 7.7514 | 1.4129 | 0.15374 | 331.5193 | 27.09 | 68.67
2021-01-24 04:15 | 0.82029 | 0.11129 | 0.056864 | 0.22956 | 11.2379 | -9.1667 | 1.413 | 0.15374 | 332.5752 | 27.07 | 68.85
2021-01-24 04:20 | 0.34603 | 0.083807 | 0.061072 | 0.18953 | 11.0936 | 11.6062 | 1.4055 | 0.14641 | 331.5759 | 27.05 | 68.73
2021-01-24 04:25 | 0.21788 | 0.090678 | 0.061073 | 0.20007 | 9.4328 | 9.7199 | 1.4056 | 0.11713 | 331.5908 | 27.03 | 68.87
2021-01-24 04:30 | 0.14099 | 0.11679 | 0.056865 | 0.23589 | 17.7288 | 14.1604 | 1.3837 | 0.15374 | 333.1254 | 27.04 | 69.02
2021-01-24 04:35 | 0.25637 | 0.14016 | 0.06319 | 0.27804 | 18.8895 | -2.3381 | 1.3765 | 0.15376 | 332.0218 | 27.06 | 69.23
2021-01-24 04:40 | 0.1282 | 0.16079 | 0.077944 | 0.32231 | 14.6149 | 11.5893 | 1.362 | 0.1611 | 332.4509 | 27.11 | 69.34
2021-01-24 04:45 | 0.28207 | 0.1347 | 0.082166 | 0.29074 | 21.94 | 29.3046 | 1.3475 | 0.14647 | 331.8381 | 27.16 | 69.42
2021-01-24 04:50 | 0.051287 | 0.11683 | 0.077955 | 0.25704 | 33.8291 | 11.95 | 1.3403 | 0.14648 | 331.1025 | 27.17 | 69.54
2021-01-24 04:55 | 0.10258 | 0.14021 | 0.08428 | 0.3013 | 19.3056 | 14.392 | 1.3403 | 0.095215 | 331.6072 | 27.17 | 69.69
2021-01-24 05:00 | 0.47451 | 0.17047 | 0.0864 | 0.34771 |  |  | 1.3259 | 0.21976 | 440.8784 | 27.21 | 69.86
2021-01-24 05:05 | 0.56434 | 0.17187 | 0.080088 | 0.34353 |  |  | 1.3187 | 0.29305 | 511.7734 | 27.26 | 69.98
2021-01-24 05:10 | 0.50021 | 0.1045 | 0.065334 | 0.22551 |  | -4.8225 | 1.326 | 0.17583 | 511.7944 | 27.25 | 70
2021-01-24 05:15 | 0.38477 | 0.12374 | 0.063226 | 0.2529 |  | 14.3444 | 1.3407 | 0.1685 | 510.8226 | 27.21 | 70.14
2021-01-24 05:20 | 0.51305 | 0.14025 | 0.056906 | 0.27399 | -5.541 | 0.57462 | 1.3481 | 0.21247 | 510.8534 | 27.18 | 70.37
2021-01-24 05:25 | 0.47462 | 0.13889 | 0.050587 | 0.26558 | 26.8145 | 23.8591 | 1.3408 | 0.23447 | 512.3748 | 27.18 | 70.61
2021-01-24 05:30 | 0.29505 | 0.13202 | 0.071669 | 0.27192 | 30.9823 | 29.6072 | 1.3482 | 0.14655 | 511.8625 | 27.16 | 70.82
2021-01-24 05:35 | 0.69282 | 0.17467 | 0.078004 | 0.34575 | 30.484 | 9.9047 | 1.3778 | 0.18321 | 510.7421 | 27.16 | 71.22
2021-01-24 05:40 | 1.5527 | 0.19397 | 0.082237 | 0.37955 | 18.9305 | 15.2655 | 1.378 | 0.39582 | 510.1024 | 27.17 | 71.71
2021-01-24 05:45 | 1.1936 | 0.22977 | 0.088576 | 0.44077 | 30.2483 | 21.182 | 1.3562 | 0.3079 | 510.4945 | 27.2 | 72
2021-01-24 05:50 | 1.1163 | 0.22283 | 0.092771 | 0.43223 | 45.084 | 9.2385 | 1.3632 | 0.28584 | 511.1264 | 27.21 | 71.29
2021-01-24 05:55 | 1.3728 | 0.20768 | 0.078002 | 0.39634 | 27.3631 | 21.1433 | 1.3631 | 0.38107 | 511.7132 | 27.21 | 70.95
2021-01-24 06:00 | 0.78265 | 0.24207 | 0.080115 | 0.45328 | 30.8955 | 6.9694 | 1.3485 | 0.27116 | 510.1029 | 27.22 | 71.05
2021-01-24 06:05 | 0.69291 | 0.33151 | 0.088557 | 0.5967 | 26.7308 | 12.2978 | 1.3486 | 0.21255 | 511.6178 | 27.22 | 71.32
2021-01-24 06:10 | 0.34647 | 0.31226 | 0.099103 | 0.57775 | 35.4166 | 16.6509 | 1.3413 | 0.36648 | 511.0767 | 27.22 | 71.42
2021-01-24 06:15 | 0.47479 | 0.26824 | 0.092778 | 0.50395 | 40.9603 | 17.5749 | 1.356 | 0.27853 | 511.0305 | 27.24 | 71.42
2021-01-24 06:20 | 1.7711 | 0.23939 | 0.09068 | 0.45762 | 41.0475 | 50.6882 | 1.3782 | 0.30056 | 509.3657 | 27.26 | 71.67
2021-01-24 06:25 | 1.5401 | 0.29031 | 0.10545 | 0.55044 | 40.5569 | 22.5168 | 1.3782 | 0.26392 | 509.7747 | 27.31 | 71.61
2021-01-24 06:30 | 2.0408 | 0.38252 | 0.12022 | 0.70445 | 53.4778 | 23.2682 | 1.3857 | 0.3006 | 509.1104 | 27.37 | 71.57
2021-01-24 06:35 | 1.4629 | 0.51725 | 0.10332 | 0.89618 | 53.1581 | 34.6483 | 1.3854 | 0.27854 | 509.1369 | 27.42 | 70.78
2021-01-24 06:40 | 1.6169 | 0.57641 | 0.15604 | 1.0396 | 41.9992 | 16.9188 | 1.3854 | 0.22723 | 510.0244 | 27.51 | 70.43
2021-01-24 06:45 | 1.3732 | 0.53105 | 0.14129 | 0.95531 | 40.2673 | 21.1193 | 1.3782 | 0.20526 | 511.9702 | 27.57 | 70.39
2021-01-24 06:50 | 1.2064 | 0.40035 | 0.10755 | 0.71912 | 36.6535 | 13.7066 | 1.3928 | 0.21259 | 509.3245 | 27.59 | 70.32
2021-01-24 06:55 | 1.3603 | 0.37831 | 0.11598 | 0.69587 | 48.8365 | 30.963 | 1.3854 | 0.23456 | 509.3328 | 27.61 | 70.02
2021-01-24 07:00 | 1.4756 | 0.48419 | 0.090665 | 0.83285 | 42.0671 | 28.1577 | 1.3926 | 0.23454 | 508.757 | 27.67 | 69.53
2021-01-24 07:05 | 1.783 | 0.58578 | 0.137 | 1.0349 | 53.9352 | 33.0014 | 1.3701 | 0.2198 | 508.8698 | 27.71 | 68.44
2021-01-24 07:10 | 1.0772 | 0.5609 | 0.11379 | 0.97566 | 61.5149 | 41.0578 | 1.3552 | 0.26371 | 509.4561 | 27.74 | 67.73
2021-01-24 07:15 | 0.65388 | 0.39583 | 0.11798 | 0.72473 | 51.3766 | 21.9805 | 1.3475 | 0.23435 | 509.4932 | 27.79 | 66.91
2021-01-24 07:20 | 1.2818 | 0.45208 | 0.17903 | 0.87411 | 54.6671 | 17.9763 | 1.3326 | 0.17572 | 507.8889 | 27.88 | 65.98
2021-01-24 07:25 | 1.5892 | 0.42041 | 0.16426 | 0.80869 | 42.6215 | 31.7226 | 1.3031 | 0.19766 | 508.3737 | 27.95 | 65.3
2021-01-24 07:30 | 1.0764 | 0.3187 | 0.14108 | 0.62749 | 42.4721 | 16.2282 | 1.3029 | 0.21959 | 508.8474 | 28.02 | 64.68
2021-01-24 07:35 | 0.74328 | 0.29399 | 0.14741 | 0.59805 | 41.0703 | 21.9807 | 1.3103 | 0.19032 | 508.7296 | 28.07 | 64.66
2021-01-24 07:40 | 0.96098 | 0.30218 | 0.1558 | 0.619 | 50.432 | 22.6534 | 1.3101 | 0.18297 | 508.195 | 28.13 | 63.99
2021-01-24 07:45 | 1.5501 | 0.37767 | 0.14525 | 0.72416 | 50.4142 | 36.5577 | 1.3245 | 0.2049 | 506.5715 | 28.21 | 63.31
2021-01-24 07:50 | 1.768 | 0.46558 | 0.1621 | 0.87576 | 53.5827 | 20.6316 | 1.3319 | 0.19758 | 506.9438 | 28.29 | 63.09
2021-01-24 07:55 | 1.6402 | 0.45056 | 0.14529 | 0.83592 | 55.4898 | 41.5174 | 1.3468 | 0.20494 | 506.7082 | 28.37 | 63.3
2021-01-24 08:00 | 1.2945 | 0.45065 | 0.16637 | 0.85714 | 54.5878 | 20.0347 | 1.3617 | 0.19034 | 507.5203 | 28.45 | 63.48
2021-01-24 08:05 | 1.7945 | 0.43421 | 0.1685 | 0.83407 | 47.0675 | 29.8812 | 1.3618 | 0.18304 | 506.2842 | 28.53 | 63.48
2021-01-24 08:10 | 1.7944 | 0.39846 | 0.18744 | 0.79822 | 51.4943 | 32.0122 | 1.3617 | 0.19767 | 506.2139 | 28.59 | 63.11
2021-01-24 08:15 | 1.7561 | 0.37925 | 0.18324 | 0.76457 | 46.1343 | 19.0218 | 1.3618 | 0.13179 | 506.5713 | 28.67 | 62.96
2021-01-24 08:20 | 1.5128 | 0.34359 | 0.18328 | 0.70995 | 47.9692 | 39.0153 | 1.3328 | 0.14646 | 506.8725 | 28.74 | 63.2
2021-01-24 08:25 | 1.6029 | 0.43027 | 0.21914 | 0.87868 | 57.4179 | 14.4135 | 1.3111 | 0.19777 | 507.6989 | 28.8 | 63.53
2021-01-24 08:30 | 1.9237 | 0.46881 | 0.2002 | 0.9188 | 58.1724 | 41.6646 | 1.3112 | 0.26371 | 504.9319 | 28.87 | 63.51
2021-01-24 08:35 | 1.8983 | 0.46886 | 0.18336 | 0.90204 | 58.1789 | 20.7474 | 1.326 | 0.2784 | 504.7416 | 28.95 | 63.49
2021-01-24 08:40 | 2.8732 | 0.56514 | 0.24239 | 1.1087 | 54.1805 | 38.2547 | 1.3335 | 0.28574 | 505.1137 | 29.02 | 63.38
2021-01-24 08:45 | 3.3081 | 0.59241 | 0.21912 | 1.1293 | 58.2012 | 31.5829 | 1.3329 | 0.27831 | 503.5812 | 29.12 | 62.09
2021-01-24 08:50 | 2.846 | 0.59233 | 0.22541 | 1.1333 | 56.5005 | 23.8042 | 1.3181 | 0.27827 | 505.0633 | 29.21 | 61.42
2021-01-24 08:55 | 2.4236 | 0.57873 | 0.22757 | 1.1147 | 54.6683 | 48.7901 | 1.3111 | 0.29299 | 505.8229 | 29.3 | 61.71
2021-01-24 09:00 | 3.1548 | 0.62002 | 0.20862 | 1.159 | 56.2216 | 15.779 | 1.3039 | 0.30766 | 503.072 | 29.37 | 61.64
2021-01-24 09:05 | 2.6673 | 0.66535 | 0.22758 | 1.2475 | 61.3485 | 27.6274 | 1.2965 | 0.293 | 503.5141 | 29.43 | 61.32
2021-01-24 09:10 | 2.8727 | 0.64477 | 0.21495 | 1.2012 | 60.7261 | 5.1811 | 1.2893 | 0.28569 | 503.9052 | 29.49 | 61.24
2021-01-24 09:15 | 2.4493 | 0.70523 | 0.24022 | 1.3212 | 63.5445 | 29.8333 | 1.2892 | 0.27835 | 503.3079 | 29.56 | 60.82
2021-01-24 09:20 | 2.8989 | 0.8663 | 0.27612 | 1.604 | 62.1656 | 11.8728 | 1.2822 | 0.30773 | 503.544 | 29.65 | 61.12
2021-01-24 09:25 | 2.5274 | 0.75504 | 0.26984 | 1.4251 | 63.5305 | 41.1563 | 1.2824 | 0.27114 | 503.3286 | 29.73 | 61.22
2021-01-24 09:30 | 2.2182 | 0.52506 | 0.26968 | 1.0745 | 73.5148 | 41.4912 | 1.2817 | 0.23436 | 503.5242 | 29.79 | 59.65
2021-01-24 09:35 | 1.7172 | 0.4863 | 0.28848 | 1.0339 | 78.1594 | 30.8885 | 1.2736 | 0.17567 | 503.6849 | 29.86 | 58.14
2021-01-24 09:40 | 4.6381 | 0.6373 | 0.28212 | 1.2569 | 78.5355 | 17.7838 | 1.2807 | 0.2781 | 502.0837 | 29.94 | 57.48
2021-01-24 09:45 | 5.4802 | 0.7316 | 0.29877 | 1.4202 | 76.7226 | 24.9835 | 1.2799 | 0.28524 | 504.3676 | 30.01 | 55.76
2021-01-24 09:50 | 3.5565 | 0.76114 | 0.32794 | 1.4946 | 91.0667 | 40.2216 | 1.2788 | 0.18999 | 504.7025 | 30.07 | 53.6
2021-01-24 09:55 | 2.2252 | 0.81433 | 0.32782 | 1.5739 | 82.6953 | 18.088 | 1.2637 | 0.1461 | 503.717 | 30.15 | 52.52
2021-01-24 10:00 | 2.0581 | 0.67834 | 0.31088 | 1.3507 | 99.8744 | 36.4072 | 1.234 | 0.18985 | 504.3008 | 30.23 | 51.39
2021-01-24 10:05 | 2.2624 | 0.64126 | 0.28564 | 1.2686 | 90.5978 | 28.2837 | 1.2339 | 0.30664 | 504.6988 | 30.34 | 50.79
2021-01-24 10:10 | 3.6685 | 0.7002 | 0.30035 | 1.3736 | 87.8803 | 32.5486 | 1.2558 | 0.34316 | 505.0867 | 30.41 | 50.65
2021-01-24 10:15 | 4.0773 | 0.7303 | 0.30244 | 1.4219 | 87.4255 | 34.418 | 1.2703 | 0.32854 | 503.4926 | 30.45 | 50.41
2021-01-24 10:20 | 4.5499 | 0.71656 | 0.31502 | 1.4134 | 78.8823 | 28.7719 | 1.2849 | 0.37962 | 503.4427 | 30.5 | 50.12
2021-01-24 10:25 | 4.7925 | 0.92202 | 0.3633 | 1.7766 | 90.5637 | 25.9995 | 1.2775 | 0.41609 | 502.7382 | 30.63 | 49.62
2021-01-24 10:30 | 4.0257 | 0.82885 | 0.336 | 1.6065 | 73.7962 | 8.7415 | 1.2775 | 0.35769 | 503.1087 | 30.72 | 49.36
2021-01-24 10:35 | 3.4053 | 0.86459 | 0.35341 | 1.6808 | 74.794 | 36.8183 | 1.287 | 0.34369 | 502.5784 | 30.83 | 52.82
2021-01-24 10:40 | 3.7542 | 0.95323 | 0.35581 | 1.817 | 98.2998 | 30.3817 | 1.31 | 0.33666 | 503.0856 | 30.89 | 54.49
2021-01-24 10:45 | 3.9079 | 0.93949 | 0.37266 | 1.8127 | 93.0208 | 61.5834 | 1.3174 | 0.39521 | 502.4708 | 30.95 | 54.3
2021-01-24 10:50 | 3.9591 | 0.8406 | 0.33476 | 1.6233 | 96.4749 | 31.7654 | 1.3247 | 0.38057 | 502.3895 | 31 | 54.14
2021-01-24 10:55 | 4.2027 | 0.84199 | 0.40635 | 1.697 | 95.1443 | 33.6213 | 1.3393 | 0.30739 | 502.8129 | 31.05 | 54.03
2021-01-24 11:00 | 3.5749 | 0.90108 | 0.35162 | 1.7328 | 84.5069 | 43.9243 | 1.3467 | 0.3074 | 503.7477 | 31.1 | 53.94
2021-01-24 11:05 | 3.5237 | 0.81316 | 0.35162 | 1.5981 | 79.2069 | 19.2713 | 1.3613 | 0.32935 | 503.2172 | 31.11 | 53.9
2021-01-24 11:10 | 3.9079 | 0.74857 | 0.32844 | 1.4759 | 69.6702 | 49.0162 | 1.3832 | 0.35861 | 505.2908 | 31.12 | 53.76
2021-01-24 11:15 | 4.1134 | 0.81735 | 0.38744 | 1.6403 | 87.968 | 34.9166 | 1.4127 | 0.3367 | 502.0786 | 31.15 | 53.95
2021-01-24 11:20 | 4.1652 | 0.80921 | 0.47173 | 1.7121 | 82.5347 | 61.4653 | 1.4348 | 0.32942 | 503.4651 | 31.21 | 54.03
2021-01-24 11:25 | 3.6278 | 0.7833 | 0.42339 | 1.6241 | 86.3904 | 23.382 | 1.4352 | 0.27825 | 502.7432 | 31.26 | 54.4
2021-01-24 11:30 | 3.0767 | 0.83829 | 0.39602 | 1.6789 | 78.6193 | 57.3082 | 1.4499 | 0.25629 | 502.1299 | 31.31 | 54.31
2021-01-24 11:35 | 2.6788 | 0.80106 | 0.34962 | 1.5775 | 67.5017 | 19.0006 | 1.4569 | 0.19768 | 502.2102 | 31.31 | 53.97
2021-01-24 11:40 | 2.7559 | 0.75302 | 0.35807 | 1.5123 | 53.3858 | 36.2298 | 1.4278 | 0.22698 | 501.127 | 31.32 | 54.09
2021-01-24 11:45 | 2.9739 | 0.70631 | 0.34755 | 1.4323 | 40.65 | 31.5437 | 1.4058 | 0.25627 | 502.1638 | 31.32 | 54.06
2021-01-24 11:50 | 4.1534 | 0.85476 | 0.34967 | 1.6599 | 53.338 | 11.7321 | 1.4059 | 0.41005 | 502.0544 | 31.37 | 54.02
2021-01-24 11:55 | 4.4096 | 0.8506 | 0.37704 | 1.6809 | 53.9921 | 42.2605 | 1.4058 | 0.43932 | 502.5241 | 31.41 | 53.81
2021-01-24 12:00 | 3.7047 | 0.72283 | 0.34967 | 1.4576 | 51.3889 | 12.2857 | 1.3912 | 0.42469 | 501.945 | 31.44 | 53.78
2021-01-24 12:05 | 2.9609 | 0.72414 | 0.33278 | 1.4407 | 50.2973 | 26.1485 | 1.3765 | 0.32215 | 502.9537 | 31.48 | 53.47
2021-01-24 12:10 | 2.3964 | 0.61132 | 0.34323 | 1.2803 | 39.0799 | -12.5277 | 1.3761 | 0.29279 | 503.0426 | 31.5 | 52.9
2021-01-24 12:15 | 2.0754 | 0.57544 | 0.30735 | 1.1894 | 47.7605 | 35.7794 | 1.3684 | 0.26344 | 504.7242 | 31.5 | 52.33
2021-01-24 12:20 | 1.8319 | 0.50811 | 0.2947 | 1.0736 | 49.8887 | 12.0725 | 1.361 | 0.24147 | 503.7137 | 31.51 | 52.15
2021-01-24 12:25 | 2.4979 | 0.66601 | 0.31574 | 1.3366 | 55.2974 | 44.6704 | 1.3463 | 0.24878 | 503.7023 | 31.53 | 52
2021-01-24 12:30 | 3.0991 | 0.72348 | 0.37457 | 1.4814 | 62.6989 | 26.3602 | 1.3313 | 0.27065 | 502.7997 | 31.54 | 51.37
2021-01-24 12:35 | 3.0602 | 0.87299 | 0.39135 | 1.7295 | 58.9308 | 16.9018 | 1.3238 | 0.30718 | 502.8368 | 31.56 | 51.02
2021-01-24 12:40 | 3.2647 | 0.79191 | 0.33029 | 1.5442 | 60.6648 | 33.656 | 1.309 | 0.35102 | 503.3471 | 31.6 | 50.65
2021-01-24 12:45 | 2.5982 | 0.66408 | 0.31547 | 1.3334 | 64.8251 | 3.2049 | 1.3013 | 0.37285 | 501.8628 | 31.65 | 49.91
2021-01-24 12:50 | 2.4571 | 0.6146 | 0.33015 | 1.2722 | 66.4439 | 28.0825 | 1.3085 | 0.39473 | 502.4319 | 31.66 | 49.59
2021-01-24 12:55 | 1.9195 | 0.57753 | 0.33854 | 1.2238 | 72.9611 | 40.5499 | 1.3011 | 0.33623 | 502.4448 | 31.67 | 49.44
2021-01-24 13:00 | 2.124 | 0.67623 | 0.35954 | 1.3961 | 80.1712 | 25.9696 | 1.3083 | 0.25581 | 502.4243 | 31.71 | 49.14
2021-01-24 13:05 | 1.7399 | 0.6254 | 0.33636 | 1.2971 | 82.6168 | 13.4078 | 1.2935 | 0.23385 | 503.5227 | 31.71 | 48.86
2021-01-24 13:10 | 1.8416 | 0.53056 | 0.29631 | 1.1096 | 88.2735 | 19.7766 | 1.293 | 0.19723 | 501.6044 | 31.74 | 47.98
2021-01-24 13:15 | 1.918 | 0.57569 | 0.32566 | 1.2102 | 70.3761 | 28.8562 | 1.2854 | 0.17529 | 502.2166 | 31.74 | 47.58
2021-01-24 13:20 | 1.5854 | 0.60581 | 0.33405 | 1.2627 | 78.8005 | -1.6468 | 1.2707 | 0.16797 | 503.2692 | 31.75 | 47.39
2021-01-24 13:25 | 1.6364 | 0.63452 | 0.34241 | 1.315 | 91.3702 | 28.0227 | 1.2706 | 0.18986 | 502.8824 | 31.71 | 47.24
2021-01-24 13:30 | 2.2756 | 0.62905 | 0.35502 | 1.3193 | 82.3821 | 24.7402 | 1.2706 | 0.22637 | 502.3079 | 31.74 | 47.2
2021-01-24 13:35 | 2.25 | 0.69482 | 0.33401 | 1.3991 | 91.8001 | 44.4989 | 1.2633 | 0.27749 | 502.8147 | 31.75 | 47.14
2021-01-24 13:40 | 2.3011 | 0.80994 | 0.32981 | 1.5734 | 89.7549 | 1.6568 | 1.2633 | 0.29939 | 502.7471 | 31.79 | 47.04
2021-01-24 13:45 | 3.119 | 0.76601 | 0.32557 | 1.4997 | 92.752 | 51.2642 | 1.2559 | 0.31397 | 501.7366 | 31.81 | 46.77
2021-01-24 13:50 | 3.1312 | 0.67956 | 0.31922 | 1.3609 | 92.0507 | 11.9933 | 1.2556 | 0.27741 | 503.354 | 31.82 | 46.38
2021-01-24 13:55 | 2.6574 | 0.63274 | 0.28551 | 1.2533 | 87.3967 | 28.0965 | 1.2552 | 0.21893 | 503.0262 | 31.82 | 45.61
2021-01-24 14:00 | 1.9927 | 0.60799 | 0.29596 | 1.2279 | 71.3288 | 14.0614 | 1.2404 | 0.16782 | 502.6064 | 31.81 | 45.31
2021-01-24 14:05 | 1.6221 | 0.58875 | 0.34629 | 1.2487 | 88.2302 | 33.2077 | 1.2256 | 0.18968 | 503.1852 | 31.81 | 45.05
2021-01-24 14:10 | 1.2769 | 0.47908 | 0.28115 | 1.0155 | 77.6849 | 11.3999 | 1.2253 | 0.15316 | 503.3214 | 31.81 | 44.49
2021-01-24 14:15 | 1.2129 | 0.51599 | 0.28113 | 1.0721 | 69.2711 | 18.6609 | 1.2252 | 0.16044 | 502.905 | 31.78 | 44.36
2021-01-24 14:20 | 2.2982 | 0.67067 | 0.26435 | 1.2924 | 75.3812 | 24.8206 | 1.2325 | 0.24796 | 504.4378 | 31.78 | 44.42
2021-01-24 14:25 | 2.5531 | 0.71708 | 0.28528 | 1.3865 | 75.4292 | 17.4327 | 1.225 | 0.26979 | 502.9625 | 31.79 | 44.03
2021-01-24 14:30 | 3.0252 | 0.67049 | 0.29364 | 1.3214 | 89.2902 | 44.9719 | 1.2322 | 0.54683 | 503.5374 | 31.78 | 43.88
2021-01-24 14:35 | 3.1652 | 0.69367 | 0.34185 | 1.4072 | 96.5901 | 42.0565 | 1.2248 | 0.59051 | 502.5661 | 31.78 | 43.63
2021-01-24 14:40 | 2.9352 | 0.64846 | 0.30826 | 1.3022 | 80.7565 | 9.9848 | 1.2246 | 0.61232 | 503.5786 | 31.82 | 43.34
2021-01-24 14:45 | 2.0541 | 0.62504 | 0.32285 | 1.2809 | 64.6289 | 7.6857 | 1.2243 | 0.45183 | 504.2039 | 31.84 | 42.7
2021-01-24 14:50 | 1.9899 | 0.66593 | 0.29344 | 1.3163 | 77.034 | 38.3384 | 1.2241 | 0.29873 | 502.7818 | 31.83 | 42.28
2021-01-24 14:55 | 2.4745 | 0.6905 | 0.35421 | 1.4126 | 79.4891 | 38.1017 | 1.224 | 0.32057 | 503.2743 | 31.86 | 42.1
2021-01-24 15:00 | 3.0731 | 0.60966 | 0.37716 | 1.3096 | 72.0817 | 21.1981 | 1.2309 | 0.2695 | 503.3786 | 31.88 | 41.49
2021-01-24 15:05 | 2.6263 | 0.75577 | 0.35404 | 1.5146 | 81.3071 | 28.2616 | 1.2234 | 0.284 | 501.8867 | 31.91 | 40.99
2021-01-24 15:10 | 1.9373 | 0.72552 | 0.3728 | 1.487 | 77.7788 | 20.3012 | 1.2158 | 0.21841 | 504.0945 | 31.9 | 40.49
2021-01-24 15:15 | 1.2742 | 0.66384 | 0.35175 | 1.3693 | 74.81 | 25.5856 | 1.2009 | 0.20379 | 504.8089 | 31.87 | 39.95
2021-01-24 15:20 | 0.9046 | 0.67335 | 0.30985 | 1.342 | 74.2637 | 13.5562 | 1.2081 | 0.19649 | 504.8996 | 31.84 | 39.85
2021-01-24 15:25 | 1.0956 | 0.56537 | 0.24073 | 1.1073 | 75.9145 | 11.7913 | 1.2152 | 0.19647 | 504.9532 | 31.85 | 39.54
2021-01-24 15:30 | 1.312 | 0.55303 | 0.23652 | 1.0842 | 82.9898 | 17.4764 | 1.2151 | 0.18917 | 504.4833 | 31.85 | 39.35
2021-01-24 15:35 | 2.1146 | 0.65958 | 0.25537 | 1.2664 | 87.3165 | 23.9692 | 1.2152 | 0.19646 | 502.3667 | 31.86 | 39.47
2021-01-24 15:40 | 2.2293 | 0.60633 | 0.29306 | 1.2225 | 95.6946 | 39.1848 | 1.2079 | 0.18919 | 503.8937 | 31.87 | 39.47
2021-01-24 15:45 | 2.1146 | 0.62816 | 0.34328 | 1.3082 | 95.8035 | 18.1803 | 1.2151 | 0.17463 | 502.8611 | 31.88 | 39.38
2021-01-24 15:50 | 1.8468 | 0.71683 | 0.3244 | 1.4253 | 88.3426 | 21.1839 | 1.215 | 0.18188 | 504.4589 | 31.89 | 39.09
2021-01-24 15:55 | 1.2353 | 0.70037 | 0.32227 | 1.3979 | 84.5228 | 28.5886 | 1.2076 | 0.17459 | 502.9466 | 31.9 | 38.85
2021-01-24 16:00 | 1.9357 | 0.73447 | 0.31808 | 1.4418 | 81.4834 | 41.4243 | 1.2075 | 0.1964 | 501.9672 | 31.88 | 38.81
2021-01-24 16:05 | 2.3687 | 0.67166 | 0.30761 | 1.3372 | 86.9837 | 24.3795 | 1.2148 | 0.1964 | 502.4739 | 31.89 | 38.76
2021-01-24 16:10 | 2.6618 | 0.75091 | 0.32019 | 1.4733 | 78.1478 | 19.2975 | 1.2222 | 0.24734 | 504.5102 | 31.88 | 38.97
2021-01-24 16:15 | 2.9546 | 0.74678 | 0.30553 | 1.4523 | 72.9482 | 30.8705 | 1.2221 | 0.24006 | 504.0498 | 31.86 | 38.92
2021-01-24 16:20 | 3.1963 | 0.69075 | 0.25738 | 1.3162 | 66.3301 | -2.3737 | 1.2147 | 0.24731 | 504.6442 | 31.84 | 38.78
2021-01-24 16:25 | 3.9345 | 0.6156 | 0.23852 | 1.18 | 52.4089 | 29.5813 | 1.2219 | 0.25456 | 504.727 | 31.82 | 38.62
2021-01-24 16:30 | 3.132 | 0.6442 | 0.26778 | 1.2573 | 75.5445 | 30.4949 | 1.2218 | 0.2618 | 503.7957 | 31.79 | 38.47
2021-01-24 16:35 | 2.6222 | 0.65364 | 0.26774 | 1.2717 | 75.2152 | 18.982 | 1.2143 | 0.21086 | 507.0374 | 31.76 | 38.16
2021-01-24 16:40 | 2.0616 | 0.55523 | 0.27393 | 1.1229 | 64.1987 | 20.9618 | 1.2066 | 0.17445 | 504.1297 | 31.73 | 37.63
2021-01-24 16:45 | 2.5063 | 0.60554 | 0.31358 | 1.2439 | 59.6926 | 32.5078 | 1.2208 | 0.21074 | 505.8866 | 31.69 | 37.14
2021-01-24 16:50 | 3.625 | 0.62586 | 0.28007 | 1.2394 | 46.2274 | -6.0544 | 1.2351 | 0.50131 | 505.0135 | 31.66 | 36.74
2021-01-24 16:55 | 2.7086 | 0.53165 | 0.20687 | 1.0239 | 28.2812 | 26.0533 | 1.2275 | 0.38497 | 505.7187 | 31.62 | 36.32
2021-01-24 17:00 | 2.2635 | 0.56027 | 0.21104 | 1.0719 | 23.4894 | 1.8922 | 1.2203 | 0.4576 | 504.2206 | 31.59 | 36.36
2021-01-24 17:05 | 1.2842 | 0.49207 | 0.21729 | 0.97155 | 30.903 | 9.1142 | 1.2056 | 0.21062 | 504.8627 | 31.54 | 36.29
2021-01-24 17:10 | 1.3986 | 0.52749 | 0.20684 | 1.0154 | 38.6425 | 18.3193 | 1.2056 | 0.1743 | 505.9677 | 31.51 | 36.27
2021-01-24 17:15 | 1.513 | 0.60787 | 0.21727 | 1.149 | 39.9623 | 18.6742 | 1.2055 | 0.18155 | 505.5478 | 31.47 | 36.22
2021-01-24 17:20 | 2.4028 | 0.64463 | 0.23815 | 1.2263 | 33.1354 | 18.0424 | 1.2127 | 0.21785 | 506.1471 | 31.44 | 36.15
2021-01-24 17:25 | 2.6058 | 0.65135 | 0.24229 | 1.2407 | 34.6562 | 13.0062 | 1.2125 | 0.19604 | 504.7452 | 31.39 | 35.96
2021-01-24 17:30 | 2.4913 | 0.67584 | 0.29867 | 1.3346 | 17.4288 | 18.7914 | 1.198 | 0.22507 | 506.9136 | 31.35 | 35.92
2021-01-24 17:35 | 1.5505 | 0.64715 | 0.27358 | 1.2656 | 14.4275 | 8.8151 | 1.1978 | 0.18875 | 507.0376 | 31.31 | 35.76
2021-01-24 17:40 | 1.4614 | 0.51631 | 0.23179 | 1.0211 | 12.9318 | -3.2736 | 1.1977 | 0.1597 | 505.6082 | 31.26 | 35.68
2021-01-24 17:45 | 1.9698 | 0.54766 | 0.26103 | 1.1005 | 20.2112 | 18.2084 | 1.205 | 0.15244 | 506.7052 | 31.22 | 35.79
2021-01-24 17:50 | 1.8427 | 0.51906 | 0.2485 | 1.0441 | 18.646 | 18.0868 | 1.2123 | 0.16696 | 506.7604 | 31.18 | 35.92
2021-01-24 17:55 | 2.0335 | 0.53817 | 0.2527 | 1.0776 | 20.396 | 22.826 | 1.2124 | 0.20327 | 506.7609 | 31.16 | 36.1
2021-01-24 18:00 | 2.1476 | 0.49995 | 0.21716 | 0.9835 | 13.7546 | -7.3094 | 1.2122 | 0.23227 | 506.9009 | 31.12 | 35.87
2021-01-24 18:05 | 1.3213 | 0.42357 | 0.19624 | 0.8455 | 16.8414 | 9.1271 | 1.2119 | 0.16691 | 507.6137 | 31.07 | 35.5
2021-01-24 18:10 | 1.4226 | 0.42074 | 0.1941 | 0.84112 | 9.2875 | 5.3855 | 1.2116 | 0.1451 | 506.7804 | 31.02 | 35.08
2021-01-24 18:15 | 1.5493 | 0.40431 | 0.23162 | 0.85136 | 3.4236 | -0.43684 | 1.2186 | 0.14507 | 507.4828 | 30.98 | 34.66
2021-01-24 18:20 | 1.7142 | 0.40565 | 0.21074 | 0.83253 | 21.0685 | 11.4384 | 1.2258 | 0.16682 | 508.0848 | 30.95 | 34.58
2021-01-24 18:25 | 1.6629 | 0.40144 | 0.21276 | 0.82602 | 1.9397 | 1.4218 | 1.2182 | 0.16677 | 507.2629 | 30.91 | 34.01
2021-01-24 18:30 | 1.4218 | 0.46134 | 0.20443 | 0.91158 | 23.3075 | 13.9642 | 1.2255 | 0.16678 | 508.9032 | 30.85 | 34.21
2021-01-24 18:35 | 1.117 | 0.52526 | 0.2065 | 1.0116 | 139.9762 | 291.722 | 1.2181 | 0.13776 | 390.3259 | 30.82 | 34.13
2021-01-24 18:40 | 1.4335 | 0.6582 | 0.23555 | 1.2445 | 205.529 | 139.0761 | 1.2246 | 0.15217 | 350.0562 | 30.73 | 32.91
2021-01-24 18:45 | 1.6455 | 0.60112 | 0.25375 | 1.1752 | 115.713 | 23.5942 | 1.2219 | 0.15183 | 352.4626 | 30.67 | 28.13
2021-01-24 18:50 | 1.3286 | 0.62532 | 0.27861 | 1.2371 | 39.4986 | 6.6708 | 1.2215 | 0.15901 | 350.523 | 30.65 | 27.36
2021-01-24 18:55 | 1.1391 | 0.56712 | 0.25372 | 1.123 | 3.5032 | -8.8189 | 1.2217 | 0.13013 | 350.987 | 30.63 | 27.91
2021-01-24 19:00 | 1.1521 | 0.43023 | 0.21012 | 0.86959 | -10.736 | -10.8373 | 1.2294 | 0.13017 | 349.3637 | 30.58 | 28.72
2021-01-24 19:05 | 1.6458 | 0.45465 | 0.18931 | 0.8862 | -0.58742 | 26.0998 | 1.2366 | 0.1374 | 350.4881 | 30.52 | 28.75
2021-01-24 19:10 | 1.9115 | 0.49531 | 0.18721 | 0.94852 | 24.1631 | 40.893 | 1.2364 | 0.19523 | 351.6238 | 30.47 | 28.62
2021-01-24 19:15 | 1.4815 | 0.42759 | 0.16646 | 0.82189 | 32.9636 | 26.3182 | 1.2368 | 0.18082 | 351.0269 | 30.44 | 29.37
2021-01-24 19:20 | 1.1656 | 0.43732 | 0.15197 | 0.82231 | 19.8854 | 8.5744 | 1.2375 | 0.12302 | 351.3956 | 30.42 | 30.54
2021-01-24 19:25 | 1.1027 | 0.38182 | 0.1458 | 0.72898 | 10.7385 | 28.5447 | 1.2381 | 0.13032 | 351.793 | 30.38 | 31.71
2021-01-24 19:30 | 1.0273 | 0.42011 | 0.16047 | 0.80444 | 28.5818 | 26.3395 | 1.2388 | 0.1304 | 351.1215 | 30.33 | 33.14
2021-01-24 19:35 | 1.1042 | 0.4585 | 0.1585 | 0.86131 | 23.708 | 33.9832 | 1.2324 | 0.13774 | 350.9445 | 30.27 | 34.85
2021-01-24 19:40 | 1.0415 | 0.49968 | 0.18157 | 0.94957 | 26.7324 | 19.4879 | 1.2333 | 0.13784 | 349.6989 | 30.23 | 36.55
2021-01-24 19:45 | 1.004 | 0.54361 | 0.16916 | 1.0024 | 17.1729 | 16.329 | 1.2341 | 0.13793 | 350.0274 | 30.19 | 38.19
2021-01-24 19:50 | 1.5766 | 0.62017 | 0.19221 | 1.1428 | 22.2457 | 22.2253 | 1.2347 | 0.1743 | 351.9971 | 30.16 | 39.22
2021-01-24 19:55 | 2.2764 | 0.59168 | 0.19644 | 1.1034 | 26.7069 | 18.2624 | 1.2349 | 0.18161 | 349.8704 | 30.13 | 39.8
2021-01-24 20:00 | 2.2647 | 0.446 | 0.17143 | 0.85298 | 9.3845 | 28.7335 | 1.2355 | 0.14535 | 350.2771 | 30.1 | 40.84
2021-01-24 20:05 | 2.3544 | 0.47477 | 0.15684 | 0.88459 | 3.5838 | 19.1305 | 1.2285 | 0.1672 | 350.5769 | 30.06 | 41.62
2021-01-24 20:10 | 3.4375 | 0.5937 | 0.19875 | 1.1088 | 6.0195 | 31.1161 | 1.229 | 0.18181 | 349.453 | 30.01 | 42.66
2021-01-24 20:15 | 1.8721 | 0.58295 | 0.18625 | 1.0819 | 1.2124 | 2.649 | 1.2221 | 0.14549 | 350.924 | 30 | 43.36
2021-01-24 20:20 | 1.5919 | 0.5024 | 0.1695 | 0.93959 | 15.1192 | 45.439 | 1.2294 | 0.11639 | 350.4557 | 29.96 | 43.42
2021-01-24 20:25 | 1.1842 | 0.48456 | 0.16529 | 0.90804 | 22.7868 | 53.2133 | 1.2219 | 0.12364 | 350.5871 | 29.9 | 43.16
2021-01-24 20:30 | 1.5021 | 0.40802 | 0.16943 | 0.79485 | 10.703 | 14.5728 | 1.2143 | 0.12361 | 349.7183 | 29.83 | 42.72
2021-01-24 20:35 | 1.6673 | 0.37521 | 0.15058 | 0.72571 | 4.3375 | 31.2996 | 1.2214 | 0.12359 | 350.3288 | 29.8 | 42.43
2021-01-24 20:40 | 1.1962 | 0.3356 | 0.17147 | 0.68379 | -1.8223 | 13.6217 | 1.2212 | 0.1163 | 350.4105 | 29.77 | 42.19
2021-01-24 20:45 | 1.2725 | 0.30148 | 0.16101 | 0.62312 | -2.0768 | 27.4052 | 1.2211 | 0.10176 | 350.9929 | 29.73 | 42.19
2021-01-24 20:50 | 1.1452 | 0.29874 | 0.161 | 0.61892 | 4.8049 | 14.6385 | 1.2211 | 0.12356 | 351.0431 | 29.7 | 42.16
2021-01-24 20:55 | 1.1961 | 0.30829 | 0.15055 | 0.62311 | 4.0923 | 14.4046 | 1.2211 | 0.10903 | 349.4966 | 29.68 | 42.24
2021-01-24 21:00 | 1.9726 | 0.42157 | 0.15057 | 0.79677 | -5.5488 | 8.2469 | 1.2285 | 0.15993 | 349.9461 | 29.7 | 42.52
2021-01-24 21:05 | 1.7823 | 0.28932 | 0.11087 | 0.55644 | -1.1508 | 1.0897 | 1.2289 | 0.15998 | 349.8264 | 29.71 | 43.22
2021-01-24 21:10 | 1.5791 | 0.30853 | 0.10882 | 0.58174 | 2.9137 | 27.7621 | 1.2221 | 0.14548 | 351.3418 | 29.65 | 44.16
2021-01-24 21:15 | 2.4201 | 0.37549 | 0.13395 | 0.70952 | 0.23436 | 8.6103 | 1.2296 | 0.16734 | 350.8061 | 29.61 | 44.67
2021-01-24 21:20 | 0.92977 | 0.26488 | 0.1172 | 0.52113 | 5.1762 | 17.8414 | 1.2222 | 0.13095 | 350.334 | 29.58 | 44.65
2021-01-24 21:25 | 0.85348 | 0.32091 | 0.1235 | 0.61749 | 3.3222 | 25.8542 | 1.2224 | 0.13097 | 351.3685 | 29.54 | 45.12
2021-01-24 21:30 | 0.99378 | 0.32643 | 0.1298 | 0.63016 | 1.9366 | -3.914 | 1.2226 | 0.11644 | 351.3548 | 29.5 | 45.63
2021-01-24 21:35 | 0.49695 | 0.40706 | 0.12353 | 0.74749 | 9.1336 | 10.7239 | 1.2155 | 0.11645 | 350.8046 | 29.49 | 45.93
2021-01-24 21:40 | 0.64994 | 0.31695 | 0.11308 | 0.59891 | 8.6149 | 1.6006 | 1.2156 | 0.094631 | 352.3921 | 29.43 | 46.4
2021-01-24 21:45 | 0.59913 | 0.33617 | 0.10054 | 0.61583 | 7.9034 | 12.2478 | 1.216 | 0.087376 | 350.7994 | 29.37 | 47.23
2021-01-24 21:50 | 0.31878 | 0.22281 | 0.083811 | 0.42534 | 4.8862 | 14.118 | 1.2163 | 0.080118 | 349.1936 | 29.32 | 48.05
2021-01-24 21:55 | 0.25506 | 0.2119 | 0.096396 | 0.42121 | 8.2435 | 4.0402 | 1.2165 | 0.087414 | 350.2652 | 29.25 | 48.6
2021-01-24 22:00 | 0.38259 | 0.16952 | 0.079632 | 0.34158 | 1.8772 | 9.4168 | 1.2165 | 0.072845 | 350.8687 | 29.18 | 48.79
2021-01-24 22:05 | 0.65048 | 0.23107 | 0.075449 | 0.42964 | -5.061 | 11.6933 | 1.2167 | 0.087424 | 351.4076 | 29.13 | 49.21
2021-01-24 22:10 | 0.68885 | 0.15863 | 0.090134 | 0.33119 | -0.081641 | -0.10205 | 1.2168 | 0.080151 | 350.3112 | 29.13 | 49.58
2021-01-24 22:15 | 0.24235 | 0.17092 | 0.083838 | 0.34583 | 6.5103 | 21.3267 | 1.2167 | 0.072858 | 351.4557 | 29.07 | 49.53
2021-01-24 22:20 | 0.48471 | 0.22562 | 0.081743 | 0.42758 | 15.0718 | 22.776 | 1.2167 | 0.080145 | 350.9642 | 29.04 | 49.65
2021-01-24 22:25 | 0.15306 | 0.22151 | 0.079645 | 0.41919 | 14.3062 | 23.4593 | 1.2167 | 0.072857 | 350.4842 | 29.01 | 49.69
2021-01-24 22:30 | 0.3189 | 0.20375 | 0.075458 | 0.38777 | 3.8166 | 11.1334 | 1.2168 | 0.10201 | 352.1076 | 28.94 | 50.05
2021-01-24 22:35 | 0.20411 | 0.21881 | 0.071272 | 0.40667 | 4.4191 | -6.5112 | 1.2169 | 0.080155 | 351.0686 | 28.91 | 50.35
2021-01-24 22:40 | 1.6328 | 0.12718 | 0.071268 | 0.26621 | 5.5107 | 14.3585 | 1.2168 | 0.10201 | 351.1951 | 28.82 | 50.46
2021-01-24 22:45 | 1.4035 | 0.33647 | 0.083861 | 0.59961 | -2.8069 | 4.2155 | 1.2244 | 0.13118 | 352.2397 | 28.76 | 51.12
2021-01-24 22:50 | 0.4849 | 0.30641 | 0.083872 | 0.55355 | -4.41 | 6.7988 | 1.2245 | 0.094754 | 350.6056 | 28.78 | 51.38
2021-01-24 22:55 | 0.72742 | 0.17511 | 0.073396 | 0.34391 | -3.1853 | 13.2417 | 1.2174 | 0.080185 | 350.8188 | 28.71 | 51.8
2021-01-24 23:00 | 0.45944 | 0.21343 | 0.067107 | 0.39426 | -7.5349 | -2.6546 | 1.2174 | 0.072898 | 350.8745 | 28.65 | 52.08
2021-01-24 23:05 | 0.48493 | 0.067032 | 0.056617 | 0.15727 | -3.665 | 7.034 | 1.2173 | 0.051025 | 351.0324 | 28.54 | 52.2
2021-01-24 23:10 | 0.30626 | 0.11354 | 0.056615 | 0.22856 | -6.7683 | 3.4199 | 1.2173 | 0.065601 | 351.672 | 28.45 | 52.38
2021-01-24 23:15 | 1.5186 | 0.26676 | 0.092265 | 0.49907 | -7.2586 | -1.6334 | 1.2173 | 0.10934 | 351.17 | 28.42 | 52.58
2021-01-24 23:20 | 0.68915 | 0.29551 | 0.065009 | 0.51797 | -8.229 | 10.618 | 1.232 | 0.080186 | 351.0685 | 28.49 | 52.51
2021-01-24 23:25 | 0.3318 | 0.17648 | 0.065006 | 0.33342 | -2.4706 | 11.9855 | 1.2319 | 0.072893 | 351.1204 | 28.46 | 52.48
2021-01-24 23:30 | 0.40847 | 0.1902 | 0.069217 | 0.36077 | -3.0226 | 0.20423 | 1.2395 | 0.080202 | 351.0924 | 28.41 | 53.25
2021-01-24 23:35 | 0.29366 | 0.20941 | 0.065039 | 0.38604 | -6.9764 | 6.2818 | 1.2471 | 0.087516 | 351.5219 | 28.41 | 53.91
2021-01-24 23:40 | 0.089389 | 0.11225 | 0.058753 | 0.23082 | 1.3791 | 1.706 | 1.24 | 0.058353 | 350.4258 | 28.41 | 54.29
2021-01-24 23:45 | 0.34479 | 0.16017 | 0.056656 | 0.30007 | -5.2715 | -0.83772 | 1.2473 | 0.05106 | 352.5405 | 28.38 | 54.43
2021-01-24 23:50 |  | 0.12457 | 0.056654 | 0.2476 | -3.79 | 11.891 | 1.2327 | 0.051058 | 351.0359 | 28.34 | 54.46
2021-01-24 23:55 | 0.42139 | 0.094454 | 0.052457 | 0.19724 | -2.891 | 3.5755 | 1.2473 | 0.058352 | 352.1626 | 28.27 | 54.67
2021-01-25 | 0.88113 | 0.083505 | 0.067147 | 0.19515 | 1.1646 | 10.5224 | 1.2473 | 0.058354 | 352.1859 | 28.24 | 54.85
2021-01-25 00:05 | 0.40861 | 0.042434 | 0.041964 | 0.10701 | 0.12258 | 13.8007 | 1.2399 | 0.036468 | 351.2506 | 28.17 | 54.88
2021-01-25 00:10 | 0.6129 | 0.035589 | 0.039865 | 0.094418 | -3.6978 | 0.41882 | 1.2399 | 0.043761 | 351.3489 | 28.09 | 55.1
2021-01-25 00:15 | 0.85557 | 0.06297 | 0.044065 | 0.14269 | 3.0239 | -0.91942 | 1.2473 | 0.051058 | 352.3909 | 28.07 | 55.35
2021-01-25 00:20 | 0.63852 | 0.061604 | 0.048264 | 0.14269 | -4.3624 | 2.2272 | 1.2401 | 0.051061 | 351.3636 | 28.04 | 55.58
2021-01-25 00:25 | 0.74071 | 0.061607 | 0.046167 | 0.1406 | -4.0254 | 5.4864 | 1.2401 | 0.043768 | 350.8744 | 28 | 55.81
2021-01-25 00:30 | 0.48536 | 0.065723 | 0.05247 | 0.15321 | -12.2005 | 0.82767 | 1.233 | 0.043774 | 351.417 | 27.94 | 56.37
2021-01-25 00:35 | 0.79198 | 0.035603 | 0.050376 | 0.10285 | -8.3592 | -0.8584 | 1.2404 | 0.036482 | 352.9858 | 27.91 | 56.71
2021-01-25 00:40 | 0.57481 | 0.03971 | 0.050374 | 0.11124 | -9.2275 | 0.55181 | 1.2404 | 0.05837 | 351.1471 | 27.85 | 56.77
2021-01-25 00:45 | 0.52371 | 0.042449 | 0.03988 | 0.10495 | -11.302 | -8.1137 | 1.2404 | 0.051074 | 350.6361 | 27.84 | 56.81
2021-01-25 00:50 | 0.72806 | 0.050663 | 0.044076 | 0.12173 | -0.90944 | 7.0609 | 1.2403 | 0.051072 | 351.205 | 27.81 | 56.82
2021-01-25 00:55 | 0.44706 | 0.045186 | 0.050373 | 0.11964 | -4.1896 | 6.1004 | 1.2403 | 0.043776 | 351.2399 | 27.78 | 56.92
2021-01-25 01:00 | 0.2427 | 0.036972 | 0.052474 | 0.10915 | 8.7883 | 8.1752 | 1.2477 | 0.043778 | 351.5632 | 27.79 | 57.08
2021-01-25 01:05 |  |  |  |  | 0.67454 | 1.8499 |  |  | 351.5431 | 27.77 | 57.47
2021-01-25 01:10 |  |  |  |  | -6.6534 | -4.5685 |  |  | 350.1908 | 27.73 | 57.56
2021-01-25 01:15 |  |  |  |  | -3.4133 | -17.5263 |  |  | 351.8443 | 27.68 | 57.51
2021-01-25 01:20 |  |  |  |  | -12.7938 | 9.299 |  |  | 351.418 | 27.62 | 57.52
2021-01-25 01:25 |  |  |  |  | -8.9923 | -7.0099 |  |  | 350.9349 | 27.59 | 57.59
2021-01-25 01:30 |  |  |  |  | -7.8988 | -9.0637 |  |  | 352.5192 | 27.58 | 57.58
2021-01-25 01:35 |  |  |  |  | -13.6926 | -1.2364 |  |  | 351.9644 | 27.61 | 57.46
2021-01-25 01:40 |  |  |  |  | -8.9915 | -1.1239 |  |  | 353.5579 | 27.61 | 57.26
2021-01-25 01:45 |  |  |  |  | -3.668 | -5.691 |  |  | 352.0262 | 27.59 | 57.24
2021-01-25 01:50 |  |  |  |  | -1.2057 | 3.7908 |  |  | 353.0711 | 27.57 | 57.48
2021-01-25 01:55 | 0.58765 | 0.11093 | 0.046182 | 0.21412 | -7.3073 | -7.7059 |  |  | 350.8965 | 27.58 | 58
2021-01-25 02:00 | 0.39604 | 0.069845 | 0.046183 | 0.15324 | 1.206 | -4.2108 |  |  | 350.9116 | 27.56 | 58.13
2021-01-25 02:05 | 0.38328 | 0.052044 | 0.044086 | 0.12386 | -3.3729 | 5.4375 |  |  | 350.9405 | 27.52 | 58.4
2021-01-25 02:10 | 0.20442 | 0.049306 | 0.037789 | 0.11337 | -5.274 | 4.814 |  |  | 352.5155 | 27.51 | 58.46
2021-01-25 02:15 | 0.62607 | 0.032872 | 0.052487 | 0.10288 | -3.7513 | -7.5435 |  |  | 350.9752 | 27.47 | 58.75
2021-01-25 02:20 | 0.56224 | 0.061641 | 0.033595 | 0.12808 | -1.6254 | 8.8731 |  |  | 351.5109 | 27.43 | 59.14
2021-01-25 02:25 | 0.11501 | 0.28082 | 0.067193 | 0.49555 | -5.8782 | -7.5138 |  |  | 351.972 | 27.47 | 59.11
2021-01-25 02:30 | 1.4186 | 0.54389 | 0.0735 | 0.9072 | -3.4659 | -3.4761 |  |  | 351.8772 | 27.52 | 59.21
2021-01-25 02:35 | 0.33227 | 0.22468 | 0.073498 | 0.41789 | 1.1042 | 4.4166 |  |  | 351.8729 | 27.53 | 59.12
2021-01-25 02:40 | 0.42171 | 0.21782 | 0.058796 | 0.39058 | 3.7929 | -3.0057 |  |  | 353.4992 | 27.49 | 59.16
2021-01-25 02:45 | 0.28118 | 0.29594 | 0.075605 | 0.52923 | 0.6237 | 2.5562 |  |  | 352.8973 | 27.52 | 59.39
2021-01-25 02:50 | 0.29395 | 0.12742 | 0.073503 | 0.26881 | 6.4209 | 16.0932 |  |  | 352.3723 | 27.53 | 59.29
2021-01-25 02:55 | 0.57514 | 0.13427 | 0.067205 | 0.27512 | 6.3291 | 6.0019 |  |  | 351.3642 | 27.49 | 59.51
2021-01-25 03:00 | 0.34508 | 0.1192 | 0.069305 | 0.25202 | 4.4171 | -0.69528 |  |  | 351.3875 | 27.47 | 59.58
2021-01-25 03:05 | 0.28118 | 0.10139 | 0.060905 | 0.21632 | 7.3414 | 11.145 |  |  | 351.9414 | 27.44 | 59.71
2021-01-25 03:10 | 0.34511 | 0.078102 | 0.050408 | 0.17013 | -5.4093 | 6.35 |  |  | 351.4644 | 27.38 | 60.11
2021-01-25 03:15 | 1.0993 | 0.079475 | 0.052509 | 0.17433 | 5.6446 |  |  |  | 352.0368 | 27.33 | 60.35
2021-01-25 03:20 | 0.69023 | 0.12743 | 0.050408 | 0.24574 | -1.1555 | 10.7471 |  |  | 352.5892 | 27.31 | 60.37
2021-01-25 03:25 | 0.60078 | 0.19184 | 0.058812 | 0.35287 | -9.4488 | 10.1033 |  |  | 351.5287 | 27.31 | 60.49
2021-01-25 03:30 | 0.71589 | 0.27683 | 0.077723 | 0.50415 | 1.5954 | -16.3223 |  |  | 352.4684 | 27.37 | 60.54
2021-01-25 03:35 | 1.2145 | 0.26176 | 0.067222 | 0.46635 | -1.8614 | 5.267 |  |  | 351.3926 | 27.39 | 60.53
2021-01-25 03:40 | 0.99715 | 0.22749 | 0.052517 | 0.40123 | -0.051136 | 11.9863 |  |  | 352.3911 | 27.43 | 60.38
2021-01-25 03:45 | 0.76711 | 0.28508 | 0.071429 | 0.50841 | 3.4775 | -8.2438 |  |  | 351.3525 | 27.4 | 60.71
2021-01-25 03:50 | 0.89506 | 0.29608 | 0.086145 | 0.53788 | 2.7312 | 15.4155 |  |  | 352.3444 | 27.41 | 60.98
2021-01-25 03:55 | 0.93348 | 0.3523 | 0.08615 | 0.62616 | 7.6724 | 17.1453 |  |  | 350.756 | 27.41 | 61.15
2021-01-25 04:00 | 0.81848 | 0.66629 | 0.1471 | 1.1705 | 0.53201 | 3.4479 |  |  | 351.1342 | 27.5 | 61.12
2021-01-25 04:05 | 0.98477 | 0.77599 | 0.15761 | 1.3471 | 3.2536 | 12.1344 |  |  | 352.6178 | 27.56 | 60.99
2021-01-25 04:10 | 0.75455 | 0.71566 | 0.15761 | 1.2546 | 7.2233 |  |  |  | 378.6407 | 27.61 | 60.78
2021-01-25 04:15 | 0.95923 | 0.60601 | 0.1345 | 1.0634 |  |  |  |  | 495.4135 | 27.64 | 60.75
2021-01-25 04:20 | 0.83135 | 0.60328 | 0.15342 | 1.0803 |  |  |  |  | 496.0033 | 27.59 | 61
2021-01-25 04:25 | 0.71632 | 0.6102 | 0.14293 | 1.0783 |  | 26.3196 |  |  | 496.0347 | 27.54 | 61.45
2021-01-25 04:30 | 0.95929 | 0.37295 | 0.124 | 0.69567 | 19.0425 | 34.6878 |  |  | 496.2178 | 27.45 | 61.59
2021-01-25 04:35 | 1.855 | 0.58422 | 0.14715 | 1.0427 | 29.6799 | 30.3144 |  |  | 493.4971 | 27.46 | 62.08
2021-01-25 04:40 | 2.0977 | 0.58276 | 0.14923 | 1.0446 | 41.7293 | 33.8296 |  |  | 493.4377 | 27.53 | 61.46
2021-01-25 04:45 | 1.6757 | 0.62528 | 0.16394 | 1.1245 | 53.8153 | 20.4353 |  |  | 493.8835 | 27.57 | 61.37
2021-01-25 04:50 | 1.0105 | 0.639 | 0.17656 | 1.1539 | 48.4439 | 50.4906 |  |  | 494.3292 | 27.61 | 61.28
2021-01-25 04:55 | 0.97228 | 0.71177 | 0.1976 | 1.2886 | 51.9401 | 13.3867 |  |  | 494.2163 | 27.64 | 61.51
2021-01-25 05:00 | 1.228 | 0.73775 | 0.20809 | 1.3389 | 51.2699 | 42.8272 |  |  | 494.1991 | 27.68 | 61.11
2021-01-25 05:05 | 1.3049 | 0.83245 | 0.22913 | 1.5051 | 58.4899 | 28.7486 |  |  | 493.0782 | 27.7 | 61.28
2021-01-25 05:10 | 1.791 | 0.83379 | 0.24594 | 1.524 | 65.9177 | 59.8694 |  |  | 492.0041 | 27.73 | 61.08
2021-01-25 05:15 | 1.8294 | 0.98332 | 0.24385 | 1.7511 | 73.7707 | 51.357 |  |  | 492.3882 | 27.8 | 60.95
2021-01-25 05:20 | 2.2132 | 1.6114 | 0.28168 | 2.7517 | 77.5863 | 89.8879 |  |  | 491.8301 | 27.83 | 60.78
2021-01-25 05:25 | 3.0576 | 2.2286 | 0.37419 | 3.7902 | 112.4164 | 98.9272 |  |  | 493.2172 | 27.93 | 60.49
2021-01-25 05:30 | 2.4824 | 1.8655 | 0.34693 | 3.2044 | 123.9967 | 112.5521 |  |  | 491.8619 | 28.06 | 60.56
2021-01-25 05:35 | 2.7512 | 2.2606 | 0.46469 | 3.932 | 115.4316 | 118.6665 |  |  | 492.2879 | 28.11 | 60.45
2021-01-25 05:40 | 3.711 | 2.5063 | 0.47732 | 4.3169 | 118.4866 | 73.1558 |  |  | 492.155 | 28.18 | 60.3
2021-01-25 05:45 | 3.6601 | 2.1978 | 0.43109 | 3.7999 | 127.1153 | 117.2765 |  |  | 492.5267 | 28.25 | 60.23
2021-01-25 05:50 | 3.622 | 2.2144 | 0.38276 | 3.7792 | 144.1932 | 111.0194 |  |  | 490.2621 | 28.34 | 60.11
2021-01-25 05:55 | 3.878 | 2.4298 | 0.45847 | 4.183 | 141.7261 | 123.8798 |  |  | 490.098 | 28.44 | 59.77
2021-01-25 06:00 | 3.2892 | 2.674 | 0.4837 | 4.5825 | 152.3227 | 122.5176 |  |  | 491.9993 | 28.55 | 59.38
2021-01-25 06:05 | 3.4175 | 2.7977 | 0.5216 | 4.8122 | 153.9323 | 90.5388 |  |  | 491.2613 | 28.66 | 59.2
2021-01-25 06:10 | 3.9804 | 2.7509 | 0.51315 | 4.7298 | 147.7367 | 143.9074 |  |  | 492.2217 | 28.73 | 58.78
2021-01-25 06:15 | 3.4681 | 2.1292 | 0.45423 | 3.7179 | 150.0082 | 112.1683 |  |  | 492.7146 | 28.77 | 58.45
2021-01-25 06:20 | 2.6745 | 1.8122 | 0.40163 | 3.1794 | 132.1853 | 85.2059 |  |  | 492.1783 | 28.8 | 58.19
2021-01-25 06:25 | 2.3419 | 1.6325 | 0.40164 | 2.904 | 116.4847 | 76.0662 |  |  | 491.6281 | 28.81 | 58.23
2021-01-25 06:30 | 2.3292 | 1.6216 | 0.40586 | 2.8894 | 106.9377 | 67.2648 |  |  | 492.0191 | 28.86 | 58.23
2021-01-25 06:35 | 2.5084 | 1.6354 | 0.37853 | 2.8853 | 115.1302 | 94.633 |  |  | 490.8511 | 28.95 | 57.91
2021-01-25 06:40 | 2.8024 | 1.5775 | 0.389 | 2.8071 | 117.0619 | 80.9248 |  |  | 491.3204 | 29 | 57.52
2021-01-25 06:45 | 3.6599 | 1.7532 | 0.40373 | 3.0911 | 107.513 | 61.5881 |  |  | 492.2832 | 29.04 | 57.44
2021-01-25 06:50 | 4.7088 | 1.8079 | 0.38057 | 3.1497 | 113.5532 | 89.4975 |  |  | 491.207 | 29.09 | 57.06
2021-01-25 06:55 | 5.2078 | 2.0712 | 0.38897 | 3.5638 | 112.2525 | 78.7283 |  |  | 490.6581 | 29.11 | 56.98
2021-01-25 07:00 | 4.3236 | 1.9513 | 0.33001 | 3.3211 | 115.0035 | 110.9613 |  |  | 490.1997 | 29.16 | 56.12
2021-01-25 07:05 | 4.9251 | 2.1804 | 0.36365 | 3.7059 | 109.421 | 74.8713 |  |  | 491.086 | 29.24 | 55.97
2021-01-25 07:10 | 5.0767 | 1.7821 | 0.38453 | 3.1141 | 118.9554 | 49.5545 |  |  | 491.14 | 29.32 | 54.82
2021-01-25 07:15 | 5.1397 | 1.5392 | 0.32984 | 2.6891 | 100.1553 | 84.9459 |  |  | 492.6706 | 29.39 | 54.18
2021-01-25 07:20 | 4.7174 | 1.7309 | 0.32351 | 2.9788 | 98.429 | 48.0588 |  |  | 491.1689 | 29.38 | 54.02
2021-01-25 07:25 | 4.5511 | 1.9625 | 0.35921 | 3.3695 | 119.546 | 111.3438 |  |  | 491.6018 | 29.44 | 53.78
2021-01-25 07:30 | 5.9957 | 2.2818 | 0.40333 | 3.9009 | 120.7015 | 97.9357 |  |  | 491.5052 | 29.5 | 53.59
2021-01-25 07:35 | 5.1905 | 2.2586 | 0.39074 | 3.8528 | 115.8269 | 84.7556 |  |  | 490.3215 | 29.58 | 53.42
2021-01-25 07:40 | 4.257 | 1.8761 | 0.39492 | 3.2707 | 116.0363 | 41.2355 |  |  | 488.7716 | 29.59 | 53.28
2021-01-25 07:45 | 3.9755 | 1.9801 | 0.48732 | 3.5247 | 128.2705 | 70.6035 |  |  | 489.7896 | 29.62 | 53.05
2021-01-25 07:50 | 3.9617 | 1.8289 | 0.40319 | 3.2067 | 120.968 | 101.645 |  |  | 489.8685 | 29.65 | 52.35
2021-01-25 07:55 | 4.6774 | 1.9221 | 0.4032 | 3.3495 | 127.7066 | 83.6825 |  |  | 490.886 | 29.66 | 52.34
2021-01-25 08:00 | 3.834 | 1.6372 | 0.3612 | 2.8707 | 118.8333 | 91.5046 |  |  | 490.8006 | 29.71 | 52.21
2021-01-25 08:05 | 3.8848 | 1.6644 | 0.38217 | 2.9335 | 108.9791 | 65.5715 |  |  | 490.2389 | 29.76 | 51.88
2021-01-25 08:10 | 3.3218 | 1.6805 | 0.38628 | 2.9622 | 104.5077 | 53.5877 |  |  | 491.3423 | 29.79 | 51.25
2021-01-25 08:15 | 3.143 | 1.5477 | 0.33171 | 2.704 | 99.4101 | 64.8629 |  |  | 490.7785 | 29.81 | 51.25
2021-01-25 08:20 | 3.9602 | 1.5283 | 0.33586 | 2.6806 | 101.2984 | 48.9732 |  |  | 490.2729 | 29.84 | 50.87
2021-01-25 08:25 | 3.3855 | 1.8009 | 0.37787 | 3.1384 | 111.4731 | 64.2859 |  |  | 490.1333 | 29.91 | 50.79
2021-01-25 08:30 | 4.3442 | 1.8272 | 0.39261 | 3.1934 | 106.2754 | 50.0661 |  |  | 488.4775 | 29.93 | 51.05
2021-01-25 08:35 | 4.0123 | 1.8876 | 0.40524 | 3.2986 | 116.2592 | 93.8006 |  |  | 490.9419 | 29.99 | 51.02
2021-01-25 08:40 | 3.9617 | 1.8508 | 0.44309 | 3.2822 | 108.8928 | 37.1734 |  |  | 489.2683 | 30.04 | 51.12
2021-01-25 08:45 | 2.9909 | 1.6963 | 0.42215 | 3.0223 | 105.6578 | 49.8482 |  |  | 490.1806 | 30.07 | 51.38
2021-01-25 08:50 | 2.7734 | 1.5578 | 0.45152 | 2.8393 | 95.0156 | 32.7284 |  |  | 489.1861 | 30.07 | 51.19
2021-01-25 08:55 | 3.1822 | 1.4084 | 0.3843 | 2.5431 | 102.3312 | 75.5752 |  |  | 489.1617 | 30.1 | 50.99
2021-01-25 09:00 | 3.8466 | 1.274 | 0.36958 | 2.3225 | 115.9953 | 97.4704 |  |  | 491.1578 | 30.16 | 50.71
2021-01-25 09:05 | 4.2678 | 1.2712 | 0.35274 | 2.2991 | 107.3337 | 42.9846 |  |  | 490.1152 | 30.2 | 50.33
2021-01-25 09:10 | 3.6031 | 1.3601 | 0.34222 | 2.4291 | 80.1462 | 50.4632 |  |  | 489.589 | 30.23 | 50.06
2021-01-25 09:15 | 3.2702 | 1.4009 | 0.35264 | 2.5 | 88.2548 | 15.5131 |  |  | 490.1386 | 30.27 | 49.5
2021-01-25 09:20 | 3.2947 | 1.254 | 0.33574 | 2.26 | 88.2566 | 68.417 |  |  | 489.7168 | 30.31 | 48.65
2021-01-25 09:25 | 3.7922 | 1.3797 | 0.3315 | 2.4485 | 74.3838 | 20.3886 |  |  | 489.1819 | 30.36 | 48.22
2021-01-25 09:30 | 3.3326 | 1.4085 | 0.38816 | 2.5471 | 84.3136 | 51.9529 |  |  | 491.6987 | 30.4 | 48.14
2021-01-25 09:35 | 3.8432 | 1.3085 | 0.37975 | 2.3855 | 71.8693 | 49.949 |  |  | 489.5814 | 30.44 | 47.95
2021-01-25 09:40 | 4.3282 | 1.4015 | 0.38603 | 2.5344 | 76.9325 | 45.1054 |  |  | 489.5212 | 30.49 | 47.72
2021-01-25 09:45 | 3.8548 | 1.5216 | 0.36705 | 2.6973 | 78.5865 | 43.8067 |  |  | 488.5693 | 30.52 | 47.04
2021-01-25 09:50 | 3.1415 | 1.2362 | 0.36303 | 2.2579 | 69.696 | 11.9736 |  |  | 489.833 | 30.55 | 48.05
2021-01-25 09:55 | 3.5295 | 1.5066 | 0.39926 | 2.7087 | 104.9555 | 61.7415 |  |  | 487.0061 | 30.6 | 50.99
2021-01-25 10:00 | 3.4802 | 1.4992 | 0.49197 | 2.79 | 109.995 | 58.2013 |  |  | 488.2853 | 30.61 | 52.11
2021-01-25 10:05 | 3.6987 | 1.4776 | 0.52995 | 2.7928 | 119.7597 | 101.2792 |  |  | 487.0974 | 30.63 | 52.61
2021-01-25 10:10 | 3.238 | 1.206 | 0.43323 | 2.2818 | 104.395 | 26.1602 |  |  | 487.5979 | 30.63 | 52.68
2021-01-25 10:15 | 3.2638 | 1.4009 | 0.36385 | 2.5112 | 89.493 | 55.6822 |  |  | 488.5988 | 30.63 | 52.82
2021-01-25 10:20 | 2.931 | 1.7041 | 0.37646 | 2.9885 | 80.5104 | 27.2976 |  |  | 488.0823 | 30.64 | 52.72
2021-01-25 10:25 | 3.3019 | 1.7355 | 0.48159 | 3.1419 | 67.8611 | 51.7661 |  |  | 489.5945 | 30.68 | 52.47
2021-01-25 10:30 | 3.4678 | 1.3745 | 0.51306 | 2.62 | 72.5295 | 55.1572 |  |  | 489.1497 | 30.68 | 52.15
2021-01-25 10:35 | 3.5187 | 1.325 | 0.44994 | 2.481 | 73.8546 | 27.6686 |  |  | 488.1075 | 30.71 | 51.89
2021-01-25 10:40 | 3.3389 | 1.4646 | 0.44564 | 2.6928 | 82.6306 | 86.0693 |  |  | 489.7398 | 30.72 | 51.41
2021-01-25 10:45 | 5.832 | 1.5273 | 0.43713 | 2.7783 | 85.9968 | 32.8537 |  |  | 487.7322 | 30.76 | 50.75
2021-01-25 10:50 | 4.6943 | 1.6139 | 0.47712 | 2.9531 | 73.769 | 48.3402 |  |  | 487.5591 | 30.83 | 50.82
2021-01-25 10:55 | 4.0172 | 1.1767 | 0.45198 | 2.2557 | 79.2382 | 51.1231 |  |  | 488.9491 | 30.87 | 51.12
2021-01-25 11:00 | 3.9542 | 0.93145 | 0.37219 | 1.7999 | 95.1455 | 61.6183 |  |  | 488.3166 | 30.87 | 51.64
2021-01-25 11:05 | 3.8911 | 1.0579 | 0.36807 | 1.9876 | 87.2844 | 48.1887 |  |  | 487.1324 | 30.89 | 52.12
2021-01-25 11:10 | 3.4691 | 1.6097 | 0.39966 | 2.867 | 82.48 | 50.4056 |  |  | 488.034 | 30.94 | 52.19
2021-01-25 11:15 | 3.1631 | 1.6694 | 0.47768 | 3.0344 | 79.0705 | 57.9864 |  |  | 487.7278 | 31.01 | 52.84
2021-01-25 11:20 | 3.0223 | 1.3468 | 0.44823 | 2.5147 | 87.2374 | 52.6601 |  |  | 487.7257 | 31.02 | 52.8
2021-01-25 11:25 | 4.355 | 1.3717 | 0.44621 | 2.5488 | 81.71 | 93.863 |  |  | 487.0887 | 31.04 | 53.14
2021-01-25 11:30 | 4.8795 | 1.2768 | 0.39564 | 2.3528 | 91.9553 | 35.0404 |  |  | 488.647 | 31.07 | 52.77
2021-01-25 11:35 | 4.3549 | 1.0229 | 0.36832 | 1.9363 | 69.0229 | 42.0121 |  |  | 487.0495 | 31.07 | 53.01
2021-01-25 11:40 | 3.6494 | 1.0638 | 0.38084 | 2.0115 | 70.4675 | 42.7886 |  |  | 486.7098 | 31.05 | 52.44
2021-01-25 11:45 | 3.1114 | 1.1832 | 0.3724 | 2.186 | 76.1285 | 68.5689 |  |  | 486.7188 | 31.06 | 52.3
2021-01-25 11:50 | 3.0972 | 1.2663 | 0.41639 | 2.3554 | 87.9489 | 54.7454 |  |  | 487.9453 | 31.08 | 51.23
2021-01-25 11:55 | 4.2743 | 1.5187 | 0.4458 | 2.7736 | 100.5248 | 61.3039 |  |  | 487.4015 | 31.12 | 50.96
2021-01-25 12:00 | 4.1335 | 1.3924 | 0.4458 | 2.5802 | 105.8266 | 94.0943 |  |  | 488.3247 | 31.19 | 50.73
2021-01-25 12:05 | 3.4683 | 1.2458 | 0.47528 | 2.3848 | 112.9118 | 64.7082 |  |  | 487.2003 | 31.22 | 50.85
2021-01-25 12:10 | 2.6244 | 1.0444 | 0.43965 | 2.0405 | 87.0932 | 48.7697 |  |  | 487.0994 | 31.2 | 51.49
2021-01-25 12:15 | 3.0484 | 1.1589 | 0.41463 | 2.191 | 88.1435 | 29.7364 |  |  | 487.2754 | 31.25 | 52.47
2021-01-25 12:20 | 3.3812 | 1.2137 | 0.4209 | 2.2792 | 69.57 | 45.7379 |  |  | 487.319 | 31.25 | 52.28
2021-01-25 12:25 | 2.7667 | 1.3305 | 0.43988 | 2.4814 | 75.4784 | 39.8398 |  |  | 485.6697 | 31.29 | 52.35
2021-01-25 12:30 | 2.9721 | 1.3802 | 0.48206 | 2.5976 | 93.4464 | 79.7543 |  |  | 484.5071 | 31.34 | 52.5
2021-01-25 12:35 | 3.0622 | 1.3185 | 0.48212 | 2.5011 | 85.7197 | 52.4076 |  |  | 486.45 | 31.37 | 52.68
2021-01-25 12:40 | 3.536 | 1.3528 | 0.4863 | 2.5578 | 85.6222 | 48.4379 |  |  | 485.3901 | 31.41 | 52.43
2021-01-25 12:45 | 6.9705 | 1.4931 | 0.50743 | 2.794 | 87.3881 | 60.1004 |  |  | 485.2367 | 31.46 | 52.6
2021-01-25 12:50 | 4.3315 | 1.4315 | 0.45274 | 2.6469 | 80.765 | 33.8008 |  |  | 486.1431 | 31.5 | 52.72
2021-01-25 12:55 | 3.845 | 1.3327 | 0.44227 | 2.483 | 92.5052 | 62.7707 |  |  | 486.0484 | 31.52 | 52.93
2021-01-25 13:00 | 4.2292 | 1.1472 | 0.38537 | 2.1438 | 75.2944 | 8.7761 |  |  | 487.1431 | 31.5 | 52.83
2021-01-25 13:05 | 5.2542 | 1.2089 | 0.42537 | 2.2764 | 88.1686 | 70.7707 |  |  | 486.1338 | 31.5 | 52.76
2021-01-25 13:10 | 4.5362 | 1.0838 | 0.43797 | 2.0993 | 91.482 | 10.4973 |  |  | 487.1877 | 31.51 | 52.54
2021-01-25 13:15 | 3.3303 | 0.86644 | 0.40201 | 1.7301 | 70.7772 | 41.7982 |  |  | 486.8839 | 31.5 | 51.74
2021-01-25 13:20 | 4.7629 | 1.1049 | 0.39552 | 2.0891 | 80.8253 | 41.821 |  |  | 485.5714 | 31.49 | 50.86
2021-01-25 13:25 | 4.9035 | 1.4809 | 0.45862 | 2.7286 | 91.5458 | 44.4926 |  |  | 487.596 | 31.52 | 50.69
2021-01-25 13:30 | 4.2616 | 1.5832 | 0.5047 | 2.9315 | 117.5954 | 81.3728 |  |  | 487.265 | 31.53 | 49.81
2021-01-25 13:35 | 3.6614 | 1.4273 | 0.51329 | 2.7011 | 131.8727 | 54.9777 |  |  | 486.5167 | 31.57 | 50.43
2021-01-25 13:40 | 3.112 | 1.3811 | 0.46296 | 2.5778 | 113.9565 | 48.8487 |  |  | 487.3504 | 31.59 | 51.06
2021-01-25 13:45 | 2.7668 | 1.2907 | 0.43148 | 2.41 | 113.2119 | 13.926 |  |  | 486.1647 | 31.64 | 51.3
2021-01-25 13:50 | 5.8148 | 1.3703 | 0.43355 | 2.534 | 116.2764 | 78.0163 |  |  | 485.1485 | 31.66 | 51.07
2021-01-25 13:55 | 5.8148 | 1.303 | 0.44617 | 2.4434 | 104.9833 | 41.4871 |  |  | 486.661 | 31.68 | 50.98
2021-01-25 14:00 | 4.5084 | 1.6092 | 0.51142 | 2.9801 | 106.6232 | 49.0594 |  |  | 486.1621 | 31.67 | 51.02
2021-01-25 14:05 | 5.7503 | 1.7504 | 0.49664 | 3.1777 | 115.9177 | 42.693 |  |  | 484.6002 | 31.71 | 50.74
2021-01-25 14:10 | 5.6088 | 1.543 | 0.47975 | 2.8428 | 91.2566 | 54.295 |  |  | 485.1041 | 31.75 | 50.39
2021-01-25 14:15 | 4.2249 | 1.3231 | 0.5028 | 2.5329 | 104.3895 | 62.9697 |  |  | 485.7129 | 31.75 | 49.98
2021-01-25 14:20 | 4.9416 | 1.4684 | 0.52801 | 2.7789 | 110.0056 | 60.4053 |  |  | 485.7435 | 31.75 | 49.85
2021-01-25 14:25 | 3.3533 | 1.2938 | 0.51316 | 2.4943 | 112.9167 | 80.5202 |  |  | 486.4094 | 31.73 | 49.39
2021-01-25 14:30 | 3.3649 | 1.2001 | 0.49405 | 2.3336 | 103.879 | 26.1207 |  |  | 484.0377 | 31.72 | 48.67
2021-01-25 14:35 | 4.171 | 1.5622 | 0.56764 | 2.9623 | 109.3875 | 77.0431 |  |  | 485.5358 | 31.74 | 48.65
2021-01-25 14:40 | 3.7355 | 1.4838 | 0.51712 | 2.7916 | 111.522 | 63.2473 |  |  | 485.5533 | 31.77 | 48.29
2021-01-25 14:45 | 3.8379 | 1.6114 | 0.52554 | 2.9956 | 120.4397 | 69.0727 |  |  | 485.5063 | 31.79 | 48.3
2021-01-25 14:50 | 3.4542 | 1.6156 | 0.52135 | 2.9977 | 123.7168 | 66.8734 |  |  | 483.4157 | 31.81 | 48.28
2021-01-25 14:55 | 4.0556 | 1.5141 | 0.52767 | 2.8507 | 109.8834 | 47.0812 |  |  | 484.3763 | 31.84 | 48.27
2021-01-25 15:00 | 6.0006 | 1.6596 | 0.48565 | 3.0316 | 111.8751 | 60.9632 |  |  | 484.3258 | 31.87 | 48.25
2021-01-25 15:05 | 4.3878 | 1.4289 | 0.44984 | 2.6402 | 112.7058 | 57.7191 |  |  | 486.4176 | 31.88 | 47.93
2021-01-25 15:10 | 3.9391 | 1.504 | 0.47495 | 2.7782 | 133.5708 | 73.3898 |  |  | 485.5109 | 31.88 | 47.43
2021-01-25 15:15 | 4.0539 | 1.4819 | 0.51273 | 2.7843 | 128.6195 | 67.6756 |  |  | 485.0571 | 31.88 | 47.23
2021-01-25 15:20 | 4.0532 | 1.3254 | 0.49583 | 2.5275 | 93.1331 | 44.4645 |  |  | 484.1201 | 31.88 | 46.86
2021-01-25 15:25 | 3.6186 | 1.431 | 0.51897 | 2.7125 | 109.147 |  |  |  | 486.1432 | 31.88 | 46.97
2021-01-25 15:30 | 3.7978 | 1.4448 | 0.46436 | 2.679 | 111.1364 | 14.3524 |  |  | 485.0974 | 31.88 | 47.06
2021-01-25 15:35 | 4.1691 | 1.4573 | 0.49804 | 2.7319 | 100.6516 | 45.7117 |  |  | 485.0126 | 31.9 | 47.23
2021-01-25 15:40 | 4.0922 | 1.5436 | 0.46439 | 2.8305 | 119.6648 | 64.6151 |  |  | 486.0455 | 31.91 | 47.1
2021-01-25 15:45 | 3.9511 | 1.6229 | 0.45174 | 2.9395 | 101.1172 | 80.3619 |  |  | 485.006 | 31.95 | 46.79
2021-01-25 15:50 | 3.657 | 1.6161 | 0.44333 | 2.9205 | 88.9026 | 49.1619 |  |  | 485.4904 | 31.97 | 46.72
2021-01-25 15:55 | 4.4236 | 1.3102 | 0.43277 | 2.4412 | 93.4533 | 79.3898 |  |  | 485.0702 | 31.95 | 46.52
2021-01-25 16:00 | 4.3087 | 1.4871 | 0.52102 | 2.8005 | 101.4337 | 42.0995 |  |  | 485.1058 | 31.92 | 46.65
2021-01-25 16:05 | 3.2727 | 1.3375 | 0.41383 | 2.4641 | 90.8683 | 73.6867 |  |  | 485.158 | 31.92 | 46.43
2021-01-25 16:10 | 2.7103 | 1.4788 | 0.38233 | 2.6511 | 105.1186 | 61.6516 |  |  | 486.2286 | 31.88 | 46.61
2021-01-25 16:15 | 2.6335 | 1.3513 | 0.38862 | 2.4599 | 97.864 | 66.0881 |  |  | 484.2431 | 31.85 | 46.62
2021-01-25 16:20 | 3.0299 | 1.3088 | 0.41594 | 2.42 | 110.4964 | 91.1156 |  |  | 485.3236 | 31.81 | 46.76
2021-01-25 16:25 | 5.51 | 1.2883 | 0.40334 | 2.3801 | 115.2021 | 61.5284 |  |  | 485.8314 | 31.81 | 46.78
2021-01-25 16:30 | 5.1266 | 1.4555 | 0.36974 | 2.6008 | 101.725 | 55.3116 |  |  | 484.8096 | 31.8 | 46.86
2021-01-25 16:35 | 4.2192 | 1.5323 | 0.34245 | 2.6913 | 94.0303 | 60.123 |  |  | 486.2639 | 31.83 | 46.93
2021-01-25 16:40 | 3.8353 | 1.4966 | 0.41384 | 2.7099 | 100.3829 | 61.4263 |  |  | 484.827 | 31.81 | 46.74
2021-01-25 16:45 | 4.1161 | 1.2909 | 0.36549 | 2.3441 | 86.8318 | 47.7263 |  |  | 484.4016 | 31.79 | 46.56
2021-01-25 16:50 | 4.5892 | 1.184 | 0.3823 | 2.1972 | 90.2098 | 55.8378 |  |  | 486.4961 | 31.75 | 46.74
2021-01-25 16:55 | 3.6688 | 1.2087 | 0.41171 | 2.2644 | 71.801 | 38.81 |  |  | 484.9645 | 31.75 | 46.72
2021-01-25 17:00 | 2.8376 | 1.2044 | 0.36756 | 2.2138 | 78.472 | 30.7487 |  |  | 485.0393 | 31.73 | 46.59
2021-01-25 17:05 | 2.8758 | 1.0756 | 0.32554 | 1.9742 | 58.5694 | 53.058 |  |  | 486.6844 | 31.68 | 46.6
2021-01-25 17:10 | 2.62 | 0.98233 | 0.32341 | 1.8292 | 46.4492 | 27.3808 |  |  | 487.9054 | 31.58 | 46.71
2021-01-25 17:15 | 2.8244 | 0.796 | 0.27931 | 1.4973 | 43.228 | 33.1878 |  |  | 486.9655 | 31.53 | 46.82
2021-01-25 17:20 | 2.8117 | 0.71792 | 0.31922 | 1.4197 | 17.2793 | 10.6641 |  |  | 485.9614 | 31.51 | 46.92
2021-01-25 17:25 | 2.8505 | 0.8167 | 0.34027 | 1.5921 | 31.0567 | 45.997 |  |  | 487.4047 | 31.52 | 47.23
2021-01-25 17:30 | 3.669 | 0.75648 | 0.29409 | 1.4536 | 45.5823 | 33.0745 |  |  | 485.7551 | 31.56 | 47.33
2021-01-25 17:35 | 4.2827 | 0.75512 | 0.28989 | 1.4474 | 46.3908 | 50.1033 |  |  | 486.8057 | 31.54 | 47.41
2021-01-25 17:40 | 3.8864 | 0.81133 | 0.26889 | 1.5125 | 55.8728 | 58.174 |  |  | 485.4796 | 31.4 | 47.84
2021-01-25 17:45 | 3.3116 | 0.75934 | 0.26683 | 1.4308 | 61.0862 | 52.6372 |  |  | 487.0851 | 31.32 | 48.32
2021-01-25 17:50 | 2.4806 | 0.70454 | 0.27524 | 1.3552 | 51.555 | 43.0852 |  |  | 486.6974 | 31.23 | 48.65
2021-01-25 17:55 | 3.2482 | 0.79924 | 0.26477 | 1.4878 | 53.5371 | 25.0344 |  |  | 485.1831 | 31.17 | 49.13
2021-01-25 18:00 | 2.0207 | 0.56622 | 0.22696 | 1.0949 | 36.5564 | 34.5613 |  |  | 485.7462 | 31.12 | 49.4
2021-01-25 18:05 | 2.2767 | 0.62798 | 0.21858 | 1.1812 | 44.9913 | 17.3028 |  |  | 486.3563 | 31.03 | 49.86
2021-01-25 18:10 | 2.635 | 0.81039 | 0.25432 | 1.4965 | 32.7453 | 33.0421 |  |  | 485.8763 | 30.99 | 50.11
2021-01-25 18:15 | 2.9805 | 1.1368 | 0.29217 | 2.0368 | 34.8345 | 29.0833 |  |  | 486.3668 | 30.99 | 50.21
2021-01-25 18:20 | 2.3664 | 0.88034 | 0.23331 | 1.5827 | 27.8241 | 33.5649 |  |  | 485.9749 | 30.92 | 50.37
2021-01-25 18:25 | 2.0979 | 0.80222 | 0.22492 | 1.4525 | 93.516 | 300.2583 |  |  | 402.7923 | 30.86 | 50.71
2021-01-25 18:30 | 3.4797 | 0.768 | 0.22073 | 1.3979 | 251.7079 | 210.5139 |  |  | 335.5078 | 30.82 | 50.99
2021-01-25 18:35 | 3.8767 | 0.70086 | 0.22495 | 1.2972 | 142.273 | 68.7312 |  |  | 333.9466 | 30.81 | 51.22
2021-01-25 18:40 | 3.5059 | 0.71737 | 0.20184 | 1.3015 | 71.2746 | 39.9826 |  |  | 334.6451 | 30.78 | 51.41
2021-01-25 18:45 | 3.8518 | 0.72432 | 0.19346 | 1.3037 | 28.9823 | 31.4393 |  |  | 335.6739 | 30.74 | 51.8
2021-01-25 18:50 | 2.7642 | 0.75863 | 0.19136 | 1.3542 | 16.1858 | 16.278 |  |  | 334.1155 | 30.75 | 51.82
2021-01-25 18:55 | 2.1886 | 0.70384 | 0.18928 | 1.2681 | 9.0818 | 44.2318 |  |  | 335.127 | 30.73 | 52.12
2021-01-25 19:00 | 3.3661 | 0.66818 | 0.18507 | 1.2093 | -2.8055 | 22.5975 |  |  | 335.1869 | 30.67 | 52.34
2021-01-25 19:05 | 3.3918 | 0.72584 | 0.17456 | 1.2851 | 0.69629 | 44.1732 |  |  | 335.1937 | 30.65 | 52.5
2021-01-25 19:10 | 3.4304 | 0.5077 | 0.16196 | 0.94229 | 6.6765 | 28.918 |  |  | 335.2291 | 30.6 | 52.78
2021-01-25 19:15 | 2.9443 | 0.5942 | 0.20825 | 1.1191 | 4.2602 | 5.909 |  |  | 334.788 | 30.51 | 53.23
2021-01-25 19:20 | 2.9189 | 0.59013 | 0.20616 | 1.1107 | 0.79885 | 34.9447 |  |  | 334.8178 | 30.46 | 53.55
2021-01-25 19:25 | 2.6246 | 0.52154 | 0.17672 | 0.97405 | -6.6677 | 11.7377 |  |  | 335.9131 | 30.38 | 53.93
2021-01-25 19:30 | 1.8695 | 0.49965 | 0.17884 | 0.94472 | -2.018 | 25.4248 |  |  | 335.4215 | 30.32 | 54.41
2021-01-25 19:35 | 1.4598 | 0.46261 | 0.16623 | 0.87324 | 0.70686 | 40.4856 |  |  | 334.9191 | 30.29 | 54.65
2021-01-25 19:40 | 1.1654 | 0.35557 | 0.1473 | 0.69443 | 10.6447 | 32.6 |  |  | 335.9984 | 30.22 | 55.04
2021-01-25 19:45 | 1.3448 | 0.3556 | 0.15153 | 0.69661 | 8.7298 | 33.4538 |  |  | 336.0518 | 30.14 | 55.53
2021-01-25 19:50 | 1.3321 | 0.3927 | 0.14523 | 0.74717 | 8.4332 | 26.601 |  |  | 337.1111 | 30.09 | 55.85
2021-01-25 19:55 | 2.1391 | 0.43941 | 0.13471 | 0.80614 | 7.9315 | 30.5167 |  |  | 334.0455 | 30.06 | 56.05
2021-01-25 20:00 | 2.7414 | 0.48476 | 0.12419 | 0.86725 | 9.0901 | 42.4477 |  |  | 335.5963 | 30.03 | 56.31
2021-01-25 20:05 | 2.2931 | 0.39688 | 0.11578 | 0.72413 | 14.3375 | 34.1272 |  |  | 336.1227 | 30.01 | 56.44
2021-01-25 20:10 | 2.6008 | 0.45872 | 0.13052 | 0.83578 | 9.2245 | 24.3936 |  |  | 335.6206 | 29.97 | 56.79
2021-01-25 20:15 | 2.5498 | 0.62084 | 0.16422 | 1.1159 | 11.2651 | 46.1983 |  |  | 334.5404 | 29.99 | 56.93
2021-01-25 20:20 | 1.9347 | 0.5137 | 0.14106 | 0.92848 | 11.7775 | 38.6126 |  |  | 336.108 | 29.97 | 56.97
2021-01-25 20:25 | 1.7938 | 0.51233 | 0.12211 | 0.90744 | 16.1341 | 12.7105 |  |  | 335.5132 | 29.88 | 57.36
2021-01-25 20:30 | 1.8453 | 0.56322 | 0.13266 | 0.99598 | 7.0223 | 52.908 |  |  | 336.5721 | 29.82 | 57.81
2021-01-25 20:35 | 2.2683 | 0.61272 | 0.13477 | 1.074 | 16.6702 | 20.279 |  |  | 336.0327 | 29.82 | 57.98
2021-01-25 20:40 | 1.7172 | 0.60171 | 0.13477 | 1.0571 | 9.3191 | 10.1085 |  |  | 336.5647 | 29.81 | 57.97
2021-01-25 20:45 | 1.4994 | 0.48908 | 0.15583 | 0.90551 | 5.8336 | 27.456 |  |  | 336.0833 | 29.77 | 58.18
2021-01-25 20:50 | 1.6147 | 0.49456 | 0.13477 | 0.89496 | -6.2436 | 10.2317 |  |  | 336.6837 | 29.7 | 58.36
2021-01-25 20:55 | 1.6661 | 0.47948 | 0.1432 | 0.87817 | -3.2399 | -2.0916 |  |  | 336.6954 | 29.67 | 58.61
2021-01-25 21:00 | 1.8454 | 0.40664 | 0.12424 | 0.74754 | 0.54336 | 18.9969 |  |  | 336.297 | 29.59 | 58.69
2021-01-25 21:05 | 1.9223 | 0.40252 | 0.12214 | 0.73914 | -7.6071 | 19.6227 |  |  | 335.315 | 29.54 | 58.91
2021-01-25 21:10 | 1.6403 | 0.36954 | 0.1095 | 0.67595 | 6.2127 | 8.8065 |  |  | 336.4299 | 29.47 | 59.1
2021-01-25 21:15 | 1.7173 | 0.3943 | 0.11793 | 0.72022 | 0.18455 | 24.2477 |  |  | 335.3985 | 29.45 | 59.33
2021-01-25 21:20 | 1.5506 | 0.34343 | 0.11371 | 0.64013 | 5.2796 | 20.3904 |  |  | 337.5408 | 29.41 | 59.21
2021-01-25 21:25 | 1.3966 | 0.3063 | 0.12212 | 0.58953 | 5.894 | 10.312 |  |  | 336.5693 | 29.39 | 59.02
2021-01-25 21:30 | 0.90968 | 0.28294 | 0.10527 | 0.53896 | -4.1205 | 12.5254 |  |  | 337.1487 | 29.35 | 59.02
2021-01-25 21:35 | 0.69184 | 0.23623 | 0.11579 | 0.47578 | 3.4746 | 9.5422 |  |  | 336.7032 | 29.3 | 59.09
2021-01-25 21:40 | 0.94803 | 0.15656 | 0.086311 | 0.3263 | -5.5345 | 0.010249 |  |  | 337.3227 | 29.22 | 59.26
2021-01-25 21:45 | 0.88398 | 0.20875 | 0.082101 | 0.40208 | 0.55345 | 20.6313 |  |  | 337.9493 | 29.12 | 59.61
2021-01-25 21:50 | 0.89687 | 0.18542 | 0.09053 | 0.37475 | 4.141 | 34.1118 |  |  | 337.4141 | 29.11 | 59.86
2021-01-25 21:55 | 0.97373 | 0.15658 | 0.084212 | 0.32211 | 3.3414 | -14.8929 |  |  | 338.5304 | 29.04 | 60.06
2021-01-25 22:00 | 1.0635 | 0.14286 | 0.077905 | 0.29688 | 5.9968 | 10.4355 |  |  | 335.9777 | 28.98 | 60.55
2021-01-25 22:05 | 1.2813 | 0.14422 | 0.073689 | 0.29476 | 6.0272 | 14.9654 |  |  | 337.0873 | 28.93 | 60.57
2021-01-25 22:10 | 0.85848 | 0.12911 | 0.077901 | 0.27581 | 7.8928 | -5.3815 |  |  | 336.622 | 28.88 | 60.78
2021-01-25 22:15 | 0.92255 | 0.12362 | 0.075797 | 0.26529 | -4.6537 | 4.6332 |  |  | 337.1909 | 28.83 | 60.98
2021-01-25 22:20 | 0.71753 | 0.11401 | 0.058952 | 0.2337 | -2.4088 | 6.6218 |  |  | 335.7352 | 28.75 | 61.23
2021-01-25 22:25 | 0.92263 | 0.18133 | 0.061063 | 0.33901 | 1.6402 | -6.4174 |  |  | 337.3419 | 28.67 | 61.75
2021-01-25 22:30 | 1.2813 | 0.20604 | 0.086324 | 0.40215 | 9.6971 | 33.0684 |  |  | 337.3905 | 28.65 | 61.63
2021-01-25 22:35 | 1.7941 | 0.23079 | 0.075807 | 0.42957 | 24.1229 | 18.3408 |  |  | 336.8286 | 28.65 | 61.96
2021-01-25 22:40 | 1.4606 | 0.1607 | 0.05895 | 0.30527 | 16.8099 | 14.145 |  |  | 338.0062 | 28.58 | 61.73
2021-01-25 22:45 | 1.2174 | 0.17584 | 0.067382 | 0.33691 | 15.1827 | 16.3923 |  |  | 336.9739 | 28.53 | 62.31
2021-01-25 22:50 | 1.4224 | 0.32694 | 0.073697 | 0.57694 | 15.5411 | 40.1445 |  |  | 336.9701 | 28.54 | 62.22
2021-01-25 22:55 | 1.0378 | 0.25273 | 0.061057 | 0.44845 | 19.0041 | 2.3678 |  |  | 336.9829 | 28.56 | 61.89
2021-01-25 23:00 | 0.99947 | 0.20605 | 0.067378 | 0.38532 | 14.8025 | 12.2397 |  |  | 337.0049 | 28.52 | 62.2
2021-01-25 23:05 | 0.64062 | 0.13185 | 0.061055 | 0.26317 | 9.1942 | 14.6574 |  |  | 337.1308 | 28.44 | 62.22
2021-01-25 23:10 | 0.56377 | 0.12637 | 0.056847 | 0.25055 | 9.3484 | -19.5886 |  |  | 338.2707 | 28.33 | 62.75
2021-01-25 23:15 | 0.97375 | 0.17169 | 0.065266 | 0.32843 | -3.8437 | 8.6202 |  |  | 338.3756 | 28.25 | 62.93
2021-01-25 23:20 | 1.4094 | 0.10851 | 0.056847 | 0.22107 | 5.9965 | 14.9247 |  |  | 337.3476 | 28.23 | 63.12
2021-01-25 23:25 | 1.3326 | 0.15385 | 0.061062 | 0.29689 | -2.4398 | -8.7647 |  |  | 337.3922 | 28.17 | 63.51
2021-01-25 23:30 | 1.102 | 0.14836 | 0.061062 | 0.28847 | 8.1189 | 12.9677 |  |  | 338.4149 | 28.18 | 63.48
2021-01-25 23:35 | 0.4613 | 0.14836 | 0.07159 | 0.299 | -0.55357 | -6.6838 |  |  | 337.93 | 28.15 | 63.6
2021-01-25 23:40 | 0.4869 | 0.11675 | 0.063164 | 0.24213 | 8.9692 | 3.9669 |  |  | 338.0094 | 28.1 | 63.61
2021-01-25 23:45 | 0.61506 | 0.13736 | 0.063167 | 0.27372 | 8.0163 | -0.45105 |  |  | 338.0138 | 28.08 | 63.82
2021-01-25 23:50 |  | 0.10164 | 0.052632 | 0.20842 | -8.3432 | 3.4336 |  |  | 336.1011 | 27.98 | 63.84
2021-01-25 23:55 | 0.23062 | 0.07966 | 0.052632 | 0.17684 | 0.60473 | -16.5429 |  |  | 337.7552 | 27.89 | 64.18
2021-01-26 | 0.21782 | 0.061809 | 0.044214 | 0.13896 | -7.3085 | -1.2813 |  |  | 337.9998 | 27.81 | 64.58
2021-01-26 00:05 | 0.26906 | 0.071421 | 0.050528 | 0.16 | -3.28 | 4.9302 |  |  | 337.5647 | 27.75 | 64.69
2021-01-26 00:10 | 0.4997 | 0.11538 | 0.058952 | 0.23791 | -10.5374 | -17.4256 |  |  | 337.5928 | 27.71 | 64.97
2021-01-26 00:15 | 0.62778 | 0.11674 | 0.056841 | 0.23579 | -16.0506 | 3.2081 |  |  | 337.6349 | 27.7 | 64.77
2021-01-26 00:20 | 1.5501 | 0.089263 | 0.04631 | 0.18314 | 1.9267 | 4.4478 |  |  | 338.2111 | 27.68 | 64.57
2021-01-26 00:25 | 0.58925 | 0.074153 | 0.048413 | 0.16418 | 2.5825 | -7.112 |  |  | 339.3202 | 27.63 | 64.63
2021-01-26 00:30 | 0.79417 | 0.081015 | 0.046305 | 0.17049 | -1.4551 | -14.5717 |  |  | 338.8532 | 27.6 | 64.61
2021-01-26 00:35 | 0.60207 | 0.078275 | 0.046309 | 0.16419 | -1.568 | 1.9881 |  |  | 337.7802 | 27.61 | 64.77
2021-01-26 00:40 | 0.61488 | 0.065915 | 0.033679 | 0.13472 | -6.2103 | -1.0863 |  |  | 337.8182 | 27.58 | 64.85
2021-01-26 00:45 | 0.52513 | 0.065905 | 0.042092 | 0.14311 | -4.2932 | -13.3715 |  |  | 338.4223 | 27.55 | 64.56
2021-01-26 00:50 | 0.37146 | 0.06179 | 0.048409 | 0.14102 | -8.3309 | 7.1218 |  |  | 338.4196 | 27.53 | 64.83
2021-01-26 00:55 | 0.53801 | 0.063167 | 0.050518 | 0.14524 | -1.0145 | -7.8396 |  |  | 339.4342 | 27.53 | 65
2021-01-26 01:00 | 0.49956 | 0.048061 | 0.046306 | 0.11998 | -2.2749 | -4.1605 |  |  | 339.4556 | 27.52 | 64.96
2021-01-26 01:05 |  |  |  |  | -2.4594 | 6.0359 |  |  | 338.4126 | 27.52 | 65.01
2021-01-26 01:10 |  |  |  |  | -6.5181 | 8.4551 |  |  | 339.3947 | 27.54 | 65.18
2021-01-26 01:15 |  |  |  |  | -11.1709 |  |  |  | 338.5162 | 27.56 | 65
2021-01-26 01:20 |  |  |  |  | -1.4551 | 5.1135 |  |  | 338.1007 | 27.5 | 64.96
2021-01-26 01:25 |  |  |  |  | -11.8461 | -2.6234 |  |  | 338.6502 | 27.47 | 65.09
2021-01-26 01:30 |  |  |  |  | -4.0067 |  |  |  | 339.7404 | 27.43 | 65.17
2021-01-26 01:35 |  |  |  |  | -0.99402 | 11.0162 |  |  | 338.7138 | 27.41 | 65.35
2021-01-26 01:40 |  |  |  |  | -9.0795 | -7.5526 |  |  | 338.1934 | 27.41 | 65.37
2021-01-26 01:45 |  |  |  |  | 1.3937 | -8.7002 |  |  | 337.2067 | 27.37 | 65.49
2021-01-26 01:50 |  |  |  |  | -7.942 | 1.7729 |  |  | 338.7763 | 27.35 | 65.62
2021-01-26 01:55 |  |  |  |  | 0.55348 | 14.0318 |  |  | 339.176 | 27.4 | 65.91
2021-01-26 02:00 |  |  |  |  | 8.0056 |  |  |  | 338.5191 | 27.5 | 65.73
2021-01-26 02:05 |  |  |  |  | -8.0665 | 6.3343 |  |  | 337.5757 | 27.44 | 65.77
2021-01-26 02:10 | 0.17938 | 0.068677 | 0.048424 | 0.15369 | -5.9759 | -8.9177 |  |  | 338.099 | 27.42 | 65.98
2021-01-26 02:15 | 0.4228 | 0.045324 | 0.037895 | 0.10526 | -11.2132 | -18.7569 |  |  | 337.6323 | 27.39 | 65.96
2021-01-26 02:20 | 1.422 | 0.039827 | 0.039997 | 0.10105 | -5.0117 | -6.0058 |  |  | 338.7627 | 27.33 | 65.98
2021-01-26 02:25 | 1.3578 | 0.039823 | 0.037888 | 0.09893 | -6.6918 | -1.2707 |  |  | 338.3371 | 27.28 | 65.89
2021-01-26 02:30 | 1.0504 | 0.045316 | 0.048413 | 0.11788 | -5.0625 | -5.4007 |  |  | 338.3542 | 27.26 | 66.01
2021-01-26 02:35 | 0.33309 | 0.089268 | 0.061049 | 0.19788 | -2.1523 | -4.3865 |  |  | 338.2669 | 27.31 | 66.06
2021-01-26 02:40 | 1.0378 | 0.05631 | 0.052631 | 0.13894 | -0.32798 | 20.7858 |  |  | 338.2503 | 27.31 | 66.19
2021-01-26 02:45 | 0.52531 | 0.10027 | 0.080003 | 0.23369 | 1.271 | -9.9015 |  |  | 338.7368 | 27.32 | 66.31
2021-01-26 02:50 | 1.5502 | 0.064552 | 0.056842 | 0.15368 | -0.94296 | -6.652 |  |  | 339.3258 | 27.27 | 66.39
2021-01-26 02:55 | 0.9994 | 0.075544 | 0.067373 | 0.18317 | 3.3108 | 13.7149 |  |  | 338.8183 | 27.24 | 66.69
2021-01-26 03:00 | 0.44848 | 0.24038 | 0.084221 | 0.45058 | 5.925 | 6.0583 |  |  | 337.8586 | 27.31 | 66.51
2021-01-26 03:05 | 1.0379 | 0.15385 | 0.054746 | 0.29057 | -2.6756 | -9.5747 |  |  | 337.8002 | 27.35 | 66.46
2021-01-26 03:10 | 0.98657 | 0.10851 | 0.040002 | 0.20843 | 4.2538 | 3.075 |  |  | 338.4374 | 27.28 | 66.41
2021-01-26 03:15 | 0.35872 | 0.090643 | 0.035788 | 0.17473 | -0.62519 | 4.9606 |  |  | 338.0642 | 27.18 | 66.55
2021-01-26 03:20 | 0.98661 | 0.13873 | 0.044215 | 0.25687 | 2.4806 | -6.7244 |  |  | 338.5337 | 27.18 | 66.93
2021-01-26 03:25 | 1.2299 | 0.087898 | 0.039999 | 0.17473 | 2.3778 | -4.1407 |  |  | 338.0926 | 27.15 | 66.71
2021-01-26 03:30 | 1.499 | 0.065926 | 0.040001 | 0.14106 | 2.5419 | 6.1806 |  |  | 338.0873 | 27.14 | 66.88
2021-01-26 03:35 | 1.6785 | 0.054942 | 0.037898 | 0.12211 | 7.452 | -1.8348 |  |  | 338.596 | 27.13 | 67.08
2021-01-26 03:40 | 0.69193 | 0.060439 | 0.04211 | 0.13475 | 9.2872 | 3.7518 |  |  | 339.0761 | 27.15 | 67.12
2021-01-26 03:45 | 1.2814 | 0.038462 | 0.040006 | 0.098961 | -7.8318 | 5.3203 |  |  | 337.5503 | 27.12 | 67.29
2021-01-26 03:50 | 1.9733 | 0.039835 | 0.042111 | 0.10317 | 7.5345 | 3.3521 |  |  | 338.0904 | 27.1 | 67.37
2021-01-26 03:55 | 1.2943 | 0.043961 | 0.044221 | 0.11161 | 3.4139 | 6.305 |  |  | 338.0339 | 27.12 | 67.56
2021-01-26 04:00 | 0.73044 | 0.078304 | 0.031586 | 0.15161 | 1.6403 | 5.2182 |  |  | 337.489 | 27.15 | 67.39
2021-01-26 04:05 | 0.46136 | 0.20607 | 0.054752 | 0.37063 | 17.4805 | 29.8347 |  |  | 338.3907 | 27.25 | 67.16
2021-01-26 04:10 | 0.61515 | 0.28988 | 0.063176 | 0.50541 | 25.5594 | 18.7313 |  |  | 337.2668 | 27.33 | 66.84
2021-01-26 04:15 | 0.71754 | 0.18406 | 0.058953 | 0.34319 | 33.5399 | 32.2483 |  |  | 337.8577 | 27.32 | 66.39
2021-01-26 04:20 | 0.6535 | 0.16071 | 0.048427 | 0.29267 | 25.1148 | 39.1381 |  |  | 337.8796 | 27.29 | 66.6
2021-01-26 04:25 | 0.48693 | 0.15797 | 0.048428 | 0.29057 | 20.5636 | -12.5268 |  |  | 336.8742 | 27.26 | 66.75
2021-01-26 04:30 | 0.58948 | 0.19645 | 0.046326 | 0.34745 | 12.8046 | 19.2735 |  |  | 336.8254 | 27.28 | 66.88
2021-01-26 04:35 | 0.75619 | 0.27616 | 0.084242 | 0.50545 | 13.514 | 21.3168 |  |  | 336.1463 | 27.38 | 66.88
2021-01-26 04:40 | 0.83301 | 0.30224 | 0.11161 | 0.57279 | 19.3054 | 14.3739 |  |  | 337.1214 | 27.46 | 66.33
2021-01-26 04:45 | 0.92266 | 0.30634 | 0.094757 | 0.56433 | 21.2213 | 22.8615 |  |  | 337.1088 | 27.49 | 66.05
2021-01-26 04:50 | 1.1405 | 0.43685 | 0.096863 | 0.76648 | 28.0693 | 28.3666 |  |  | 337.0659 | 27.53 | 65.88
2021-01-26 04:55 | 0.98673 | 0.45608 | 0.08844 | 0.78753 | 29.5352 | 21.4466 |  |  | 337.5278 | 27.58 | 65.68
2021-01-26 05:00 | 0.92259 | 0.44368 | 0.0758 | 0.75589 | 18.2364 | 32.6185 |  |  | 337.9062 | 27.57 | 65.59
2021-01-26 05:05 | 1.2556 | 0.35299 | 0.050528 | 0.5916 | 27.3262 | 6.3242 |  |  | 338.482 | 27.55 | 65.39
2021-01-26 05:10 | 0.98659 | 0.3324 | 0.075795 | 0.58531 | 18.4096 | 18.7889 |  |  | 337.9944 | 27.51 | 65.66
2021-01-26 05:15 | 0.89695 | 0.32417 | 0.077904 | 0.57481 | 19.5586 | 12.014 |  |  | 336.9424 | 27.51 | 65.79
2021-01-26 05:20 | 1.0764 | 0.35028 | 0.084223 | 0.62114 | 25.1766 | 18.9542 |  |  | 336.8907 | 27.55 | 65.69
2021-01-26 05:25 | 1.7555 | 0.35714 | 0.092643 | 0.64008 | 5.761 | 0.13326 |  |  | 337.877 | 27.6 | 65.44
2021-01-26 05:30 | 1.7808 | 0.36257 | 0.088416 | 0.64418 | 11.9196 | -1.0659 |  |  | 336.3719 | 27.61 | 64.95
2021-01-26 05:35 | 2.8568 | 0.57129 | 0.1263 | 1.002 | 21.819 | 37.7349 |  |  | 336.8965 | 27.62 | 64.77
2021-01-26 05:40 | 3.1514 | 0.59601 | 0.11788 | 1.0336 | 24.4324 | 36.2796 |  |  | 337.8646 | 27.68 | 64.54
2021-01-26 05:45 | 2.5363 | 0.56575 | 0.13471 | 0.99981 | 43.8394 | 23.8463 |  |  | 337.847 | 27.72 | 64.18
2021-01-26 05:50 | 3.5603 | 0.48463 | 0.11995 | 0.86282 | 43.728 | 46.8529 |  |  | 337.3539 | 27.76 | 63.5
2021-01-26 05:55 | 3.1756 | 0.48868 | 0.12835 | 0.87741 | 35.0139 | 32.0739 |  |  | 337.8669 | 27.81 | 62.92
2021-01-26 06:00 | 2.433 | 0.59989 | 0.13046 | 1.0521 | 29.9649 | -9.22 |  |  | 337.808 | 27.85 | 62.88
2021-01-26 06:05 | 3.0346 | 0.66022 | 0.13676 | 1.1488 | 15.283 | 22.7914 |  |  | 336.7418 | 27.91 | 62.39
2021-01-26 06:10 | 2.4574 | 0.63526 | 0.12409 | 1.0978 | 25.5981 | 31.2296 |  |  | 336.8094 | 27.97 | 61.15
2021-01-26 06:15 | 3.5062 | 0.68863 | 0.13457 | 1.188 | 21.8459 | 0.58351 |  |  | 336.284 | 28.04 | 60.37
2021-01-26 06:20 | 3.6974 | 0.68437 | 0.13875 | 1.1878 | 19.6717 | 19.5898 |  |  | 336.8137 | 28.09 | 59.68
2021-01-26 06:25 | 3.4156 | 0.6651 | 0.10931 | 1.1288 | 24.0189 | 31.459 |  |  | 336.7945 | 28.14 | 59.23
2021-01-26 06:30 | 3.6578 | 0.67866 | 0.18073 | 1.221 | 34.1732 | 22.3251 |  |  | 336.8288 | 28.18 | 58.5
2021-01-26 06:35 | 3.7343 | 0.67587 | 0.17652 | 1.2125 | 38.3453 | 35.8489 |  |  | 336.7826 | 28.24 | 58.14
2021-01-26 06:40 | 4.3351 | 0.74027 | 0.19752 | 1.3343 | 47.8476 | 49.4538 |  |  | 335.1898 | 28.29 | 57.86
2021-01-26 06:45 | 4.7188 | 0.78277 | 0.21013 | 1.4079 | 63.6023 | 49.5355 |  |  | 336.1805 | 28.33 | 57.72
2021-01-26 06:50 | 3.0684 | 0.67705 | 0.17857 | 1.2185 | 88.3087 | 86.3244 |  |  | 339.3286 | 28.36 | 57.04
2021-01-26 06:55 | 2.6079 | 0.66193 | 0.16595 | 1.1806 |  |  |  |  | 489.3084 | 28.4 | 56.72
2021-01-26 07:00 | 3.5536 | 0.67556 | 0.17644 | 1.212 |  | -15.4313 |  |  | 490.7659 | 28.49 | 56.16
2021-01-26 07:05 | 2.927 | 0.68235 | 0.18062 | 1.2287 | 6.3294 | 23.2727 |  |  | 490.7277 | 28.54 | 55.78
2021-01-26 07:10 | 2.6708 | 0.68496 | 0.17219 | 1.2221 | 19.7718 | 17.3285 |  |  | 490.2243 | 28.59 | 55.14
2021-01-26 07:15 | 2.6575 | 0.51773 | 0.16376 | 0.95735 | 35.7747 | 40.7729 |  |  | 491.2543 | 28.65 | 54.48
2021-01-26 07:20 | 2.0954 | 0.47527 | 0.15536 | 0.88177 | 53.6007 | 11.8976 |  |  | 489.0558 | 28.73 | 54.23
2021-01-26 07:25 | 1.8907 | 0.50261 | 0.15534 | 0.92577 | 66.2068 | 47.1971 |  |  | 490.5289 | 28.81 | 53.72
2021-01-26 07:30 | 2.121 | 0.50679 | 0.17636 | 0.95319 | 65.5005 | 57.4765 |  |  | 490.8474 | 28.89 | 53.81
2021-01-26 07:35 | 2.2103 | 0.50813 | 0.17425 | 0.95314 | 69.1155 | 36.4282 |  |  | 489.2251 | 28.95 | 53.5
2021-01-26 07:40 | 2.1466 | 0.43283 | 0.15957 | 0.82093 | 68.2616 | 43.1362 |  |  | 490.6438 | 29.01 | 53.48
2021-01-26 07:45 | 2.5172 | 0.46025 | 0.16797 | 0.87135 | 69.5112 | 4.6 |  |  | 489.9799 | 29.09 | 53.32
2021-01-26 07:50 | 3.1167 | 0.67096 | 0.18471 | 1.2132 | 64.6234 | 26.6811 |  |  | 490.0334 | 29.16 | 52.29
2021-01-26 07:55 | 3.5251 | 0.75305 | 0.19518 | 1.3495 | 55.0944 | 14.5399 |  |  | 489.4003 | 29.26 | 51.77
2021-01-26 08:00 | 3.2172 | 0.72125 | 0.21608 | 1.3216 | 71.3814 | 47.2574 |  |  | 489.4661 | 29.35 | 50.48
2021-01-26 08:05 | 3.6247 | 0.58833 | 0.21602 | 1.1157 | 60.1807 | 12.3241 |  |  | 488.4745 | 29.41 | 49.64
2021-01-26 08:10 | 2.9468 | 0.54153 | 0.20333 | 1.0313 | 40.4432 | 16.9611 |  |  | 489.1317 | 29.48 | 48.22
2021-01-26 08:15 | 2.5251 | 0.53043 | 0.17393 | 0.987 | 38.8297 | 8.1108 |  |  | 490.2106 | 29.54 | 47.37
2021-01-26 08:20 | 2.8685 | 0.59861 | 0.20321 | 1.1208 | 46.1209 | -19.195 |  |  | 489.741 | 29.6 | 46.52
2021-01-26 08:25 | 2.9566 | 0.66532 | 0.20941 | 1.2313 | 60.2745 | 32.2987 |  |  | 489.8332 | 29.66 | 45.46
2021-01-26 08:30 | 3.3503 | 0.6391 | 0.20304 | 1.1827 | 63.8161 | 5.2789 |  |  | 490.4585 | 29.72 | 44.33
2021-01-26 08:35 | 2.7886 | 0.61153 | 0.2469 | 1.1843 | 59.1446 | 26.7608 |  |  | 491.0317 | 29.81 | 43.15
2021-01-26 08:40 | 2.4182 | 0.70402 | 0.2677 | 1.3468 | 66.8752 | -0.05091 |  |  | 489.5524 | 29.91 | 41.81
2021-01-26 08:45 | 2.4813 | 0.75161 | 0.276 | 1.4302 | 70.0675 | 13.0505 |  |  | 488.9791 | 30.01 | 41.08
2021-01-26 08:50 | 2.748 | 0.77192 | 0.29685 | 1.4801 | 60.8527 | 1.2213 |  |  | 488.9157 | 30.11 | 40.39
2021-01-26 08:55 | 3.1417 | 0.71041 | 0.29052 | 1.3795 | 74.5979 | 8.5781 |  |  | 490.4523 | 30.18 | 39.77
2021-01-26 09:00 | 2.8362 | 0.62854 | 0.26751 | 1.2309 | 73.2685 | 27.0038 |  |  | 490.3348 | 30.28 | 39.34
2021-01-26 09:05 | 2.1746 | 0.53304 | 0.26748 | 1.0846 | 77.9718 | 8.9529 |  |  | 489.7371 | 30.36 | 38.94
2021-01-26 09:10 | 2.5817 | 0.44172 | 0.2257 | 0.90278 | 74.0069 | 17.2045 |  |  | 488.5559 | 30.44 | 38.85
2021-01-26 09:15 | 3.3701 | 0.49215 | 0.22151 | 0.97589 | 69.4156 | -18.6994 |  |  | 487.9786 | 30.49 | 38.65
2021-01-26 09:20 | 2.8987 | 0.65283 | 0.21935 | 1.2221 | 67.4327 | 19.7314 |  |  | 489.039 | 30.56 | 37.86
2021-01-26 09:25 | 3.2041 | 0.72648 | 0.27787 | 1.3914 | 72.9405 | 22.5199 |  |  | 488.8742 | 30.64 | 37.85
2021-01-26 09:30 | 2.9116 | 0.72237 | 0.26742 | 1.3747 | 84.7784 | 21.6548 |  |  | 488.7724 | 30.71 | 37.65
2021-01-26 09:35 | 4.2214 | 0.73877 | 0.25072 | 1.3831 | 80.1246 | 16.8956 |  |  | 488.6472 | 30.77 | 37.65
2021-01-26 09:40 | 4.9592 | 0.83288 | 0.25909 | 1.5358 | 65.0036 | 22.6953 |  |  | 489.5304 | 30.84 | 37.66
2021-01-26 09:45 | 4.9207 | 0.93506 | 0.29669 | 1.7321 | 70.055 | 14.6579 |  |  | 488.9335 | 30.91 | 37.37
2021-01-26 09:50 | 5.4418 | 0.99634 | 0.29458 | 1.8239 | 66.9793 | 6.6928 |  |  | 488.3001 | 31 | 37.06
2021-01-26 09:55 | 4.2458 | 0.8885 | 0.282 | 1.6439 | 69.5606 | 26.97 |  |  | 488.3232 | 31.04 | 36.59
2021-01-26 10:00 | 3.2034 | 0.78902 | 0.30288 | 1.5123 | 64.6584 | -0.1017 |  |  | 487.6986 | 31.11 | 36.43
2021-01-26 10:05 | 2.5048 | 0.7592 | 0.29041 | 1.4562 | 48.6821 | 11.016 |  |  | 487.4828 | 31.18 | 36.74
2021-01-26 10:10 | 3.0903 | 0.70892 | 0.31346 | 1.4022 | 51.7141 | 0.10174 |  |  | 487.8353 | 31.23 | 37.05
2021-01-26 10:15 | 3.1685 | 0.80755 | 0.30737 | 1.5473 | 52.467 | 21.0011 |  |  | 485.3821 | 31.3 | 38.14
2021-01-26 10:20 | 2.7969 | 1.0112 | 0.33007 | 1.8801 | 72.6993 | 33.7867 |  |  | 486.7588 | 31.36 | 36.08
2021-01-26 10:25 | 2.7188 | 0.9874 | 0.30688 | 1.8204 | 65.7286 | 11.3833 |  |  | 487.4754 | 31.44 | 34.49
2021-01-26 10:30 | 2.6281 | 0.94046 | 0.27538 | 1.717 | 62.7999 | 1.554 |  |  | 486.1779 | 31.49 | 32.98
2021-01-26 10:35 | 2.5768 | 0.83821 | 0.31912 | 1.604 | 55.5261 | 12.1451 |  |  | 486.6988 | 31.55 | 32.43
2021-01-26 10:40 | 3.3802 | 0.85413 | 0.37586 | 1.6851 | 56.0654 | 27.5295 |  |  | 487.014 | 31.66 | 34.53
2021-01-26 10:45 | 3.3907 | 0.92299 | 0.39648 | 1.8113 | 61.1791 | 11.0126 |  |  | 487.2562 | 31.71 | 33.06
2021-01-26 10:50 | 2.6661 | 0.93092 | 0.36508 | 1.7899 | 63.3978 | 29.891 |  |  | 488.363 | 31.74 | 32.47
2021-01-26 10:55 | 3.1364 | 0.96103 | 0.3255 | 1.7986 | 66.6191 | 14.9228 |  |  | 486.6049 | 31.82 | 32.69
2021-01-26 11:00 | 3.0474 | 0.95555 | 0.35053 | 1.8152 | 67.531 | 18.0001 |  |  | 486.51 | 31.89 | 32.49
2021-01-26 11:05 | 4.2389 | 0.89522 | 0.33159 | 1.7038 | 63.7617 | 16.8136 |  |  | 487.6806 | 31.95 | 31.38
2021-01-26 11:10 | 4.316 | 0.85595 | 0.32749 | 1.6395 | 59.7743 | 17.193 |  |  | 486.4189 | 32.03 | 31.68
2021-01-26 11:15 | 4.1141 | 0.87525 | 0.33801 | 1.6817 | 57.9728 | 4.429 |  |  | 486.203 | 32.08 | 32.16
2021-01-26 11:20 | 2.8851 | 0.99871 | 0.38428 | 1.913 | 55.73 | 0.42705 |  |  | 486.6557 | 32.15 | 33.96
2021-01-26 11:25 | 2.5014 | 1.1053 | 0.4006 | 2.0948 | 47.0117 | 14.3331 |  |  | 485.55 | 32.17 | 31.98
2021-01-26 11:30 | 3.9477 | 1.0015 | 0.37336 | 1.9085 | 61.8934 | 31.0736 |  |  | 485.6292 | 32.22 | 31.23
2021-01-26 11:35 | 3.8459 | 1.0028 | 0.37959 | 1.9167 | 63.991 | 20.2676 |  |  | 486.0648 | 32.29 | 30.97
2021-01-26 11:40 | 3.7946 | 0.96185 | 0.38162 | 1.856 | 53.5862 | 3.5535 |  |  | 487.5903 | 32.34 | 30.62
2021-01-26 11:45 | 3.8887 | 0.98633 | 0.3717 | 1.8836 | 48.5761 | 9.577 |  |  | 486.8613 | 32.38 | 33.28
2021-01-26 11:50 | 4.397 | 0.82829 | 0.31114 | 1.5808 | 39.9241 | 1.9215 |  |  | 486.3039 | 32.41 | 33.21
2021-01-26 11:55 | 3.8203 | 0.7456 | 0.3024 | 1.4453 | 51.4988 | 14.9257 |  |  | 486.9105 | 32.42 | 30.64
2021-01-26 12:00 | 2.9701 | 0.80822 | 0.35247 | 1.5913 | 46.0385 | 6.3057 |  |  | 486.3291 | 32.46 | 30.64
2021-01-26 12:05 | 2.208 | 0.85973 | 0.35031 | 1.6661 | 41.5411 | 15.8977 |  |  | 486.3911 | 32.49 | 30.14
2021-01-26 12:10 | 2.3981 | 0.84332 | 0.31691 | 1.6096 | 41.1102 | -0.89326 |  |  | 485.8514 | 32.54 | 29.84
2021-01-26 12:15 | 4.0112 | 0.80829 | 0.3233 | 1.5623 | 50.0939 | -4.0112 |  |  | 486.0845 | 32.59 | 30.57
2021-01-26 12:20 | 2.3619 | 0.79363 | 0.30047 | 1.517 | 55.528 | 14.456 |  |  | 486.3768 | 32.61 | 31.3
2021-01-26 12:25 | 2.6914 | 0.75667 | 0.29831 | 1.4561 | 45.8852 | 20.7895 |  |  | 485.8987 | 32.67 | 30.67
2021-01-26 12:30 | 2.9716 | 0.6766 | 0.29006 | 1.3272 | 49.7204 | 23.702 |  |  | 486.7142 | 32.7 | 31.27
2021-01-26 12:35 | 2.7059 | 0.71633 | 0.29225 | 1.3882 | 58.5491 | 21.4135 |  |  | 484.9605 | 32.73 | 31.9
2021-01-26 12:40 | 3.7696 | 0.89119 | 0.32535 | 1.6914 | 60.4857 | 7.4934 |  |  | 485.3085 | 32.79 | 30.01
2021-01-26 12:45 | 4.0346 | 0.9371 | 0.35441 | 1.7908 | 64.4922 | 22.3703 |  |  | 485.4301 | 32.83 | 29.2
2021-01-26 12:50 | 3.2736 | 0.89093 | 0.32942 | 1.6951 | 70.71 | 12.2316 |  |  | 486.3653 | 32.86 | 29.32
2021-01-26 12:55 | 2.9935 | 0.8716 | 0.31889 | 1.6549 | 72.6348 | 3.3791 |  |  | 485.9828 | 32.88 | 28.64
2021-01-26 13:00 | 3.5894 | 0.94904 | 0.30428 | 1.759 | 72.7313 | 22.7691 |  |  | 485.9211 | 32.94 | 28.41
2021-01-26 13:05 | 3.7153 | 0.88763 | 0.29379 | 1.6544 | -8.3993 | -1.5013 |  |  | 486.5394 | 32.95 | 27.91
2021-01-26 13:10 | 3.7291 | 0.78727 | 0.35223 | 1.5569 | 22.1917 | 29.6397 |  |  | 484.8585 | 32.95 | 28.48
2021-01-26 13:15 | 4.0078 | 0.81305 | 0.39806 | 1.6443 | 75.6518 | 28.613 |  |  | 484.8589 | 32.97 | 28.32
2021-01-26 13:20 | 3.4401 | 0.8505 | 0.3838 | 1.6875 | 92.4327 | 36.1322 |  |  | 484.3927 | 33 | 29.94
2021-01-26 13:25 | 2.9562 | 0.78207 | 0.35234 | 1.5511 | 105.7844 | 10.9215 |  |  | 485.6608 | 33 | 28.97
2021-01-26 13:30 | 2.0916 | 0.73247 | 0.32704 | 1.4498 | 111.7066 | 17.9704 |  |  | 484.596 | 32.98 | 27.3
2021-01-26 13:35 | 3.2203 | 0.878 | 0.32083 | 1.6687 | 102.3302 | 36.6052 |  |  | 485.5994 | 32.95 | 27.62
2021-01-26 13:40 | 3.2465 | 0.96386 | 0.32716 | 1.8046 | 105.5913 | 39.0286 |  |  | 484.8905 | 33 | 28.01
2021-01-26 13:45 | 2.967 | 1.1227 | 0.38127 | 2.1022 | 130.2722 | 33.169 |  |  | 484.8802 | 33.06 | 27.58
2021-01-26 13:50 | 2.004 | 1.1 | 0.37099 | 2.0592 | 128.9073 | 41.907 |  |  | 484.5682 | 33.15 | 28.11
2021-01-26 13:55 | 3.3612 | 0.98034 | 0.31471 | 1.8174 | 103.9258 | 39.2791 |  |  | 484.0072 | 33.18 | 28.07
2021-01-26 14:00 | 2.6124 | 0.8551 | 0.32508 | 1.6337 | 100.1744 | 61.8963 |  |  | 484.059 | 33.2 | 27.71
2021-01-26 14:05 |  |  |  |  | 97.5182 | 28.794
2021-01-26 14:10 | 3.1562 | 0.76909 | 0.37491 | 1.5559 | 115.0737 | 33.5344 |  |  | 484.132 | 33.3 | 26.65
2021-01-26 14:15 | 2.6656 | 0.82459 | 0.46303 | 1.727 | 126.4238 | 32.4234 |  |  | 483.8927 | 33.35 | 29.2
2021-01-26 14:20 | 2.9846 | 0.82098 | 0.44034 | 1.6988 | 125.3993 | 30.1052 |  |  | 483.551 | 33.39 | 30.22
2021-01-26 14:25 | 3.2547 | 0.73052 | 0.3656 | 1.4854 | 147.8256 | 80.1578 |  |  | 481.9771 | 33.42 | 32.14
2021-01-26 14:30 | 4.1105 | 0.6903 | 0.33458 | 1.3948 | 180.1806 | 64.2411 |  |  | 481.5593 | 33.39 | 34.01
2021-01-26 14:35 | 4.7609 | 0.65911 | 0.31167 | 1.3241 | 182.5231 | 43.7086 |  |  | 482.536 | 33.33 | 34.66
2021-01-26 14:40 | 3.4375 | 0.71242 | 0.31171 | 1.4058 | 149.5368 | 41.2494 |  |  | 483.0466 | 33.29 | 34.98
2021-01-26 14:45 | 4.7621 | 0.7712 | 0.3515 | 1.5336 | 101.4956 | 27.9408 |  |  | 482.0027 | 33.27 | 35.24
2021-01-26 14:50 | 3.1192 | 0.77249 | 0.38703 | 1.5711 | 88.622 | 33.6929 |  |  | 484.1183 | 33.25 | 35.1
2021-01-26 14:55 | 2.929 | 0.62525 | 0.35156 | 1.31 | 64.3879 | 43.5026 |  |  | 482.4937 | 33.23 | 35.64
2021-01-26 15:00 | 2.84 | 0.70447 | 0.3453 | 1.4251 | 26.541 | 33.785 |  |  | 482.0217 | 33.19 | 35.82
2021-01-26 15:05 | 3.0064 | 0.68007 | 0.37888 | 1.4234 | 11.1796 | 21.9821 |  |  | 483.5076 | 33.14 | 36.4
2021-01-26 15:10 | 3.5544 | 0.57086 | 0.32238 | 1.1974 | 2.7008 | 28.6389 |  |  | 483.0103 | 33.11 | 36.6
2021-01-26 15:15 | 3.9244 | 0.78812 | 0.28055 | 1.4886 | -2.5891 | 16.7067 |  |  | 483.0217 | 33.06 | 36.97
2021-01-26 15:20 | 2.7532 | 0.87585 | 0.30579 | 1.6483 | 7.8312 | 6.4241 |  |  | 482.8154 | 33.08 | 37.62
2021-01-26 15:25 | 3.7111 | 0.88043 | 0.28709 | 1.6346 | 31.8316 | 35.9636 |  |  | 482.0598 | 33.07 | 38.68
2021-01-26 15:30 | 5.2691 | 0.92317 | 0.37316 | 1.7882 | 38.7233 | 46.6537 |  |  | 483.4762 | 33.02 | 39.54
2021-01-26 15:35 | 4.4794 | 0.9508 | 0.41521 | 1.8726 | 61.7258 | 37.5807 |  |  | 483.7994 | 33.05 | 40.02
2021-01-26 15:40 | 4.1478 | 0.89338 | 0.37328 | 1.7427 | 62.9029 | 45.7197 |  |  | 482.3135 | 33.01 | 40.2
2021-01-26 15:45 | 3.0119 | 0.7128 | 0.33554 | 1.4281 | 41.085 | 9.0869 |  |  | 481.8931 | 32.95 | 40.36
2021-01-26 15:50 | 3.2292 | 0.6595 | 0.33137 | 1.3423 | 17.4605 | 17.6239 |  |  | 482.472 | 32.88 | 40.68
2021-01-26 15:55 | 3.1016 | 0.68551 | 0.29783 | 1.3486 | 12.529 | 16.6441 |  |  | 481.9976 | 32.85 | 40.8
2021-01-26 16:00 | 3.3062 | 0.65685 | 0.31254 | 1.3194 | 8.2413 | 26.8685 |  |  | 483.5167 | 32.82 | 41.09
2021-01-26 16:05 | 3.3194 | 0.64599 | 0.32517 | 1.3154 | 1.3482 | 25.8405 |  |  | 481.9722 | 32.79 | 41.42
2021-01-26 16:10 | 3.5367 | 0.60086 | 0.32519 | 1.2462 | 1.8692 | 23.2681 |  |  | 483.4858 | 32.78 | 41.56
2021-01-26 16:15 | 2.7327 | 0.58725 | 0.35881 | 1.259 | 0.48013 | 12.1055 |  |  | 482.4199 | 32.77 | 41.84
2021-01-26 16:20 | 2.3241 | 0.73511 | 0.36301 | 1.4877 | 24.2729 | 35.7658 |  |  | 481.9294 | 32.75 | 41.94
2021-01-26 16:25 | 2.7456 | 0.89806 | 0.32106 | 1.6976 | 26.7668 | 35.2362 |  |  | 484.4682 | 32.74 | 42.05
2021-01-26 16:30 | 2.3756 | 0.8393 | 0.25394 | 1.5404 | 14.9791 | 20.4557 |  |  | 483.9138 | 32.73 | 42.32
2021-01-26 16:35 | 2.5928 | 0.69282 | 0.27284 | 1.3327 | 14.0396 | 33.2291 |  |  | 483.9897 | 32.67 | 42.54
2021-01-26 16:40 | 3.1677 | 0.70792 | 0.29384 | 1.379 | 18.3934 | 24.7697 |  |  | 484.0298 | 32.63 | 42.73
2021-01-26 16:45 | 5.9524 | 0.70657 | 0.26656 | 1.3496 | 27.6724 | 22.5119 |  |  | 483.0162 | 32.62 | 42.8
2021-01-26 16:50 | 6.1053 | 0.73253 | 0.25605 | 1.3789 | 11.0151 | 29.5302 |  |  | 482.0949 | 32.58 | 42.76
2021-01-26 16:55 | 7.1138 | 0.86665 | 0.28961 | 1.618 | 15.8879 | 47.7149 |  |  | 484.6893 | 32.56 | 42.71
2021-01-26 17:00 | 4.4699 | 1.0227 | 0.30009 | 1.8677 | 21.5576 | 31.3863 |  |  | 482.2084 | 32.53 | 42.7
2021-01-26 17:05 | 3.9335 | 0.89127 | 0.298 | 1.6663 | 33.8794 | 28.1579 |  |  | 484.786 | 32.51 | 42.76
2021-01-26 17:10 | 2.8981 | 0.68019 | 0.27482 | 1.3153 | 16.2904 | 34.552 |  |  | 484.4911 | 32.48 | 42.15
2021-01-26 17:15 | 3.0636 | 0.64589 | 0.2559 | 1.2459 | 19.2599 | 10.7635 |  |  | 484.5884 | 32.46 | 41.93
2021-01-26 17:20 | 1.7364 | 0.66244 | 0.28112 | 1.2965 | 5.1478 | 28.9463 |  |  | 483.5255 | 32.43 | 42.37
2021-01-26 17:25 | 1.7748 | 0.69944 | 0.29583 | 1.368 | 12.3904 | 3.473 |  |  | 484.0638 | 32.39 | 42.61
2021-01-26 17:30 | 2.9494 | 0.709 | 0.29582 | 1.3805 | 10.2348 | 28.0283 |  |  | 483.5995 | 32.37 | 42.6
2021-01-26 17:35 | 2.1452 | 0.65567 | 0.26647 | 1.2694 | 21.513 | 30.962 |  |  | 483.6135 | 32.34 | 42.81
2021-01-26 17:40 | 2.6433 | 0.71731 | 0.27488 | 1.3744 | 21.3407 | 23.2306 |  |  | 484.1571 | 32.3 | 43.03
2021-01-26 17:45 | 3.6139 | 0.67763 | 0.27489 | 1.3136 | 22.7103 | 27.1952 |  |  | 483.168 | 32.27 | 43.17
2021-01-26 17:50 | 2.7072 | 0.60096 | 0.26649 | 1.1877 | 20.9528 | 5.4553 |  |  | 484.1957 | 32.27 | 43.14
2021-01-26 17:55 | 2.5028 | 0.50102 | 0.20773 | 0.97571 | 16.1102 | 16.4575 |  |  | 485.2742 | 32.24 | 43.17
2021-01-26 18:00 | 1.7367 | 0.42848 | 0.19515 | 0.85193 | 25.0392 | 22.4954 |  |  | 485.8064 | 32.22 | 43.26
2021-01-26 18:05 | 2.5796 | 0.43944 | 0.20355 | 0.87714 | 26.46 | 29.2286 |  |  | 484.8342 | 32.18 | 43.42
2021-01-26 18:10 | 2.8989 | 0.55719 | 0.22244 | 1.0765 | 20.8824 | 14.9058 |  |  | 485.3811 | 32.15 | 43.54
2021-01-26 18:15 | 2.1327 | 0.53393 | 0.19306 | 1.0115 | 29.7307 | 21.782 |  |  | 484.4114 | 32.11 | 43.69
2021-01-26 18:20 | 2.7587 | 0.53534 | 0.21406 | 1.0346 | 26.5553 | 11.5151 |  |  | 483.8796 | 32.1 | 43.87
2021-01-26 18:25 | 2.1456 | 0.49013 | 0.18048 | 0.93177 | 18.1455 | 39.4788 |  |  | 485.4789 | 32.07 | 43.86
2021-01-26 18:30 | 1.6602 | 0.43261 | 0.19096 | 0.85408 | 22.1391 | 14.3337 |  |  | 484.5499 | 32.03 | 43.84
2021-01-26 18:35 | 2.8351 | 0.50243 | 0.22034 | 0.98839 | 25.613 | 21.0155 |  |  | 484.5728 | 32 | 43.98
2021-01-26 18:40 | 4.1374 | 0.48596 | 0.22872 | 0.97362 | 19.9616 | 21.0649 |  |  | 484.7061 | 31.94 | 43.97
2021-01-26 18:45 | 3.4731 | 0.44487 | 0.2371 | 0.91901 | 27.0905 | 24.0362 |  |  | 487.2936 | 31.94 | 43.84
2021-01-26 18:50 | 3.524 | 0.45716 | 0.22449 | 0.92733 | 28.5391 | 44.2284 |  |  | 486.3532 | 31.91 | 43.77
2021-01-26 18:55 | 3.4344 | 0.42292 | 0.16784 | 0.8161 | 38.8028 | 11.8277 |  |  | 485.912 | 31.88 | 43.75
2021-01-26 19:00 | 2.0938 | 0.36679 | 0.16154 | 0.72376 | 30.6509 | 31.8765 |  |  | 487.0006 | 31.85 | 43.75
2021-01-26 19:05 | 2.0555 | 0.32984 | 0.15524 | 0.66083 | 28.7306 | 10.8774 |  |  | 486.555 | 31.81 | 43.84
2021-01-26 19:10 | 1.417 | 0.28739 | 0.15103 | 0.59155 | 21.8962 | 10.3251 |  |  | 487.6457 | 31.79 | 43.74
2021-01-26 19:15 | 0.90643 | 0.2874 | 0.15314 | 0.59158 | 20.8352 | 31.7328 |  |  | 487.1398 | 31.77 | 43.9
2021-01-26 19:20 | 1.2512 | 0.32028 | 0.17833 | 0.66926 | 30.52 | 21.3783 |  |  | 477.3925 | 31.76 | 44.1
2021-01-26 19:25 | 1.4682 | 0.35585 | 0.16993 | 0.71538 | 373.9041 | 627.3883 |  |  | 336.5706 | 31.72 | 44.15
2021-01-26 19:30 | 2.0429 | 0.42567 | 0.16784 | 0.82033 | 320.9345 | 171.8562 |  |  | 336.1374 | 31.63 | 44.5
2021-01-26 19:35 | 3.4989 | 0.46817 | 0.15738 | 0.87501 | 156.2821 | 84.0049 |  |  | 337.6911 | 31.57 | 44.96
2021-01-26 19:40 | 2.5671 | 0.47782 | 0.16999 | 0.90241 | 83.1274 | 44.4756 |  |  | 336.6761 | 31.52 | 45.37
2021-01-26 19:45 | 2.7328 | 0.45038 | 0.18675 | 0.87712 | 52.1628 | 43.0297 |  |  | 338.1393 | 31.47 | 45.29
2021-01-26 19:50 | 3.1551 | 0.48612 | 0.23299 | 0.97813 | 34.2238 | 31.2806 |  |  | 336.5197 | 31.45 | 45.98
2021-01-26 19:55 | 2.6047 | 0.54477 | 0.22659 | 1.0616 | 34.3213 | 50.6648 |  |  | 337.2115 | 31.42 | 45.15
2021-01-26 20:00 | 2.5655 | 0.55824 | 0.21602 | 1.0717 | 29.7439 | 26.2825 |  |  | 336.8502 | 31.4 | 44.39
2021-01-26 20:05 | 2.4646 | 0.5681 | 0.19305 | 1.066 | 17.704 | 17.3669 |  |  | 337.1851 | 31.41 | 45.41
2021-01-26 20:10 | 2.809 | 0.49686 | 0.18043 | 0.94203 | 15.618 | 33.3199 |  |  | 336.7357 | 31.39 | 45.2
2021-01-26 20:15 | 1.5576 | 0.54745 | 0.16573 | 1.0049 | 23.9304 | 41.8552 |  |  | 336.79 | 31.37 | 45.05
2021-01-26 20:20 | 1.7243 | 0.61066 | 0.1742 | 1.1123 | 31.1747 | 48.4327 |  |  | 337.5135 | 31.36 | 46.01
2021-01-26 20:25 | 1.4953 | 0.50693 | 0.16591 | 0.94294 | 45.6623 | 45.5498 |  |  | 337.8217 | 31.35 | 47.39
2021-01-26 20:30 | 1.9691 | 0.49483 | 0.16389 | 0.92028 | 50.9421 | 62.3683 |  |  | 338.2393 | 31.29 | 48.57
2021-01-26 20:35 | 1.6228 | 0.50408 | 0.15118 | 0.92386 | 39.5809 | 36.0338 |  |  | 337.0072 | 31.22 | 47.31
2021-01-26 20:40 | 2.2871 | 0.42186 | 0.17846 | 0.8251 | 24.3067 | 17.6116 |  |  | 338.1072 | 31.18 | 47.24
2021-01-26 20:45 | 3.118 | 0.3685 | 0.17218 | 0.73913 | 11.3476 | 18.698 |  |  | 337.5534 | 31.17 | 47.59
2021-01-26 20:50 | 2.2746 | 0.4233 | 0.18268 | 0.83153 | 11.0001 | 37.7641 |  |  | 339.1375 | 31.13 | 47.71
2021-01-26 20:55 | 2.7223 | 0.53845 | 0.19531 | 1.0207 | 25.6944 | 58.2802 |  |  | 338.4127 | 31.12 | 48.1
2021-01-26 21:00 | 2.5441 | 0.5989 | 0.17436 | 1.0945 | 38.179 | 48.4883 |  |  | 337.8268 | 31.1 | 48.75
2021-01-26 21:05 | 3.5665 | 0.55499 | 0.15124 | 0.99984 | 26.292 | 28.6032 |  |  | 338.9346 | 31.06 | 48.64
2021-01-26 21:10 | 1.7389 | 0.54828 | 0.17649 | 1.0169 | 14.2798 | 35.6279 |  |  | 337.906 | 30.98 | 49.43
2021-01-26 21:15 | 1.9308 | 0.49759 | 0.17229 | 0.93501 | 22.6483 | 41.7879 |  |  | 339.0293 | 30.88 | 49.82
2021-01-26 21:20 | 1.9691 | 0.43725 | 0.15128 | 0.82151 | 6.833 | 33.2444 |  |  | 338.1403 | 30.77 | 50.02
2021-01-26 21:25 | 3.1072 | 0.27689 | 0.14708 | 0.5715 | 1.2991 | 7.1708 |  |  | 338.7456 | 30.68 | 50.34
2021-01-26 21:30 | 2.4802 | 0.22613 | 0.12394 | 0.47056 | -13.6537 | 14.3594 |  |  | 339.4884 | 30.53 | 50.38
2021-01-26 21:35 | 4.3716 | 0.29187 | 0.13863 | 0.58602 | -7.7411 | 23.4788 |  |  | 339.1255 | 30.44 | 50.3
2021-01-26 21:40 | 1.304 | 0.18364 | 0.10714 | 0.38863 | -6.4637 | 13.3876 |  |  | 339.6834 | 30.36 | 50.84
2021-01-26 21:45 | 1.7518 | 0.27552 | 0.12817 | 0.5484 | 1.4424 | 37.9109 |  |  | 339.7106 | 30.27 | 51.59
2021-01-26 21:50 | 3.0955 | 0.29207 | 0.12821 | 0.57591 | 26.176 | 57.4685 |  |  | 337.3944 | 30.24 | 52.48
2021-01-26 21:55 | 3.2874 | 0.26602 | 0.1156 | 0.52127 | 21.9807 | 31.9886 |  |  | 338.9839 | 30.2 | 52.62
2021-01-26 22:00 | 3.1206 | 0.20017 | 0.10087 | 0.4056 | 22.5809 | 30.715 |  |  | 339.6758 | 30.09 | 52.6
2021-01-26 22:05 | 1.676 | 0.14127 | 0.086196 | 0.30274 | 21.8013 | 47.4101 |  |  | 339.6603 | 29.99 | 53.76
2021-01-26 22:10 | 1.7918 | 0.11525 | 0.077815 | 0.25448 | 29.5499 | 46.0655 |  |  | 340.1544 | 29.9 | 54.87
2021-01-26 22:15 | 1.4597 | 0.14275 | 0.071536 | 0.28825 | 36.5691 | 48.3798 |  |  | 339.5709 | 29.83 | 56.08
2021-01-26 22:20 | 1.3322 | 0.14281 | 0.082087 | 0.30309 | 35.4866 | 55.889 |  |  | 339.4862 | 29.79 | 57.09
2021-01-26 22:25 | 1.8571 | 0.14142 | 0.07787 | 0.29254 | 47.7581 | 53.4346 |  |  | 339.0823 | 29.72 | 57.09
2021-01-26 22:30 | 1.5371 | 0.1126 | 0.067354 | 0.23995 | 55.0902 | 72.142 |  |  | 340.6274 | 29.69 | 57.44
2021-01-26 22:35 | 1.9472 | 0.10437 | 0.082095 | 0.23997 | 47.7573 | 60.7112 |  |  | 339.6215 | 29.64 | 57.81
2021-01-26 22:40 | 2.0365 | 0.05904 | 0.079976 | 0.17047 | 47.5437 | 48.845 |  |  | 340.7943 | 29.57 | 57.62
2021-01-26 22:45 | 2.165 | 0.056306 | 0.075783 | 0.16209 | 48.0971 | 35.2145 |  |  | 339.4582 | 29.47 | 58.4
2021-01-26 22:50 | 1.6404 | 0.072813 | 0.088446 | 0.20006 | 27.1998 | 25.4671 |  |  | 339.4227 | 29.39 | 59.54
2021-01-26 22:55 | 2.2808 | 0.07555 | 0.090539 | 0.20634 | 18.9848 | 19.0771 |  |  | 339.562 | 29.31 | 59.47
2021-01-26 23:00 | 0.62798 | 0.056329 | 0.080025 | 0.16637 | 17.7782 | 13.267 |  |  | 340.0759 | 29.26 | 60.05
2021-01-26 23:05 | 1.8973 | 0.12094 | 0.080049 | 0.26332 | 23.3115 | 52.2023 |  |  | 341.0046 | 29.26 | 60.77
2021-01-26 23:10 | 1.3719 | 0.11133 | 0.088484 | 0.25913 | 28.6371 | 29.191 |  |  | 339.4465 | 29.24 | 61.07
2021-01-26 23:15 | 1.2952 | 0.13747 | 0.088504 | 0.29712 | 20.5388 | 15.6145 |  |  | 339.3694 | 29.24 | 61.61
2021-01-26 23:20 | 0.91065 | 0.1155 | 0.088518 | 0.26556 | 11.8616 | 32.5577 |  |  | 338.8087 | 29.23 | 62.04
2021-01-26 23:25 | 1.193 | 0.14164 | 0.094852 | 0.31196 | 17.702 | 32.541 |  |  | 339.8456 | 29.19 | 62.46
2021-01-26 23:30 | 1.1931 | 0.23242 | 0.099079 | 0.45534 | 17.8271 | 27.8029 |  |  | 340.347 | 29.17 | 62.79
2021-01-26 23:35 | 0.61583 | 0.17054 | 0.088544 | 0.34996 | 15.2315 | 13.2608 |  |  | 339.3172 | 29.15 | 63.01
2021-01-26 23:40 | 0.64154 | 0.22282 | 0.078009 | 0.42167 | 19.7183 | 25.0045 |  |  | 338.7867 | 29.14 | 63.23
2021-01-26 23:45 | 0.38497 | 0.19534 | 0.090671 | 0.39009 | 19.0535 | 18.4273 |  |  | 338.7091 | 29.17 | 63.43
2021-01-26 23:50 |  | 0.16231 | 0.082228 | 0.32891 | 8.9613 | 6.2 |  |  | 339.2681 | 29.16 | 63.24
2021-01-26 23:55 | 0.80842 | 0.12931 | 0.078017 | 0.27622 | 13.2632 | 16.579 |  |  | 337.7201 | 29.14 | 63.48
2021-01-27 | 0.83416 | 0.12106 | 0.082241 | 0.26992 | 8.2749 | 14.3629 |  |  | 338.7552 | 29.11 | 63.8
2021-01-27 00:05
2021-01-27 00:10
2021-01-27 00:15 | 0.41058 | 0.068773 | 0.069576 | 0.1771 | 3.9621 | 15.3969 |  |  | 340.0763 | 28.91 | 64.08
2021-01-27 00:20 | 0.25657 | 0.049507 | 0.067454 | 0.14334 | -1.2828 | 2.032 |  |  | 339.7032 | 28.84 | 63.88
2021-01-27 00:25 | 0.43616 | 0.03713 | 0.065346 | 0.12226 | 5.8087 | -2.2065 |  |  | 339.7263 | 28.82 | 63.95
2021-01-27 00:30 | 0.80826 | 0.02063 | 0.065353 | 0.096975 | 2.0322 | 10.859 |  |  | 340.0689 | 28.79 | 64.37
2021-01-27 00:35 | 0.56432 | 0.020623 | 0.061117 | 0.092729 | 3.2833 | 17.6477 |  |  | 340.2142 | 28.76 | 63.68
2021-01-27 00:40 | 0.56428 | 0.038494 | 0.073757 | 0.13276 | 19.8524 | 3.8268 |  |  | 340.7535 | 28.76 | 63.52
2021-01-27 00:45 | 0.53883 | 0.033007 | 0.065352 | 0.11595 | 8.2724 | 3.1714 |  |  | 340.0867 | 28.78 | 64.36
2021-01-27 00:50 | 0.52596 | 0.045381 | 0.063238 | 0.1328 | 4.1871 | 13.2489 |  |  | 339.6345 | 28.75 | 64.25
2021-01-27 00:55 | 0.83384 | 0.046757 | 0.063239 | 0.13491 | 14.7269 | 14.7167 |  |  | 340.2031 | 28.7 | 64.47
2021-01-27 01:00 | 0.62873 | 0.045392 | 0.06747 | 0.13705 | 10.7475 | 8.3968 |  |  | 340.6657 | 28.68 | 65.1
2021-01-27 01:05 |  |  |  |  | 14.1038 | 17.2449 |  |  | 339.1778 | 28.63 | 65.24
2021-01-27 01:10 |  |  |  |  | 18.0952 | 13.5586 |  |  | 338.7142 | 28.61 | 65.09
2021-01-27 01:15 |  |  |  |  | 11.7942 | 3.8288 |  |  | 339.7072 | 28.62 | 65.27
2021-01-27 01:20 |  |  |  |  | 15.585 | 32.8742 |  |  | 340.1236 | 28.65 | 65.64
2021-01-27 01:25 |  |  |  |  | 25.112 | 19.5886 |  |  | 339.659 | 28.61 | 65.74
2021-01-27 01:30 |  |  |  |  | 15.7296 | 2.9262 |  |  | 339.6893 | 28.56 | 66.12
2021-01-27 01:35 |  |  |  |  | 12.3618 | 10.2878 |  |  | 339.2191 | 28.52 | 66.26
2021-01-27 01:40 |  |  |  |  | 14.3757 | 7.9272 |  |  | 339.7352 | 28.49 | 66.63
2021-01-27 01:45 |  |  |  |  | 5.0116 | 0.70861 |  |  | 340.2195 | 28.48 | 66.99
2021-01-27 01:50 |  |  |  |  | 6.9631 | 6.121 |  |  | 340.2518 | 28.44 | 67.24
2021-01-27 01:55 |  |  |  |  | 8.289 | 11.5553 |  |  | 339.1976 | 28.42 | 67.63
2021-01-27 02:00 |  |  |  |  | 3.3694 | 10.6732 |  |  | 339.1135 | 28.46 | 67.76
2021-01-27 02:05 |  |  |  |  | 13.3759 | 5.4243 |  |  | 339.0179 | 28.52 | 67.73
2021-01-27 02:10 | 0.29535 | 0.097738 | 0.071743 | 0.22156 | 12.3174 | 10.1292 | 1.2396 | -0.007335 | 339.5457 | 28.52 | 67.65
2021-01-27 02:15 | 0.51364 | 0.070204 | 0.069631 | 0.17724 | 8.095 | 17.9671 | 1.2176 | 0 | 339.0594 | 28.5 | 67.67
2021-01-27 02:20 | -0.012839 | 0.046797 | 0.067513 | 0.13925 | 9.2958 | 2.9582 | 1.2101 | -0.0073339 | 338.639 | 28.45 | 67.57
2021-01-27 02:25 | 0.26961 | 0.039912 | 0.050631 | 0.11181 | 4.3651 | -10.2707 | 1.1953 | -0.022 | 338.7232 | 28.4 | 67.56
2021-01-27 02:30 | 0.42369 | 0.059183 | 0.056962 | 0.14768 | 1.7461 | 10.1377 | 1.1734 | 0.0073336 | 339.776 | 28.37 | 67.79
2021-01-27 02:35 | 0.59065 | 0.083964 | 0.082286 | 0.21099 | 8.6799 | 14.9049 | 1.1662 | 0.022003 | 339.1718 | 28.42 | 67.82
2021-01-27 02:40 | 0.5649 | 0.059181 | 0.065399 | 0.15611 | 17.4708 | -5.6901 | 1.1514 | 0.014667 | 338.683 | 28.43 | 67.49
2021-01-27 02:45 | 0.94996 | 0.092203 | 0.056954 | 0.19829 | 8.3083 | 12.0773 | 1.1439 | 0.021998 | 339.8098 | 28.38 | 67.42
2021-01-27 02:50 | 0.82156 | 0.14724 | 0.082265 | 0.30797 | 6.4287 | 23.0859 | 1.1439 | 0.02933 | 340.8662 | 28.37 | 67.38
2021-01-27 02:55 | 1.181 | 0.082564 | 0.071716 | 0.19827 | 19.5422 | 10.1048 | 1.1438 | 0.036661 | 340.3836 | 28.35 | 67.37
2021-01-27 03:00 | [9 empty] | 28.36 | 67.46
2021-01-27 03:05 | 1.7712 | 0.16648 | 0.08647 | 0.34166 | 11.7567 | 14.0054 | 1.173 | 0.051319 | 338.8959 | 28.33 | 67.14
2021-01-27 03:10 | 1.3218 | 0.14995 | 0.073804 | 0.30576 | 22.7191 | 12.6069 | 1.1801 | 0.03665 | 340.0432 | 28.28 | 66.92
2021-01-27 03:15 | 0.69299 | 0.27652 | 0.10965 | 0.53351 | 18.0998 | 9.5889 | 1.1875 | 0.036651 | 340.0102 | 28.3 | 66.92
2021-01-27 03:20 | 0.62877 | 0.21047 | 0.084342 | 0.40695 | 8.4794 | 13.1194 | 1.1874 | 0.029319 | 339.4891 | 28.33 | 66.58
2021-01-27 03:25 | 0.60305 | 0.20494 | 0.082226 | 0.39637 | 16.8751 | 13.2619 | 1.1873 | 0.036645 | 340.0489 | 28.32 | 66.39
2021-01-27 03:30 | 0.65416 | 0.1705 | 0.088523 | 0.34777 | 10.9078 | 9.2044 | 1.1869 | 0.02198 | 340.6985 | 28.3 | 65.66
2021-01-27 03:35 | 0.83356 | 0.28457 | 0.10536 | 0.54156 | 7.879 | 15.5119 | 1.1867 | 0.0293 | 340.0779 | 28.3 | 65.19
2021-01-27 03:40 | 1.0772 | 0.34641 | 0.094821 | 0.62792 | 21.1328 | 3.5392 | 1.1939 | 0.036623 | 339.5209 | 28.35 | 64.87
2021-01-27 03:45 | 1.0896 | 0.28719 | 0.098997 | 0.53922 | 14.5309 | 18.7046 | 1.1861 | 0.043931 | 340.2034 | 28.32 | 64.02
2021-01-27 03:50 | 1.0509 | 0.29813 | 0.080025 | 0.53912 | 4.6138 | 3.7218 | 1.1859 | 0.051244 | 340.3106 | 28.28 | 63.71
2021-01-27 03:55 | 0.98672 | 0.31321 | 0.086333 | 0.56643 |  |  | 1.1785 | 0.029279 | 435.9025 | 28.22 | 63.63
2021-01-27 04:00 | 1.4095 | 0.28159 | 0.10317 | 0.5369 |  |  | 1.1637 | 0.036595 | 484.1724 | 28.24 | 63.34
2021-01-27 04:05 | 1.4222 | 0.55078 | 0.12422 | 0.96847 |  | 0.21525 | 1.1563 | 0.14637 | 483.7304 | 28.21 | 63.3
2021-01-27 04:10 | 0.84551 | 0.47517 | 0.098938 | 0.82729 |  | -1.0044 | 1.1708 | 0.13172 | 482.2918 | 28.18 | 63.04
2021-01-27 04:15 | 1.5754 | 0.51078 | 0.10313 | 0.88606 | 4.0679 | 2.8691 | 1.1925 | 0.11706 | 484.5892 | 28.1 | 62.85
2021-01-27 04:20 | 1.7157 | 0.50373 | 0.13886 | 0.90889 | 12.8038 | 25.1672 | 1.1921 | 0.080449 | 484.7929 | 28.08 | 62.02
2021-01-27 04:25 | 1.6384 | 0.76427 | 0.14092 | 1.3124 | 43.0376 | 67.2751 | 1.2063 | 0.11698 | 484.9334 | 28.09 | 61.16
2021-01-27 04:30 | 2.0607 | 0.92342 | 0.17667 | 1.5921 | 50.6449 | 64.714 | 1.2063 | 0.13891 | 484.8934 | 28.12 | 61.01
2021-01-27 04:35 | 2.5722 | 0.91366 | 0.18295 | 1.5834 | 63.7609 | 52.2946 | 1.2061 | 0.15351 | 484.8975 | 28.17 | 60.39
2021-01-27 04:40 | 3.9666 | 0.81478 | 0.18502 | 1.4318 | 58.4907 | 21.8444 | 1.2133 | 0.19734 | 482.8042 | 28.22 | 59.87
2021-01-27 04:45 | 4.5164 | 0.9834 | 0.24387 | 1.7492 | 51.8938 | 65.333 | 1.2205 | 0.25578 | 483.7747 | 28.29 | 59.4
2021-01-27 04:50 | 3.5185 | 0.98616 | 0.30275 | 1.8123 | 80.6363 | 82.4173 | 1.2278 | 0.30695 | 484.1096 | 28.38 | 59.19
2021-01-27 04:55 | 2.8025 | 1.2511 | 0.33855 | 2.2563 | 83.4055 | 66.9128 | 1.2134 | 0.19736 | 483.8574 | 28.48 | 59.32
2021-01-27 05:00 | 2.0598 | 1.5292 | 0.3679 | 2.712 | 78.6569 | 62.209 | 1.2204 | 0.21193 | 482.8055 | 28.56 | 58.45
2021-01-27 05:05 | 2.8278 | 1.5898 | 0.39528 | 2.8322 | 93.4484 | 91.2783 | 1.2279 | 0.2485 | 484.222 | 28.61 | 58.6
2021-01-27 05:10 | 3.4036 | 1.5884 | 0.44153 | 2.8763 | 91.4516 | 79.5876 | 1.2206 | 0.26312 | 483.6263 | 28.66 | 58.41
2021-01-27 05:15 | 3.2492 | 1.6113 | 0.44983 | 2.9197 | 98.1104 | 73.1914 | 1.2202 | 0.26305 | 481.5461 | 28.74 | 57.5
2021-01-27 05:20 | 3.9284 | 1.9301 | 0.53408 | 3.4946 | 92.0404 | 85.9187 | 1.2133 | 0.2412 | 481.2493 | 28.83 | 57.98
2021-01-27 05:25 | 4.8483 | 2.4423 | 0.618 | 4.3617 | 108.847 | 121.7416 | 1.2203 | 0.30689 | 481.7876 | 28.91 | 56.97
2021-01-27 05:30 | 7.0733 | 2.4777 | 0.64525 | 4.4453 | 132.9632 | 126.1483 | 1.2274 | 0.37261 | 482.2341 | 28.99 | 56.43
2021-01-27 05:35 | 5.5637 | 2.9575 | 0.73559 | 5.2668 | 123.2257 | 26.2148 | 1.2493 | 0.3872 | 482.7296 | 29.02 | 56.21
2021-01-27 05:40 | 4.4123 | 2.7283 | 0.68931 | 4.8714 | 138.923 |  | 1.2492 | 0.35796 | 480.6688 | 29.03 | 56.02
2021-01-27 05:45 | 4.7327 | 3.0784 | 0.72513 | 5.4438 | 158.9988 | 113.2782 | 1.2567 | 0.33609 | 480.5501 | 29.04 | 56.38
2021-01-27 05:50 | 5.8459 | 3.1554 | 0.75671 | 5.5934 | 176.3757 | 169.9388 | 1.2568 | 0.44571 | 481.366 | 29.16 | 56.15
2021-01-27 05:55 | 6.1523 | 3.9448 | 0.72511 | 6.774 | 207.7522 | 170.3828 | 1.2347 | 0.49681 | 479.1453 | 29.28 | 55.53
2021-01-27 06:00 | 7.5333 | 4.2709 | 0.84066 | 7.3873 | 205.4275 | 183.173 | 1.242 | 0.49678 | 477.7718 | 29.51 | 54.66
2021-01-27 06:05 | 5.8585 | 3.3033 | 0.83445 | 5.8979 | 198.2169 | 164.2836 | 1.359 | 0.46031 | 479.4893 | 29.7 | 54.34
2021-01-27 06:10 | 5.9613 | 3.3132 | 0.86185 | 5.9425 | 180.7738 | 127.6899 | 1.2934 | 0.40189 | 478.287 | 29.78 | 54.28
2021-01-27 06:15 | 5.4233 | 3.8461 | 0.83441 | 6.732 | 166.8631 | 162.5142 | 1.2566 | 0.48951 | 478.2272 | 29.86 | 53.71
2021-01-27 06:20 | 8.0585 | 4.2275 | 0.86176 | 7.3418 | 198.0399 | 199.5646 | 1.2567 | 0.65757 | 479.6349 | 29.94 | 53.56
2021-01-27 06:25 | 6.5636 | 3.0641 | 0.72323 | 5.4221 | 204.1098 | 163.7812 | 1.2424 | 0.51889 | 479.9494 | 29.99 | 54
2021-01-27 06:30 | 8.137 | 2.9323 | 0.76524 | 5.2621 | 187.7036 | 151.1536 | 1.257 | 0.48232 | 477.8216 | 30.04 | 53.74
2021-01-27 06:35 | 8.6882 | 3.4772 | 0.68544 | 6.0133 | 180.1715 | 153.1064 | 1.2644 | 0.50431 | 479.1544 | 30.12 | 53.82
2021-01-27 06:40 | 5.9896 | 2.8002 | 0.5615 | 4.8517 | 162.2004 | 112.1437 | 1.272 | 0.43862 | 479.459 | 30.19 | 54.09
2021-01-27 06:45 | 5.9127 | 2.9909 | 0.64141 | 5.2259 | 163.815 | 154.365 | 1.3451 | 0.46055 | 478.4639 | 30.17 | 54.11
2021-01-27 06:50 | 7.6934 | 3.0753 | 0.69625 | 5.4101 | 168.5951 | 144.4677 | 1.3162 | 0.54109 | 478.304 | 30.2 | 54.55
2021-01-27 06:55 | 6.8964 | 2.9668 | 0.6875 | 5.2351 | 162.76 | 138.1019 | 1.279 | 0.53351 | 478.5385 | 30.2 | 53.44
2021-01-27 07:00 | 8.2533 | 3.5363 | 0.69806 | 6.1186 | 163.9907 | 142.6473 | 1.2864 | 0.50432 | 477.3557 | 30.27 | 53.4
2021-01-27 07:05 | 6.8489 | 3.037 | 0.6437 | 5.301 | 177.3502 | 149.8009 | 1.2577 | 0.43143 | 479.0295 | 30.38 | 54.11
2021-01-27 07:10 | 9.0485 | 2.6315 | 0.52366 | 4.5594 | 159.8166 | 127.3086 | 1.2501 | 0.4898 | 479.6549 | 30.39 | 53.5
2021-01-27 07:15 | 7.844 | 2.6132 | 0.51936 | 4.5249 | 141.8633 | 126.6717 | 1.3156 | 0.54819 | 479.6929 | 30.42 | 53.01
2021-01-27 07:20 | 6.9989 | 2.5965 | 0.54665 | 4.5267 | 138.2584 | 121.6862 | 1.3302 | 0.47506 | 478.1969 | 30.41 | 52.85
2021-01-27 07:25 | 8.2758 | 2.5916 | 0.41826 | 4.3928 | 171.8291 | 179.5958 | 1.2274 | 0.51144 | 478.7091 | 30.51 | 51.84
2021-01-27 07:30 | 8.713 | 2.9008 | 0.50457 | 4.9511 | 196.1736 | 180.4928 | 1.2205 | 0.65043 | 479.0161 | 30.54 | 52.39
2021-01-27 07:35 | 10.2038 | 2.762 | 0.50637 | 4.7401 | 166.6368 | 108.8919 | 1.2416 | 0.64273 | 480.9038 | 30.51 | 51.15
2021-01-27 07:40 | 7.8645 | 2.4209 | 0.4917 | 4.2047 | 141.2893 | 104.7368 | 1.2417 | 0.43826 | 478.6987 | 30.57 | 51.15
2021-01-27 07:45 | 6.5465 | 2.6468 | 0.52315 | 4.5823 | 121.9492 | 103.5474 | 1.2197 | 0.38708 | 479.8421 | 30.54 | 50.96
2021-01-27 07:50 | 6.9565 | 2.7403 | 0.5001 | 4.6985 | 137.3092 | 101.4218 | 1.2198 | 0.40174 | 478.214 | 30.55 | 51.2
2021-01-27 07:55 | 6.8293 | 2.9051 | 0.49805 | 4.9511 | 135.0919 | 127.8175 | 1.2199 | 0.4383 | 478.2 | 30.53 | 51.47
2021-01-27 08:00 | 7.5293 | 2.9586 | 0.52933 | 5.0623 | 160.73 | 164.2173 | 1.2194 | 0.45271 | 480.0186 | 30.5 | 50.55
2021-01-27 08:05 | 7.0175 | 2.6117 | 0.49359 | 4.4949 | 179.1579 | 141.7515 | 1.2266 | 0.39427 | 479.5127 | 30.51 | 50.39
2021-01-27 08:10 | 6.2168 | 2.375 | 0.44981 | 4.0904 | 163.6516 | 123.803 | 1.2202 | 0.3361 | 480.2004 | 30.51 | 52.01
2021-01-27 08:15 | 7.1013 | 2.7323 | 0.53613 | 4.7243 | 149.8046 | 130.7143 | 1.2278 | 0.41659 | 480.1208 | 30.48 | 52.69
2021-01-27 08:20 | 5.835 | 2.5254 | 0.53617 | 4.405 | 147.2663 | 117.5387 | 1.2279 | 0.43854 | 480.636 | 30.46 | 52.91
2021-01-27 08:25 | 5.6905 | 2.2468 | 0.4854 | 3.9315 | 113.4733 | 62.4553 | 1.2198 | 0.40904 | 479.9564 | 30.43 | 51.56
2021-01-27 08:30 | 5.4209 | 1.9763 | 0.48109 | 3.5105 | 107.5477 | 81.6503 | 1.2269 | 0.47468 | 480.7031 | 30.35 | 51.32
2021-01-27 08:35 | 6.1733 | 1.7045 | 0.50615 | 3.1188 | 100.5116 | 79.0186 | 1.263 | 0.36503 | 481.5238 | 30.25 | 50.94
2021-01-27 08:40 | 5.1005 | 1.7609 | 0.49573 | 3.197 | 92.9706 | 72.9672 | 1.2559 | 0.33588 | 479.9358 | 30.22 | 51.4
2021-01-27 08:45 | 5.9744 | 2.0188 | 0.50873 | 3.6031 | 100.7493 | 84.5889 | 1.2569 | 0.44576 | 481.1985 | 30.17 | 53.31
2021-01-27 08:50 | 9.5999 | 1.8321 | 0.49571 | 3.3041 | 94.2556 | 71.8498 | 1.2486 | 0.36508 | 481.1501 | 30.12 | 51.61
2021-01-27 08:55 | 7.6963 | 1.8776 | 0.45376 | 3.3318 | 99.8113 | 85.9017 | 1.2633 | 0.2994 | 481.5857 | 30.11 | 51.99
2021-01-27 09:00 | 5.3335 | 1.8194 | 0.41613 | 3.205 | 131.8808 | 107.416 | 1.242 | 0.29953 | 481.9122 | 30.1 | 53.01
2021-01-27 09:05 | 4.6173 | 1.7578 | 0.43505 | 3.1294 | 110.8661 | 85.746 | 1.2274 | 0.36529 | 480.3777 | 30.08 | 53.11
2021-01-27 09:10 | 5.0392 | 1.8194 | 0.39721 | 3.1861 | 98.7177 | 66.4871 | 1.2346 | 0.3872 | 480.518 | 30 | 53.29
2021-01-27 09:15 | 3.7473 | 1.5726 | 0.36777 | 2.7783 | 67.5589 | 43.8729 | 1.2492 | 0.34335 | 482.2537 | 29.9 | 53.51
2021-01-27 09:20 | 4.2845 | 1.7165 | 0.42031 | 3.0536 | 57.6854 | 46.5637 | 1.2565 | 0.34335 | 483.845 | 29.88 | 53.57
2021-01-27 09:25 | 6.4082 | 2.2775 | 0.4687 | 3.9598 | 73.9927 | 60.8334 | 1.2494 | 0.3507 | 481.1602 | 29.9 | 53.77
2021-01-27 09:30 | 4.9124 | 2.0132 | 0.44564 | 3.5315 | 73.0617 | 83.3265 | 1.2495 | 0.28498 | 481.0915 | 29.9 | 54.1
2021-01-27 09:35 | 3.684 | 1.4467 | 0.39726 | 2.6148 | 87.3304 | 75.2961 | 1.2421 | 0.2265 | 483.7331 | 29.9 | 53.89
2021-01-27 09:40 | 3.1977 | 1.3643 | 0.37622 | 2.4675 | 94.1006 | 89.7926 | 1.2494 | 0.21188 | 482.2597 | 29.86 | 53.91
2021-01-27 09:45 | 5.4232 | 1.7208 | 0.45188 | 3.0917 | 96.544 | 87.1403 | 1.2566 | 0.35069 | 481.279 | 29.83 | 53.95
2021-01-27 09:50 | 4.911 | 2.0085 | 0.5485 | 3.6272 | 101.2595 | 67.2403 | 1.2638 | 0.40178 | 482.4229 | 29.8 | 53.77
2021-01-27 09:55 | 4.0034 | 1.9882 | 0.4771 | 3.5246 | 98.6409 | 77.2653 | 1.2566 | 0.32146 | 481.9299 | 29.75 | 54.18
2021-01-27 10:00 | 3.1458 | 1.7725 | 0.4833 | 3.2003 | 76.1853 | 74.9373 | 1.2564 | 0.33601 | 483.1013 | 29.73 | 53.76
2021-01-27 10:05 | 3.8494 | 1.5245 | 0.37406 | 2.713 | 83.5061 | 67.3614 | 1.2638 | 0.36525 | 482.5623 | 29.72 | 53.96
2021-01-27 10:10 | 4.0037 | 1.4302 | 0.32579 | 2.5159 | 72.8801 | 48.6277 | 1.264 | 0.31418 | 483.5071 | 29.72 | 54.42
2021-01-27 10:15 | 3.121 | 1.5535 | 0.32367 | 2.705 | 67.9958 | 57.9883 | 1.264 | 0.26302 | 484.6652 | 29.66 | 54.5
2021-01-27 10:20 | 4.2986 | 1.9228 | 0.39521 | 3.3425 | 71.6426 | 63.2092 | 1.2569 | 0.21923 | 483.5892 | 29.6 | 55.21
2021-01-27 10:25 | 4.8492 | 1.6432 | 0.46463 | 2.9812 | 64.8739 | 64.8637 | 1.2351 | 0.22656 | 484.0439 | 29.61 | 55.42
2021-01-27 10:30 | 3.0818 | 1.4256 | 0.42865 | 2.6118 | 62.4538 | 53.0934 | 1.2052 | 0.23373 | 484.8853 | 29.58 | 54.19
2021-01-27 10:35 | 4.2208 | 1.6536 | 0.44977 | 2.9823 | 80.0368 | 66.3256 | 1.1982 | 0.29223 | 485.3438 | 29.55 | 54.82
2021-01-27 10:40 | 4.5032 | 1.8308 | 0.45617 | 3.2626 | 85.3248 | 88.5282 | 1.2057 | 0.37268 | 482.6521 | 29.54 | 55.36
2021-01-27 10:45 | 4.3491 | 1.6908 | 0.37414 | 2.9658 | 83.5849 | 67.2117 | 1.2056 | 0.35802 | 484.8107 | 29.53 | 55.1
2021-01-27 10:50 | 4.7076 | 1.503 | 0.33002 | 2.6339 | 113.0028 | 103.301 | 1.213 | 0.36535 | 482.695 | 29.53 | 55.26
2021-01-27 10:55 | 4.5673 | 1.6129 | 0.32375 | 2.796 | 112.5128 | 86.5468 | 1.2204 | 0.41654 | 484.7923 | 29.49 | 55.63
2021-01-27 11:00 | 3.4804 | 1.7036 | 0.37005 | 2.9814 | 88.8321 | 61.3062 | 1.2206 | 0.40199 | 483.6629 | 29.5 | 55.95
2021-01-27 11:05 | 2.9956 | 1.5178 | 0.40179 | 2.7284 | 63.8661 | 35.5995 | 1.2139 | 0.30712 | 483.3926 | 29.52 | 57.05
2021-01-27 11:10 | 3.1359 | 1.5464 | 0.34283 | 2.7132 | 64.2334 | 44.8088 | 1.2063 | 0.29244 | 482.4233 | 29.53 | 56.59
2021-01-27 11:15 | 3.391 | 1.5898 | 0.34483 | 2.7818 | 73.0503 | 71.873 | 1.1987 | 0.33622 | 482.6033 | 29.5 | 56.04
2021-01-27 11:20 | 3.3636 | 1.7563 | 0.41821 | 3.1103 | 92.5548 | 93.2403 | 1.2054 | 0.40179 | 484.4474 | 29.48 | 54.88
2021-01-27 11:25 | 3.5025 | 1.8774 | 0.4201 | 3.2978 | 95.8316 | 50.9889 | 1.2121 | 0.36508 | 481.0123 | 29.5 | 53.62
2021-01-27 11:30 | 3.7328 | 1.8226 | 0.39701 | 3.1887 | 83.7676 | 56.5541 | 1.2048 | 0.30668 | 482.9515 | 29.58 | 53.46
2021-01-27 11:35 | 3.2194 | 2.1241 | 0.40936 | 3.6653 | 69.1002 | 62.1912 | 1.2114 | 0.32838 | 484.2474 | 29.61 | 51.9
2021-01-27 11:40 | 2.7455 | 1.8618 | 0.39239 | 3.2462 | 80.2363 | 73.9433 | 1.24 | 0.29177 | 483.4142 | 29.61 | 50.88
2021-01-27 11:45 | 2.8092 | 1.6194 | 0.39447 | 2.8767 | 83.8377 | 52.0167 | 1.2545 | 0.26987 | 484.5334 | 29.58 | 50.83
2021-01-27 11:50 | 3.1406 | 1.4562 | 0.36082 | 2.5929 | 82.0947 | 78.2953 | 1.2543 | 0.27711 | 484.1577 | 29.55 | 50.44
2021-01-27 11:55 | 2.9495 | 1.4673 | 0.3273 | 2.5765 | 84.6078 | 56.1396 | 1.2544 | 0.28444 | 482.6419 | 29.48 | 50.95
2021-01-27 12:00 | 2.6813 | 1.6904 | 0.41752 | 3.0087 | 77.5802 | 39.9597 | 1.2544 | 0.26256 | 484.2072 | 29.48 | 50.95
2021-01-27 12:05 | 2.7964 | 1.8205 | 0.44901 | 3.2396 | 85.929 | 53.3225 | 1.2545 | 0.25527 | 484.0599 | 29.56 | 50.81
2021-01-27 12:10 | 2.5792 | 1.5631 | 0.41542 | 2.8114 | 81.7275 | 69.7661 | 1.2617 | 0.24068 | 484.6159 | 29.55 | 50.75
2021-01-27 12:15 | 2.6046 | 1.4631 | 0.36504 | 2.6057 | 68.0454 | 48.9657 | 1.2544 | 0.22608 | 483.0679 | 29.56 | 50.56
2021-01-27 12:20 | 3.7418 | 1.5237 | 0.36094 | 2.6966 | 71.445 | 49.4486 | 1.262 | 0.28449 | 482.9569 | 29.55 | 51.21
2021-01-27 12:25 | 4.4048 | 1.7409 | 0.4049 | 3.0735 | 61.1507 | 48.4548 | 1.2544 | 0.32817 | 484.619 | 29.57 | 50.52
2021-01-27 12:30 | 3.5497 | 1.8835 | 0.41333 | 3.3004 | 65.9982 | 52.392 | 1.2618 | 0.24798 | 484.0365 | 29.58 | 50.71
2021-01-27 12:35 | 2.9123 | 1.661 | 0.43238 | 2.9763 | 88.7492 | 76.2517 | 1.2695 | 0.21888 | 482.7973 | 29.59 | 51.56
2021-01-27 12:40 | 2.5406 | 1.4713 | 0.48671 | 2.7419 | 70.658 | 45.2158 | 1.2616 | 0.16044 | 484.7601 | 29.49 | 50.69
2021-01-27 12:45 | 9.2328 | 1.7742 | 0.59385 | 3.3134 | 75.4155 | 69.674 | 1.2473 | 0.19695 | 485.1314 | 29.51 | 51.21
2021-01-27 12:50 | 5.2607 | 2.2722 | 0.4553 | 3.9382 | 78.5534 | 62.6588 | 1.2326 | 0.21881 | 484.5836 | 29.56 | 50.8
2021-01-27 12:55 | 2.8211 | 1.95 | 0.40693 | 3.396 | 77.1318 | 63.5191 | 1.225 | 0.24791 | 485.3081 | 29.52 | 50.24
2021-01-27 13:00 | 2.9366 | 1.6069 | 0.34617 | 2.8092 | 73.4713 | 74.1556 | 1.2325 | 0.26255 | 485.1513 | 29.53 | 50.77
2021-01-27 13:05 | 3.1905 | 1.8415 | 0.44877 | 3.2714 | 62.7178 | 23.8497 | 1.2465 | 0.25514 | 483.756 | 29.56 | 49.61
2021-01-27 13:10 | 2.9607 | 2.0835 | 0.51796 | 3.7117 | 68.9742 | 50.6178 | 1.2392 | 0.24784 | 484.2456 | 29.59 | 49.45
2021-01-27 13:15 | 2.8589 | 2.4669 | 0.44881 | 4.2322 | 78.9369 | 60.7827 | 1.2321 | 0.2989 | 485.2055 | 29.61 | 49.65
2021-01-27 13:20 | 3.6876 | 2.4567 | 0.4466 | 4.2123 | 75.6103 | 52.5301 | 1.2463 | 0.379 | 486.9392 | 29.58 | 49.16
2021-01-27 13:25 | 3.8945 | 1.9232 | 0.36718 | 3.3151 | 82.191 | 51.7703 | 1.2472 | 0.32821 | 486.6769 | 29.53 | 50.97
2021-01-27 13:30 | 4.0845 | 1.6255 | 0.35236 | 2.8441 | 73.0104 | 59.4703 | 1.2467 | 0.29892 | 486.4683 | 29.45 | 50.3
2021-01-27 13:35 | 4.1608 | 1.5269 | 0.35653 | 2.697 | 73.6994 | 52.3084 | 1.2466 | 0.32077 | 487.107 | 29.4 | 50.27
2021-01-27 13:40 | 3.3706 | 1.3413 | 0.37343 | 2.4294 | 82.1296 | 55.6655 | 1.2471 | 0.29171 | 485.5081 | 29.32 | 51.29
2021-01-27 13:45 | 3.8439 | 1.6181 | 0.36932 | 2.8496 | 72.188 | 53.9111 | 1.2692 | 0.36472 | 484.4138 | 29.28 | 51.97
2021-01-27 13:50 | 3.0276 | 1.8337 | 0.45971 | 3.2704 | 87.2046 | 84.7213 | 1.2915 | 0.29187 | 486.7815 | 29.33 | 52.63
2021-01-27 13:55 | 2.7469 | 1.6723 | 0.3275 | 2.8908 | 70.6777 | 50.0416 | 1.2771 | 0.24083 | 485.2044 | 29.3 | 53.01
2021-01-27 14:00 | 3.1172 | 1.5736 | 0.37996 | 2.7899 | 52.4091 | 47.8714 | 1.2551 | 0.24081 | 486.3644 | 29.25 | 52.99
2021-01-27 14:05 | 3.117 | 1.5406 | 0.44711 | 2.8065 | 55.1445 | 51.0975 | 1.2477 | 0.25539 | 484.8132 | 29.26 | 52.8
2021-01-27 14:10 | 2.9634 | 1.676 | 0.41768 | 2.9867 | 58.1437 | 66.1551 | 1.2549 | 0.27725 | 485.3639 | 29.27 | 52.55
2021-01-27 14:15 | 3.5106 | 1.4424 | 0.35241 | 2.5613 | 57.2221 | 33.4468 | 1.2615 | 0.29168 | 486.1792 | 29.26 | 51.21
2021-01-27 14:20 | 3.4325 | 1.3063 | 0.30822 | 2.3106 | 52.9189 | 18.1194 | 1.2609 | 0.26968 | 485.9577 | 29.21 | 50.26
2021-01-27 14:25 | 3.8655 | 1.3102 | 0.31444 | 2.3227 | 51.8663 | 53.4074 | 1.2679 | 0.28419 | 486.1118 | 29.18 | 49.82
2021-01-27 14:30 | 4.1718 | 1.4976 | 0.32493 | 2.6204 | 60.1043 | 51.776 | 1.3263 | 0.4008 | 485.5904 | 29.17 | 49.92
2021-01-27 14:35 | 3.5235 | 1.6847 | 0.33774 | 2.9222 | 72.3078 | 68.1001 | 1.349 | 0.34273 | 487.2307 | 29.25 | 51.29
2021-01-27 14:40 | 3.7036 | 1.7853 | 0.36305 | 3.0996 | 83.7988 | 84.9942 | 1.3204 | 0.33556 | 486.4415 | 29.3 | 52.06
2021-01-27 14:45 | 3.895 | 1.8071 | 0.39661 | 3.1645 | 97.8626 | 78.8193 | 1.2911 | 0.31366 | 485.9754 | 29.28 | 52
2021-01-27 14:50 | 3.4223 | 1.6783 | 0.38609 | 2.9587 | 99.7068 | 77.5384 | 1.2765 | 0.26259 | 485.9997 | 29.28 | 51.88
2021-01-27 14:55 | 3.3308 | 1.7265 | 0.40262 | 3.0469 | 83.2268 | 51.1183 | 1.2684 | 0.22597 | 485.8496 | 29.24 | 50.47
2021-01-27 15:00 | 3.7532 | 2.0473 | 0.45939 | 3.5975 | 116.1288 | 143.6214 | 1.2615 | 0.29897 | 485.1038 | 29.28 | 51.14
2021-01-27 15:05 | 3.8566 | 2.089 | 0.46165 | 3.6617 | 162.8549 | 156.6435 | 1.2546 | 0.31365 | 484.7184 | 29.42 | 51.52
2021-01-27 15:10 | 4.0608 | 2.1903 | 0.46164 | 3.819 | 143.6761 | 93.9248 | 1.2692 | 0.27718 | 483.5726 | 29.49 | 51.26
2021-01-27 15:15 | 3.6656 | 2.062 | 0.39246 | 3.5531 | 111.3226 | 51.845 | 1.2694 | 0.23346 | 485.5715 | 29.49 | 51.7
2021-01-27 15:20 | 3.5384 | 1.6816 | 0.37783 | 2.9555 | 83.7269 | 70.5746 | 1.2696 | 0.28457 | 485.5621 | 29.45 | 52.18
2021-01-27 15:25 | 3.8829 | 1.5075 | 0.37569 | 2.6865 | 91.2391 | 83.4221 | 1.2184 | 0.26265 | 485.1369 | 29.42 | 52.03
2021-01-27 15:30 | 7.7796 | 1.6433 | 0.38833 | 2.9072 | 104.4734 | 75.0618 | 1.2404 | 0.4451 | 484.5759 | 29.41 | 52.33
2021-01-27 15:35 | [9 empty] | 29.41 | 52.92
2021-01-27 15:40 | 4.6381 | 1.7875 | 0.41361 | 3.1556 | 70.3463 | 43.5959 | 1.2845 | 0.36492 | 484.0872 | 29.32 | 53.15
2021-01-27 15:45 | 4.2433 | 1.688 | 0.35703 | 2.9444 | 68.0868 | 52.6269 | 1.2411 | 0.34312 | 484.4516 | 29.33 | 53.82
2021-01-27 15:50 | 3.694 | 1.6196 | 0.31925 | 2.8019 | 59.0635 | 64.3808 | 1.2485 | 0.43077 | 484.4091 | 29.33 | 54.03
2021-01-27 15:55 | 3.6042 | 1.5825 | 0.37173 | 2.7974 | 71.0621 | 43.1587 | 1.3725 | 0.41613 | 482.934 | 29.3 | 53.91
2021-01-27 16:00 | 3.6176 | 1.3978 | 0.36129 | 2.5038 | 80.5435 | 92.4266 | 1.4019 | 0.29207 | 483.8345 | 29.34 | 54.18
2021-01-27 16:05 | 3.795 | 1.3862 | 0.32964 | 2.4545 | 75.6444 | 51.52 | 1.3721 | 0.24815 | 485.585 | 29.35 | 53.16
2021-01-27 16:10 | 4.0363 | 1.4569 | 0.35471 | 2.5879 | 88.3685 | 62.6284 | 1.3279 | 0.33561 | 485.7516 | 29.36 | 52.23
2021-01-27 16:15 | 3.9205 | 1.3704 | 0.34624 | 2.4489 | 76.8469 | 52.195 | 1.2765 | 0.32825 | 484.7902 | 29.37 | 51.71
2021-01-27 16:20 | 4.2122 | 1.2397 | 0.33769 | 2.238 | 78.3529 | 64.9554 | 1.3197 | 0.38642 | 485.5876 | 29.34 | 50.68
2021-01-27 16:25 | 3.7413 | 1.4058 | 0.33152 | 2.4843 | 81.2722 | 63.7736 | 1.3202 | 0.28445 | 486.4083 | 29.37 | 51.46
2021-01-27 16:30 | 4.4946 | 1.7795 | 0.31892 | 3.0465 | 77.9506 | 55.0179 | 1.291 | 0.35009 | 486.3705 | 29.4 | 51.32
2021-01-27 16:35 | 4.6714 | 1.5995 | 0.27894 | 2.7307 | 88.0369 | 83.4829 | 1.2758 | 0.33536 | 486.0992 | 29.37 | 50.41
2021-01-27 16:40 | 4.5181 | 1.4982 | 0.26215 | 2.5586 | 109.2203 | 86.9923 | 1.2685 | 0.33535 | 485.6899 | 29.31 | 50.5
2021-01-27 16:45 | 4.7975 | 1.4758 | 0.31868 | 2.5809 | 102.492 | 80.9137 | 1.2681 | 0.31339 | 485.9781 | 29.22 | 50.05
2021-01-27 16:50 | 4.3518 | 1.4064 | 0.29778 | 2.4536 | 113.5309 | 103.0354 | 1.283 | 0.30617 | 488.0594 | 29.16 | 50.76
2021-01-27 16:55 | 4.2773 | 1.2798 | 0.27065 | 2.2323 | 128.0775 | 94.4009 | 1.2909 | 0.33548 | 485.2675 | 29.13 | 51.97
2021-01-27 17:00 | 4.2258 | 1.2742 | 0.18041 | 2.1335 | 105.2696 | 64.4772 | 1.2835 | 0.34274 | 486.3735 | 29.12 | 51.78
2021-01-27 17:05 | 4.1111 | 1.3043 | 0.23916 | 2.2385 | 85.0819 | 69.618 | 1.2908 | 0.32817 | 486.3977 | 29.09 | 51.99
2021-01-27 17:10 | 3.614 | 1.3498 | 0.22453 | 2.2936 | 74.549 | 45.4834 | 1.3568 | 0.32825 | 487.8807 | 29.07 | 52.64
2021-01-27 17:15 | 3.2436 | 1.2635 | 0.20564 | 2.1424 | 72.585 | 50.7022 | 1.364 | 0.34283 | 487.5036 | 28.99 | 52.8
2021-01-27 17:20 | 3.3839 | 1.2087 | 0.22661 | 2.0794 | 79.9667 | 61.0272 | 1.3275 | 0.32822 | 487.6078 | 28.92 | 52.93
2021-01-27 17:25 | 3.9081 | 1.0433 | 0.21406 | 1.8132 | 66.7796 | 46.2328 | 1.2985 | 0.27721 | 487.5898 | 28.88 | 53.47
2021-01-27 17:30 | 4.0228 | 1.1952 | 0.24762 | 2.0796 | 55.4256 | 36.7086 | 1.3058 | 0.24073 | 488.6773 | 28.87 | 53.38
2021-01-27 17:35 | 4.1379 | 1.1363 | 0.19097 | 1.9307 | 67.4835 | 42.5335 | 1.2766 | 0.2845 | 488.6615 | 28.87 | 53.46
2021-01-27 17:40 | 4.0744 | 0.9735 | 0.18259 | 1.6748 | 50.6094 | 37.5407 | 1.2621 | 0.25535 | 488.78 | 28.77 | 53.99
2021-01-27 17:45 | 4.1893 | 0.95158 | 0.17419 | 1.6349 | 58.0778 | 64.096 | 1.2621 | 0.31371 | 487.3455 | 28.69 | 54.2
2021-01-27 17:50 | 3.5004 | 0.81484 | 0.18473 | 1.4338 | 55.5357 | 28.2891 | 1.2697 | 0.28459 | 487.9065 | 28.6 | 55.04
2021-01-27 17:55 | 3.0921 | 0.89717 | 0.18896 | 1.5642 | 44.8532 | 51.7222 | 1.2699 | 0.24814 | 489.4926 | 28.54 | 55.66
2021-01-27 18:00 | 2.6187 | 1.064 | 0.17842 | 1.8115 | 47.1013 | 30.0042 | 1.2623 | 0.2262 | 488.6549 | 28.48 | 55.27
2021-01-27 18:05 | 3.4227 | 0.94468 | 0.12172 | 1.5698 | 62.1917 | 53.9465 | 1.2693 | 0.19697 | 489.4666 | 28.37 | 55.06
2021-01-27 18:10 | 2.8864 | 0.77082 | 0.12592 | 1.3054 | 69.2536 | 51.271 | 1.2621 | 0.17509 | 489.6806 | 28.23 | 55.58
2021-01-27 18:15 | 2.9114 | 0.60367 | 0.1154 | 1.0428 | 70.006 | 47.7467 | 1.2618 | 0.16046 | 488.9556 | 28.09 | 55.52
2021-01-27 18:20 | 2.273 | 0.64613 | 0.14059 | 1.131 | 53.9905 | 33.4976 | 1.2619 | 0.13129 | 489.6234 | 27.99 | 55.95
2021-01-27 18:25 | 2.2475 | 0.61875 | 0.14059 | 1.089 | 36.8484 | 10.9002 | 1.2619 | 0.25529 | 490.2591 | 27.9 | 56.3
2021-01-27 18:30 | 2.3367 | 0.62282 | 0.13009 | 1.0848 | 40.8912 | 33.7509 | 1.2691 | 0.26986 | 490.8976 | 27.85 | 56.3
2021-01-27 18:35 | 2.3113 | 0.56946 | 0.13849 | 1.0093 | 35.9386 | 21.2587 | 1.2691 | 0.23341 | 491.4987 | 27.79 | 56.62
2021-01-27 18:40 | 2.4264 | 0.56813 | 0.14269 | 1.0135 | 43.1741 | 59.6019 | 1.2692 | 0.21883 | 492.1723 | 27.68 | 57.16
2021-01-27 18:45 | 1.8389 | 0.59551 | 0.15109 | 1.0639 | 63.2388 | 53.799 | 1.2692 | 0.16048 | 493.8672 | 27.61 | 57.39
2021-01-27 18:50 | 1.6731 | 0.56545 | 0.13012 | 0.99686 | 47.6946 | 18.851 | 1.2694 | 0.1459 | 493.437 | 27.52 | 57.97
2021-01-27 18:55 | 1.5706 | 0.42298 | 0.12799 | 0.77635 | 29.0017 | 26.8871 | 1.2618 | 0.124 | 493.7581 | 27.38 | 57.95
2021-01-27 19:00 | 1.7998 | 0.32567 | 0.11326 | 0.61457 | 35.6084 | 10.8449 | 1.2614 | 0.11666 | 492.6182 | 27.22 | 57.51
2021-01-27 19:05 | 1.3143 | 0.3365 | 0.10065 | 0.61436 | 15.7615 | 19.0486 | 1.2609 | 0.094753 | 495.1446 | 27.07 | 57.08
2021-01-27 19:10 | 1.1736 | 0.35145 | 0.096424 | 0.63514 | 9.2052 | 3.9086 | 1.246 | 0.065579 | 493.9003 | 26.95 | 56.69
2021-01-27 19:15 | 1.1225 | 0.49772 | 0.1027 | 0.86562 | 22.3266 | 12.5102 | 1.2386 | 0.12386 | 495.0976 | 26.9 | 56.53
2021-01-27 19:20 | 0.98228 | 0.48548 | 0.10271 | 0.84687 | 33.0352 | 21.7071 | 1.2533 | 0.1093 | 495.0964 | 26.86 | 57.04
2021-01-27 19:25 | 0.95676 | 0.36239 | 0.090136 | 0.64353 | 21.1456 | 0.030616 | 1.2679 | 0.094727 | 496.356 | 26.74 | 57.42
2021-01-27 19:30 | 1.1354 | 0.3665 | 0.07756 | 0.63935 | 23.0748 | 8.9605 | 1.2679 | 0.094728 | 494.4491 | 26.61 | 57.9
2021-01-27 19:35 | 1.1228 | 0.33921 | 0.096442 | 0.61639 | 25.2324 | 25.5896 | 1.2681 | 0.094744 | 494.9281 | 26.59 | 58.44
2021-01-27 19:40 | 1.0335 | 0.31597 | 0.090157 | 0.57449 | 15.72 | 10.0853 | 1.2682 | 0.094749 | 495.8936 | 26.61 | 58.57
2021-01-27 19:45 | 1.8375 | 0.31599 | 0.083871 | 0.56823 | 28.5321 | 31.9723 | 1.2828 | 0.087465 | 496.3981 | 26.61 | 58.71
2021-01-27 19:50 | 1.4802 | 0.37892 | 0.094357 | 0.67518 | 24.8372 | 15.3739 | 1.2755 | 0.10933 | 496.3893 | 26.61 | 58.76
2021-01-27 19:55 | 1.161 | 0.40895 | 0.090149 | 0.717 | 22.996 | 20.3014 | 1.2753 | 0.10932 | 497.1645 | 26.51 | 58.65
2021-01-27 20:00 | 1.1866 | 0.49376 | 0.10063 | 0.8554 | 30.887 | 15.3822 | 1.2754 | 0.10203 | 496.6332 | 26.5 | 58.79
2021-01-27 20:05 | 1.1101 | 0.51707 | 0.069193 | 0.86177 | 20.7738 | 13.4749 | 1.2609 | 0.094753 | 496.6155 | 26.48 | 59.15
2021-01-27 20:10 | 0.85499 | 0.49384 | 0.081778 | 0.83875 | 16.8036 | 6.2682 | 1.2756 | 0.087469 | 496.1593 | 26.42 | 59.51
2021-01-27 20:15 | 1.2634 | 0.45009 | 0.088074 | 0.77589 | 17.019 | 14.5279 | 1.2829 | 0.10934 | 496.1979 | 26.38 | 59.81
2021-01-27 20:20 | 1.3656 | 0.37896 | 0.075495 | 0.65639 | 24.0847 | 4.6454 | 1.2976 | 0.087477 | 495.6003 | 26.41 | 59.81
2021-01-27 20:25 | 1.1996 | 0.32697 | 0.069203 | 0.5704 | 14.6917 | 18.9593 | 1.283 | 0.036448 | 496.0843 | 26.44 | 59.68
2021-01-27 20:30 | 1.4292 | 0.31326 | 0.058712 | 0.5389 | 21.275 | -0.17355 | 1.2756 | 0.07289 | 496.3112 | 26.33 | 59.81
2021-01-27 20:35 | 1.3527 | 0.3639 | 0.054522 | 0.61232 | 16.1613 | 17.2537 | 1.2611 | 0.094762 | 495.2749 | 26.3 | 60.07
2021-01-27 20:40 | 1.2762 | 0.33928 | 0.075493 | 0.59346 | 16.5393 | 4.0736 | 1.2611 | 0.10205 | 495.382 | 26.23 | 60.37
2021-01-27 20:45 | 1.1359 | 0.3051 | 0.071304 | 0.53897 | 22.3399 | 4.615 | 1.2685 | 0.094771 | 496.423 | 26.22 | 60.61
2021-01-27 20:50 | 1.1998 | 0.23807 | 0.081794 | 0.44462 | 21.7998 | 11.7117 | 1.2685 | 0.087485 | 495.9008 | 26.2 | 60.83
2021-01-27 20:55 | 1.2381 | 0.1984 | 0.073408 | 0.37753 | 12.6618 | 17.2364 | 1.2686 | 0.072907 | 495.3839 | 26.18 | 61.02
2021-01-27 21:00 | 0.97007 | 0.14641 | 0.044045 | 0.27056 | 21.5866 | 28.9796 | 1.2394 | 0.029163 | 496.5357 | 26.12 | 61.28
2021-01-27 21:05 | 0.85515 | 0.13135 | 0.029362 | 0.2307 | 39.9851 | 145.2065 | 1.2248 | 0.043743 | 449.0774 | 25.98 | 61.63
2021-01-27 21:10 | 1.0722 | 0.2244 | 0.058727 | 0.4006 | 319.3372 | 343.9055 | 1.2249 | 0.08749 | 327.4509 | 25.97 | 61.89
2021-01-27 21:15 | 1.8509 | 0.32841 | 0.077607 | 0.5831 | 251.2605 | 92.1306 | 1.2322 | 0.10208 | 328.8732 | 26.11 | 61.52
2021-01-27 21:20 | 1.9146 | 0.35165 | 0.071311 | 0.61034 | 140.7404 | 46.0013 | 1.2248 | 0.080198 | 327.6567 | 26.27 | 60.77
2021-01-27 21:25 | 1.4167 | 0.27091 | 0.062917 | 0.48027 | 67.992 | 24.1275 | 1.2175 | 0.080194 | 328.7038 | 26.3 | 60.49
2021-01-27 21:30 | 1.4806 | 0.27639 | 0.05453 | 0.47609 | 38.7603 | 22.229 | 1.2175 | 0.094777 | 327.6344 | 26.3 | 60.57
2021-01-27 21:35 | 1.404 | 0.25997 | 0.073408 | 0.47191 | 33.3801 | 2.0218 | 1.2248 | 0.087489 | 328.6972 | 26.29 | 60.68
2021-01-27 21:40 | 0.94454 | 0.17104 | 0.052435 | 0.31461 | 25.998 | -0.84754 | 1.2249 | 0.072909 | 328.2044 | 26.25 | 60.88
2021-01-27 21:45 | 0.90629 | 0.14778 | 0.046145 | 0.27267 | 9.987 | 3.8396 | 1.2249 | 0.06562 | 328.269 | 26.18 | 61.24
2021-01-27 21:50 | 1.0469 | 0.1916 | 0.058739 | 0.35244 | 1.2869 | -0.18384 | 1.2251 | 0.13855 | 328.17 | 26.22 | 61.58
2021-01-27 21:55 | 0.84271 | 0.17657 | 0.041962 | 0.31262 | 8.0594 | 1.2053 | 1.218 | 0.19692 | 327.7809 | 26.24 | 61.8
2021-01-27 22:00 | 0.65123 | 0.15605 | 0.050358 | 0.28956 | 19.7055 | 13.6682 | 1.2254 | 0.15317 | 327.8122 | 26.19 | 62.19
2021-01-27 22:05 | 0.70235 | 0.17112 | 0.069246 | 0.33364 | 20.1869 | 16.9791 | 1.2327 | 0.19695 | 328.0953 | 26.21 | 62.37
2021-01-27 22:10 | 0.68959 | 0.15332 | 0.056656 | 0.29168 | 11.064 | 8.4283 | 1.2619 | 0.14589 | 328.6678 | 26.17 | 62.53
2021-01-27 22:15 | 0.86857 | 0.21771 | 0.090251 | 0.42397 | 20.212 | 17.2385 | 1.2768 | 0.13133 | 328.0416 | 26.19 | 63.11
2021-01-27 22:20 | 1.022 | 0.21227 | 0.069274 | 0.39465 | 28.4938 | 13.1636 | 1.2697 | 0.10216 | 327.4005 | 26.24 | 63.42
2021-01-27 22:25 | 0.79213 | 0.12463 | 0.056683 | 0.24983 | 19.8696 | 13.3281 | 1.2625 | 0.080275 | 327.9266 | 26.22 | 63.72
2021-01-27 22:30 | 0.7155 | 0.097246 | 0.03989 | 0.18895 | 0.59284 | 1.5741 | 1.2699 | 0.065683 | 326.9518 | 26.13 | 64.18
2021-01-27 22:35 | 0.79231 | 0.18083 | 0.058796 | 0.33808 | 1.1655 | 4.8663 | 1.2701 | 0.080294 | 327.9494 | 26.13 | 64.73
2021-01-27 22:40 | 0.77966 | 0.17538 | 0.048305 | 0.31503 | 12.5053 | 2.3006 | 1.263 | 0.073007 | 327.7947 | 26.22 | 64.88
2021-01-27 22:45 | 0.66464 | 0.13154 | 0.031504 | 0.23313 | 14.5302 | 9.9799 | 1.2704 | 0.051106 | 327.7987 | 26.21 | 64.98
2021-01-27 22:50 | 0.56239 | 0.082211 | 0.035705 | 0.15962 | -0.37834 | -3.0267 | 1.2704 | 0.043805 | 328.4157 | 26.13 | 65.29
2021-01-27 22:55 | 0.58798 | 0.13291 | 0.044108 | 0.24784 | -2.1576 | -13.7843 | 1.2631 | 0.065711 | 328.5008 | 26.04 | 65.76
2021-01-27 23:00 | 0.54964 | 0.082217 | 0.027305 | 0.15333 | 4.6323 | -4.0801 | 1.2558 | 0.051109 | 328.0413 | 25.97 | 66.09
2021-01-27 23:05 | 0.48575 | 0.10551 | 0.025206 | 0.18484 | 10.0627 | 7.6288 | 1.2559 | 0.029206 | 327.5545 | 25.92 | 66.39
2021-01-27 23:10 | 1.0482 | 0.11237 | 0.035709 | 0.20795 | 2.843 | -15.2783 | 1.2486 | 0.073017 | 327.0635 | 25.88 | 66.59
2021-01-27 23:15 | 0.83098 | 0.15623 | 0.02941 | 0.26889 | -2.6387 | -1.1762 | 1.2487 | 0.087629 | 328.0706 | 25.9 | 66.79
2021-01-27 23:20 | 0.81826 | 0.17955 | 0.054623 | 0.32984 | 7.753 | 4.2549 | 1.2561 | 0.073029 | 326.4007 | 25.95 | 66.82
2021-01-27 23:25 | 0.80537 | 0.18638 | 0.050415 | 0.3361 | 13.2848 | -1.7897 | 1.256 | 0.058416 | 327.9979 | 25.98 | 66.34
2021-01-27 23:30 | 0.6774 | 0.16168 | 0.044104 | 0.29193 | 0.87935 | -8.4765 | 1.2557 | 0.043804 | 329.1872 | 25.92 | 66.01
2021-01-27 23:35 | 0.62623 | 0.15481 | 0.048301 | 0.28351 | -3.7114 | 0.98152 | 1.2556 | 0.0365 | 328.2191 | 25.86 | 66.01
2021-01-27 23:40 | 0.47285 | 0.11508 | 0.054599 | 0.2289 | 6.1343 | 8.3733 | 1.2629 | 0.043799 | 329.3333 | 25.82 | 66.08
2021-01-27 23:45 | 0.47283 | 0.1548 | 0.052497 | 0.28978 | 14.2208 | -2.106 | 1.2628 | 0.051097 | 328.3197 | 25.79 | 66.07
2021-01-27 23:50 |  | 0.12874 | 0.048284 | 0.24562 | 7.1543 | -1.8499 | 1.2625 | 0.036487 | 327.3973 | 25.75 | 65.37
2021-01-27 23:55 | 0.43415 | 0.10266 | 0.050357 | 0.20772 | -3.0441 | -10.2765 | 1.2545 | 0.47409 | 328.6926 | 25.69 | 64.08
2021-01-28 | 0.39573 | 0.075266 | 0.056636 | 0.17201 | -4.1156 | 10.5086 |  |  | 328.2949 | 25.65 | 63.42
2021-01-28 00:05
2021-01-28 00:10
2021-01-28 00:15 | 0.81694 | 0.038314 | 0.065022 | 0.12585 | -12.2132 | -12.2439 | 1.2687 | 0.53226 | 328.4393 | 25.54 | 63.62
2021-01-28 00:20 | 0.59993 | 0.039682 | 0.069216 | 0.13214 | -8.6594 | -5.5347 | 1.2614 | 0.42288 | 328.4889 | 25.5 | 63.72
2021-01-28 00:25 | 0.5232 | 0.060191 | 0.083876 | 0.17404 | 2.4297 | 0.12251 | 1.261 | 0.40819 | 329.1078 | 25.5 | 62.92
2021-01-28 00:30 | 0.36993 | 0.062904 | 0.090132 | 0.18655 | 7.7558 | -4.8984 | 1.2533 | 0.27688 | 327.6473 | 25.49 | 61.82
2021-01-28 00:35 | 0.35715 | 0.086144 | 0.08803 | 0.22007 | -0.040817 | 0.70409 | 1.2313 | 0.255 | 328.9283 | 25.5 | 61.5
2021-01-28 00:40 | 0.39546 | 0.097095 | 0.1111 | 0.25783 | -5.2252 | -5.4701 | 1.2242 | 0.22589 | 328.314 | 25.54 | 61.71
2021-01-28 00:45 | 0.40827 | 0.11762 | 0.12579 | 0.30608 | 3.5519 | -6.5629 | 1.2316 | 0.16033 | 329.3028 | 25.57 | 61.97
2021-01-28 00:50 | 0.34448 | 0.050605 | 0.12579 | 0.20336 | 11.5031 | 2.1843 | 1.2462 | 0.10203 | 328.2703 | 25.54 | 62.11
2021-01-28 00:55 | 0.14035 | 0.050607 | 0.13628 | 0.21594 | 13.7796 | 6.9204 | 1.2462 | 0.080167 | 328.8355 | 25.5 | 62.35
2021-01-28 01:00 | 0.20417 | 0.090285 | 0.1321 | 0.27049 | -5.7372 | -11.4438 | 1.261 | 0.058311 | 328.8099 | 25.48 | 62.86
2021-01-28 01:05 |  |  |  |  | -3.2673 | 1.4907 |  |  | 328.6973 | 25.53 | 63.2
2021-01-28 01:10 |  |  |  |  | 10.1294 | -0.20422 |  |  | 329.1622 | 25.57 | 63.25
2021-01-28 01:15 |  |  |  |  | 14.1011 | -5.0645 |  |  | 328.0878 | 25.59 | 63.09
2021-01-28 01:20 |  |  |  |  | 6.0654 | 11.028 |  |  | 328.0661 | 25.6 | 63.15
2021-01-28 01:25 |  |  |  |  | 2.6549 | 3.676 |  |  | 328.9205 | 25.6 | 63.25
2021-01-28 01:30 |  |  |  |  | 6.4331 | -0.39824 |  |  | 328.4428 | 25.55 | 63.45
2021-01-28 01:35 |  |  |  |  | 10.5173 | -3.7372 |  |  | 329.6029 | 25.47 | 63.67
2021-01-28 01:40 |  |  |  |  | -1.981 | -6.3004 |  |  | 329.8518 | 25.42 | 63.88
2021-01-28 01:45 |  |  |  |  | -6.454 | 7.6794 |  |  | 329.0289 | 25.48 | 63.92
2021-01-28 01:50 |  |  |  |  | 6.9751 | 2.6552 |  |  | 329.1528 | 25.54 | 63.75
2021-01-28 01:55 |  |  |  |  | 21.2926 | 13.5619 |  |  | 327.8238 | 25.6 | 63.56
2021-01-28 02:00 |  |  |  |  | 13.3265 | -0.88844 |  |  | 330.039 | 25.53 | 63.71
2021-01-28 02:05 |  |  |  |  | 0.29616 | 2.8595 |  |  | 329.5928 | 25.44 | 64.18
2021-01-28 02:10 | 0.67663 | 0.12591 | 0.041956 | 0.23495 | 2.0733 | 8.8141 | 1.298 | -0.021877 | 328.1608 | 25.45 | 64.36
2021-01-28 02:15 | 0.14042 | 0.076634 | 0.03566 | 0.15313 | 9.5895 | 2.3284 | 1.276 | -0.0072917 | 328.188 | 25.45 | 64.11
2021-01-28 02:20 | 0.15317 | 0.064313 | 0.035657 | 0.13424 | 12.9075 | 4.6565 | 1.2686 | 0.014582 | 328.8229 | 25.38 | 64.13
2021-01-28 02:25 | 0.16594 | 0.060209 | 0.035658 | 0.12795 | -0.51059 | -8.292 | 1.2687 | 0.021874 | 328.3273 | 25.34 | 64.36
2021-01-28 02:30 | 0.17872 | 0.056109 | 0.039856 | 0.12376 | -4.8613 | -5.4332 | 1.2615 | 0.029168 | 328.8424 | 25.33 | 64.65
2021-01-28 02:35 | 0.20427 | 0.047901 | 0.046153 | 0.11958 | 3.5849 | -1.7567 | 1.2616 | 0.014585 | 329.327 | 25.35 | 64.8
2021-01-28 02:40 | 0.24258 | 0.039691 | 0.048252 | 0.10909 | 12.0728 | 1.7874 | 1.2616 | 0.021878 | 329.8451 | 25.35 | 64.92
2021-01-28 02:45 | 0.22983 | 0.043801 | 0.041962 | 0.1091 | 3.4321 | -0.6946 | 1.2544 | 0.029173 | 328.735 | 25.37 | 65.08
2021-01-28 02:50 | 0.21709 | 0.068446 | 0.052458 | 0.15737 | -8.8265 | -16.2738 | 1.2546 | 0.014588 | 329.1192 | 25.47 | 65.03
2021-01-28 02:55 | 0.19155 | 0.047913 | 0.041967 | 0.11541 | -3.1874 | 1.4405 | 1.2546 | 0.043765 | 329.1029 | 25.48 | 65.04
2021-01-28 03:00 | [9 empty] | 25.5 | 65.23
2021-01-28 03:05 | 0.16605 | 0.18348 | 0.046175 | 0.32742 | 11.4037 | 0.70507 | 1.2622 | 0.03648 | 328.3749 | 25.59 | 65.31
2021-01-28 03:10 | 0.21712 | 0.12733 | 0.035676 | 0.23085 | -0.07152 | 14.0691 | 1.2621 | 0.01459 | 327.8482 | 25.62 | 64.86
2021-01-28 03:15 | 0.19157 | 0.14239 | 0.058761 | 0.27911 | 1.6858 | 6.0281 | 1.2547 | 0.021885 | 327.885 | 25.59 | 64.94
2021-01-28 03:20 | 0.17881 | 0.13965 | 0.071355 | 0.28542 | 4.1892 | 3.0653 | 1.2621 | 0.036477 | 328.9546 | 25.57 | 65.14
2021-01-28 03:25 | 0.16605 | 0.13967 | 0.067165 | 0.28335 | 9.5544 | 0.95033 | 1.2622 | 0.029184 | 328.4096 | 25.55 | 65.55
2021-01-28 03:30 | 0.1533 | 0.13694 | 0.069271 | 0.27918 | 0.33725 | 10.0766 | 1.2624 | 0.029187 | 327.856 | 25.54 | 65.9
2021-01-28 03:35 | 0.16609 | 0.13285 | 0.083975 | 0.28762 | -1.5331 | 8.003 | 1.2552 | 0.036489 | 327.2852 | 25.54 | 66.27
2021-01-28 03:40 | 0.34504 | 0.1685 | 0.073496 | 0.33178 | 11.8796 | 5.8682 | 1.2628 | 0.051096 | 327.0768 | 25.66 | 66.5
2021-01-28 03:45 | 0.38343 | 0.18634 | 0.067206 | 0.35283 | 19.8362 | 8.1083 | 1.2557 | 0.051104 | 328.5309 | 25.74 | 66.62
2021-01-28 03:50 | 0.43459 | 0.53988 | 0.11342 | 0.94097 | 11.4426 | 23.3045 | 1.2631 | 0.051108 | 326.3284 | 25.79 | 66.68
2021-01-28 03:55 | 0.58803 | 0.66189 | 0.13234 | 1.1448 | 9.5108 | 17.1399 | 1.2632 | 0.073019 | 327.2926 | 25.85 | 66.71
2021-01-28 04:00 | 0.6776 | 0.50847 | 0.13445 | 0.91385 | 17.8578 | 6.1572 | 1.2561 | 0.08033 | 327.1567 | 25.94 | 66.69
2021-01-28 04:05 | 0.48587 | 0.47699 | 0.13026 | 0.86351 | 19.8847 | 6.1373 | 1.2635 | 0.073033 | 327.0623 | 26 | 66.71
2021-01-28 04:10 | 0.3836 | 0.46056 | 0.14498 | 0.84884 | 12.9093 | 12.7047 | 1.2489 | 0.080341 | 327.3396 | 26.03 | 66.8
2021-01-28 04:15 | 0.43476 | 0.56613 | 0.1807 | 1.0485 | 7.2937 | 17.7893 | 1.2636 | 0.087647 | 327.8471 | 26.04 | 66.86
2021-01-28 04:20 | 0.5753 | 0.57424 | 0.19117 | 1.0735 | 16.8755 | 17.6017 | 1.2706 | 0.05842 | 326.841 | 26.05 | 66.25
2021-01-28 04:25 | 0.80474 | 0.66823 | 0.22459 | 1.2489 |  |  | 1.2623 | 0.094852 | 430.0327 | 26.08 | 63.59
2021-01-28 04:30 | 1.2762 | 0.56776 | 0.18454 | 1.0569 |  |  | 1.2684 | 0.12393 | 447.7031 | 26.22 | 60.47
2021-01-28 04:35 | 1.2631 | 0.62642 | 0.17611 | 1.1363 |  | 16.2494 | 1.2608 | 0.12389 | 447.2202 | 26.27 | 59.51
2021-01-28 04:40 | 1.684 | 0.73304 | 0.17819 | 1.3018 | 8.3791 | 39.0481 | 1.268 | 0.13845 | 448.6617 | 26.34 | 59.07
2021-01-28 04:45 | 2.2324 | 0.90527 | 0.20752 | 1.5951 | 47.1881 | 65.1082 | 1.2824 | 0.18216 | 447.5382 | 26.41 | 58.56
2021-01-28 04:50 | 2.6772 | 1.3052 | 0.25557 | 2.2562 | 67.8636 | 57.1751 | 1.2816 | 0.2039 | 448.7633 | 26.48 | 56.61
2021-01-28 04:55 | 3.3009 | 1.4468 | 0.34973 | 2.5696 | 95.779 | 79.527 | 1.2812 | 0.22567 | 449.3279 | 26.55 | 55.5
2021-01-28 05:00 | 2.2301 | 1.515 | 0.37483 | 2.6971 | 95.5981 | 78.4604 | 1.2884 | 0.23293 | 446.5466 | 26.66 | 54.92
2021-01-28 05:05 | 2.8671 | 1.8209 | 0.41249 | 3.2036 | 88.8 | 71.7352 | 1.2956 | 0.26203 | 446.925 | 26.79 | 54.24
2021-01-28 05:10 | 3.0838 | 2.1324 | 0.56955 | 3.8381 | 103.4725 | 75.0303 | 1.2883 | 0.30571 | 447.2767 | 26.9 | 53.98
2021-01-28 05:15 | 3.2745 | 2.1936 | 0.53179 | 3.8942 | 103.3774 | 88.0267 | 1.2954 | 0.33478 | 447.1714 | 27.01 | 53.27
2021-01-28 05:20 | 3.185 | 2.2917 | 0.49615 | 4.009 | 115.2825 | 100.6365 | 1.2953 | 0.3493 | 448.1526 | 27.09 | 52.77
2021-01-28 05:25 | 2.9306 | 2.0093 | 0.52762 | 3.6075 | 112.8209 | 83.7696 | 1.3028 | 0.27657 | 444.8109 | 27.16 | 52.92
2021-01-28 05:30 | 4.2425 | 2.7233 | 0.6406 | 4.8192 | 122.8668 | 126.4443 | 1.2953 | 0.34931 | 444.7616 | 27.23 | 52.37
2021-01-28 05:35 | 4.6249 | 3.2356 | 0.78299 | 5.7426 | 158.3415 | 141.3913 | 1.2881 | 0.36387 | 443.3614 | 27.45 | 51.8
2021-01-28 05:40 | 3.4786 | 3.001 | 0.76424 | 5.3643 | 158.9519 | 119.8485 | 1.2883 | 0.33481 | 443.645 | 27.58 | 51.73
2021-01-28 05:45 | 4.0526 | 3.246 | 0.87532 | 5.8508 | 146.259 | 114.9397 | 1.3103 | 0.34941 | 442.9119 | 27.68 | 51.77
2021-01-28 05:50 | 6.1945 | 3.8654 | 0.9718 | 6.8948 | 154.6738 | 129.4472 | 1.325 | 0.56059 | 442.622 | 27.83 | 51.73
2021-01-28 05:55 | 6.3254 | 4.1341 | 0.96814 | 7.3072 | 166.8682 | 157.5025 | 1.3185 | 0.70659 | 442.0287 | 28.01 | 52.66
2021-01-28 06:00 | 4.8938 | 3.6573 | 0.9277 | 6.5316 | 169.6615 | 123.0379 | 1.3103 | 0.65516 | 443.207 | 28.13 | 50.55
2021-01-28 06:05 | 5.4185 | 3.8993 | 0.78562 | 6.7627 | 175.525 | 144.5896 | 1.3473 | 0.54619 | 442.349 | 28.23 | 51.32
2021-01-28 06:10 | 6.6946 | 3.8426 | 0.8088 | 6.6988 | 175.6251 | 149.8159 | 1.3693 | 0.53899 | 442.7016 | 28.3 | 51.53
2021-01-28 06:15 | 5.7135 | 3.4425 | 0.767 | 6.0438 | 173.7004 | 128.1353 | 1.2748 | 0.48079 | 442.5822 | 28.34 | 51.76
2021-01-28 06:20 | 4.9364 | 3.4007 | 0.81325 | 6.026 | 186.6398 | 152.6895 | 1.2605 | 0.51002 | 442.4601 | 28.37 | 52.12
2021-01-28 06:25 | 5.9553 | 3.0403 | 0.79837 | 5.4587 | 196.477 | 180.399 | 1.282 | 0.44433 | 442.5747 | 28.37 | 51.46
2021-01-28 06:30 | 6.3376 | 2.8501 | 0.69146 | 5.0582 | 210.1571 | 164.6287 | 1.2965 | 0.48801 | 443.6082 | 28.4 | 51.24
2021-01-28 06:35 | 6.0089 | 2.9089 | 0.63939 | 5.0983 | 190.4782 | 118.6776 | 1.3336 | 0.50282 | 442.9127 | 28.37 | 52.55
2021-01-28 06:40 | 6.1131 | 2.8607 | 0.64799 | 5.033 | 160.4147 | 141.7514 | 1.3778 | 0.51028 | 443.2291 | 28.41 | 53.3
2021-01-28 06:45 | 6.2397 | 2.8999 | 0.60596 | 5.0511 | 162.309 | 119.9045 | 1.4213 | 0.49562 | 443.1656 | 28.5 | 52.63
2021-01-28 06:50 | 5.778 | 2.7935 | 0.58895 | 4.8709 | 148.6614 | 112.4476 | 1.3406 | 0.43714 | 442.8042 | 28.51 | 51.57
2021-01-28 06:55 | 5.4075 | 2.7262 | 0.53859 | 4.7174 | 138.2698 | 117.0987 | 1.304 | 0.50266 | 443.9189 | 28.5 | 51.34
2021-01-28 07:00 | 5.522 | 2.8572 | 0.54694 | 4.9266 | 150.8301 | 146.484 | 1.2966 | 0.48806 | 441.7504 | 28.56 | 51
2021-01-28 07:05 | 6.4403 | 2.8053 | 0.57838 | 4.8785 | 168.7585 | 145.3541 | 1.3039 | 0.69932 | 442.6646 | 28.65 | 50.78
2021-01-28 07:10 | 6.8465 | 2.892 | 0.6285 | 5.0615 | 172.6801 | 142.9991 | 1.3181 | 0.72097 | 443.2247 | 28.71 | 49.92
2021-01-28 07:15 | 7.6366 | 2.963 | 0.66199 | 5.2037 | 171.6304 | 155.6892 | 1.3108 | 0.64083 | 443.1754 | 28.76 | 49.64
2021-01-28 07:20 | 7.726 | 2.9658 | 0.65362 | 5.1996 | 190.1457 | 161.3836 | 1.3545 | 0.55346 | 442.0244 | 28.82 | 49.52
2021-01-28 07:25 | 7.4702 | 3.0092 | 0.57395 | 5.1865 | 185.0571 | 158.1847 | 1.3544 | 0.45874 | 442.0419 | 28.84 | 49.2
2021-01-28 07:30 | 6.7821 | 2.9 | 0.51113 | 4.9563 | 175.0394 | 133.694 | 1.3107 | 0.42963 | 442.4628 | 28.9 | 49.13
2021-01-28 07:35 | 7.4444 | 3.6622 | 0.60954 | 6.2252 | 174.7185 | 147.3375 | 1.3033 | 0.5024 | 442.9261 | 28.91 | 48.94
2021-01-28 07:40 | 6.7549 | 2.932 | 0.52148 | 5.0158 | 175.8011 | 151.7689 | 1.2886 | 0.44408 | 442.9404 | 28.95 | 48.42
2021-01-28 07:45 | 6.1446 | 2.2808 | 0.52998 | 4.0261 | 166.4185 | 105.1666 | 1.2889 | 0.38593 | 442.3397 | 28.93 | 49.05
2021-01-28 07:50 | 5.6609 | 1.9422 | 0.45882 | 3.4359 | 143.8993 | 102.4064 | 1.2963 | 0.34957 | 443.3637 | 28.91 | 49.44
2021-01-28 07:55 | 6.3623 | 2.3755 | 0.52168 | 4.1651 | 129.3681 | 102.0318 | 1.3182 | 0.43697 | 442.2681 | 28.93 | 49.45
2021-01-28 08:00 | 9.8955 | 3.2726 | 0.62024 | 5.6366 | 159.1133 | 144.3925 | 1.3402 | 0.53901 | 442.6602 | 28.98 | 49.65
2021-01-28 08:05 | 8.8875 | 3.1548 | 0.59715 | 5.4309 | 168.1306 | 120.0845 | 1.3037 | 0.50256 | 443.6115 | 29.07 | 49.23
2021-01-28 08:10 | 6.4401 | 2.7752 | 0.49035 | 4.7443 | 150.5022 | 124.1908 | 1.2893 | 0.45163 | 443.9938 | 29.13 | 49.37
2021-01-28 08:15 | 6.3003 | 2.6578 | 0.52392 | 4.5958 | 148.7982 | 84.102 | 1.2967 | 0.50994 | 441.7989 | 29.17 | 49.42
2021-01-28 08:20 | 7.2716 | 2.6736 | 0.55971 | 4.6579 | 126.3888 | 89.9337 | 1.3044 | 0.64125 | 444.8286 | 29.17 | 50.13
2021-01-28 08:25 | 6.1994 | 2.899 | 0.51144 | 4.9551 | 127.8054 | 101.783 | 1.3188 | 0.60476 | 444.3007 | 29.2 | 49.81
2021-01-28 08:30 | 4.4895 | 2.8754 | 0.49251 | 4.9 | 129.8699 | 85.1583 | 1.3259 | 0.37883 | 445.9097 | 29.22 | 49.43
2021-01-28 08:35 | 4.8859 | 2.5272 | 0.51148 | 4.3853 | 124.1805 | 85.665 | 1.3116 | 0.31333 | 444.2425 | 29.22 | 49.91
2021-01-28 08:40 | 5.1657 | 2.9096 | 0.56169 | 5.0217 | 129.5575 | 104.8541 | 1.2677 | 0.39342 | 444.3464 | 29.2 | 49.56
2021-01-28 08:45 | 3.992 | 1.9975 | 0.3919 | 3.4537 | 118.6011 | 102.3373 | 1.2676 | 0.33511 | 443.4397 | 29.12 | 49.63
2021-01-28 08:50 | 5.2036 | 2.1192 | 0.38771 | 3.6361 | 96.93 | 83.0333 | 1.2895 | 0.47353 | 442.9997 | 29.06 | 49.81
2021-01-28 08:55 | 5.4217 | 2.0171 | 0.47165 | 3.5615 | 91.6152 | 72.3267 | 1.297 | 0.52465 | 442.9838 | 29 | 50.56
2021-01-28 09:00 | 4.2353 | 1.5959 | 0.46117 | 2.9074 | 75.9391 | 50.5274 | 1.3043 | 0.47364 | 444.1866 | 28.9 | 50.84
2021-01-28 09:05 | 4.3624 | 1.5288 | 0.40243 | 2.7458 | 65.8904 | 55.6144 | 1.2969 | 0.38616 | 444.89 | 28.81 | 50.86
2021-01-28 09:10 | 4.1195 | 1.6092 | 0.39818 | 2.8648 | 87.3791 | 96.7659 | 1.2894 | 0.35696 | 444.5423 | 28.73 | 50.75
2021-01-28 09:15 | 3.367 | 1.6816 | 0.39818 | 2.9759 | 111.2118 | 87.2452 | 1.2894 | 0.27683 | 444.6518 | 28.66 | 50.92
2021-01-28 09:20 | 3.1761 | 1.7844 | 0.40243 | 3.1377 | 96.0021 | 72.2261 | 1.2896 | 0.29872 | 443.566 | 28.64 | 51.32
2021-01-28 09:25 | 2.6282 | 1.8615 | 0.47171 | 3.325 | 94.9231 | 63.0677 | 1.2899 | 0.24778 | 442.9164 | 28.65 | 51.9
2021-01-28 09:30 | 2.7695 | 1.6268 | 0.46767 | 2.9612 | 75.4024 | 37.4919 | 1.2831 | 0.22599 | 444.8766 | 28.65 | 52.74
2021-01-28 09:35 | 2.9232 | 1.701 | 0.44259 | 3.0499 | 57.4433 | 36.3961 | 1.276 | 0.22604 | 444.851 | 28.61 | 53.34
2021-01-28 09:40 | 3.5364 | 2.0104 | 0.46152 | 3.5432 | 66.5091 | 66.9176 | 1.298 | 0.30628 | 443.7755 | 28.59 | 53.69
2021-01-28 09:45 | 4.3389 | 2.1464 | 0.38793 | 3.6801 | 68.6867 | 53.9856 | 1.3121 | 0.37175 | 445.6299 | 28.53 | 52.83
2021-01-28 09:50 | 4.2344 | 2.4146 | 0.38982 | 4.091 | 82.6171 | 66.8631 | 1.3113 | 0.3934 | 445.4081 | 28.49 | 51.55
2021-01-28 09:55 | 3.4062 | 1.9297 | 0.42555 | 3.3813 | 71.9619 | 69.9718 | 1.2971 | 0.34978 | 444.816 | 28.46 | 52.26
2021-01-28 10:00 | 2.8971 | 1.8032 | 0.42782 | 3.1919 | 68.1834 | 68.408 | 1.2758 | 0.26973 | 444.7496 | 28.38 | 53.56
2021-01-28 10:05 | 2.6537 | 1.4702 | 0.32704 | 2.5807 | 69.4442 | 63.3612 | 1.2607 | 0.24777 | 445.5009 | 28.34 | 52.74
2021-01-28 10:10 | 2.2326 | 1.8367 | 0.30397 | 3.1194 | 81.2411 | 70.0756 | 1.2534 | 0.24777 | 445.5394 | 28.32 | 52.75
2021-01-28 10:15 | 2.7431 | 2.0557 | 0.37317 | 3.5242 | 71.8046 | 51.3706 | 1.2535 | 0.26964 | 445.5431 | 28.3 | 52.96
2021-01-28 10:20 | 4.2095 | 2.002 | 0.45695 | 3.5256 | 66.3318 | 45.5954 | 1.2532 | 0.32788 | 445.1266 | 28.28 | 52.55
2021-01-28 10:25 | 4.3763 | 1.7562 | 0.4843 | 3.1762 | 79.7989 | 81.4729 | 1.2608 | 0.38626 | 444.4883 | 28.29 | 53.07
2021-01-28 10:30 | 4.0191 | 1.3678 | 0.3669 | 2.4614 | 102.5107 |  | 1.2754 | 0.34982 | 445.0708 | 28.25 | 53.22
2021-01-28 10:35 | 3.3941 | 1.1271 | 0.25999 | 1.9877 | 102.5492 |  | 1.2901 | 0.31341 | 446.1258 | 28.17 | 53.72
2021-01-28 10:40 | 3.7382 | 1.1037 | 0.27673 | 1.9665 | 79.9176 | 29.5073 | 1.3045 | 0.31336 | 448.4046 | 28.1 | 53.59
2021-01-28 10:45 | 3.3927 | 1.2087 | 0.2976 | 2.1482 | 64.2719 | 60.6803 | 1.3041 | 0.30598 | 445.4405 | 28.05 | 52.96
2021-01-28 10:50 | 3.0858 | 1.8057 | 0.32267 | 3.0905 | 79.6488 | 64.9187 | 1.3037 | 0.28406 | 446.5671 | 28.08 | 52.21
2021-01-28 10:55 | 3.4423 | 2.0405 | 0.35195 | 3.4818 | 89.3154 | 77.5964 | 1.3035 | 0.29857 | 445.5792 | 28.08 | 51.8
2021-01-28 11:00 | 3.8494 | 1.8556 | 0.33931 | 3.1836 | 81.9753 | 57.7671 | 1.3033 | 0.28395 | 446.1715 | 28.1 | 51.2
2021-01-28 11:05 | 2.9571 | 1.9813 | 0.40423 | 3.4412 | 81.0559 | 70.6652 | 1.296 | 0.29123 | 446.6206 | 28.16 | 50.97
2021-01-28 11:10 | 2.2951 | 2.0147 | 0.33732 | 3.4256 | 77.88 | 68.8424 | 1.2891 | 0.25491 | 444.8408 | 28.19 | 51.74
2021-01-28 11:15 | 2.5366 | 1.7887 | 0.3812 | 3.1229 | 72.6964 | 61.255 | 1.2887 | 0.25483 | 446.1649 | 28.16 | 50.99
2021-01-28 11:20 | 2.7284 | 1.5594 | 0.38548 | 2.7779 | 79.0259 | 63.6654 | 1.289 | 0.22576 | 446.0814 | 28.15 | 51.59
2021-01-28 11:25 | 2.4855 | 1.4798 | 0.42308 | 2.6914 | 67.963 | 60.0807 | 1.2814 | 0.18202 | 445.1492 | 28.14 | 50.98
2021-01-28 11:30 | 2.3826 | 1.538 | 0.39989 | 2.7574 | 63.8089 | 82.1565 | 1.2591 | 0.21834 | 444.8491 | 28.1 | 50.11
2021-01-28 11:35 | 2.9423 | 1.5593 | 0.38511 | 2.7774 | 73.7744 | 92.167 | 1.2587 | 0.25464 | 444.9186 | 28.15 | 49.13
2021-01-28 11:40 | 3.1714 | 2.0631 | 0.40602 | 3.5684 | 68.2278 | 80.292 | 1.2659 | 0.24736 | 445.4248 | 28.18 | 48.92
2021-01-28 11:45 | 3.4624 | 2.1069 | 0.48946 | 3.7191 | 71.4174 | 81.8556 | 1.2724 | 0.29084 | 445.603 | 28.23 | 47.32
2021-01-28 11:50 | 3.4494 | 2.1818 | 0.49988 | 3.8464 | 79.5788 | 94.517 | 1.2796 | 0.3199 | 445.5767 | 28.27 | 47.02
2021-01-28 11:55 | 3.6782 | 1.8719 | 0.46219 | 3.3315 | 78.125 | 80.0392 | 1.2722 | 0.34168 | 447.12 | 28.33 | 46.6
2021-01-28 12:00 | 3.9327 | 1.5936 | 0.51865 | 2.9613 | 70.3766 | 49.0865 | 1.2722 | 0.32714 | 443.9452 | 28.33 | 46.6
2021-01-28 12:05 | 4.0856 | 1.3016 | 0.39528 | 2.3884 | 68.6175 | 28.3267 | 1.2723 | 0.34896 | 446.0318 | 28.34 | 46.66
2021-01-28 12:10 | 3.08 | 1.3002 | 0.37435 | 2.3674 | 46.2258 | 23.0314 | 1.2795 | 0.27626 | 446.0725 | 28.32 | 46.65
2021-01-28 12:15 | 2.5454 | 1.1761 | 0.33879 | 2.1436 | 42.59 | 11.3017 | 1.2722 | 0.25444 | 446.1116 | 28.3 | 46.65
2021-01-28 12:20 | 2.3033 | 1.4256 | 0.33875 | 2.5239 | 47.553 | 34.0639 | 1.2721 | 0.24714 | 445.1354 | 28.28 | 46.4
2021-01-28 12:25 | 2.3418 | 1.4339 | 0.34088 | 2.5389 | 64.0428 | 43.8423 | 1.2722 | 0.23263 | 445.0532 | 28.3 | 46.65
2021-01-28 12:30 | 2.4311 | 1.3044 | 0.37019 | 2.3717 | 67.7132 | 38.3878 | 1.2796 | 0.23265 | 446.0339 | 28.33 | 46.76
2021-01-28 12:35 | 2.6344 | 1.6576 | 0.39525 | 2.9382 | 73.4891 | 57.372 | 1.2867 | 0.23262 | 446.022 | 28.37 | 46.38
2021-01-28 12:40 | 2.9908 | 1.9878 | 0.44754 | 3.4946 | 74.5904 | 75.2013 | 1.3013 | 0.26898 | 446.0116 | 28.37 | 46.44
2021-01-28 12:45 | 4.6442 | 1.6109 | 0.3178 | 2.7891 | 75.4877 | 48.9408 | 1.2864 | 0.26164 | 445.5798 | 28.38 | 45.77
2021-01-28 12:50 | 2.6083 | 1.4158 | 0.35543 | 2.5256 | 71.0687 | 61.9078 | 1.2791 | 0.23983 | 446.6611 | 28.37 | 45.75
2021-01-28 12:55 | 2.5956 | 1.4172 | 0.34079 | 2.5131 | 58.8139 | 51.709 | 1.2791 | 0.23984 | 445.1143 | 28.34 | 45.85
2021-01-28 13:00 | 2.4939 | 1.7296 | 0.34498 | 2.9961 | 41.8058 | 53.2675 | 1.2864 | 0.26165 | 445.0896 | 28.35 | 45.88
2021-01-28 13:05 | 3.0032 | 1.7147 | 0.29274 | 2.9211 | 67.5761 | 50.341 | 1.2866 | 0.23987 | 445.5292 | 28.38 | 46.06
2021-01-28 13:10 | 3.411 | 1.6345 | 0.30953 | 2.815 | 72.3636 | 59.1474 | 1.2941 | 0.28353 | 446.0228 | 28.35 | 46.6
2021-01-28 13:15 | 2.9909 | 1.6277 | 0.32207 | 2.8171 | 59.391 | 43.66 | 1.2868 | 0.2908 | 444.9697 | 28.35 | 46.57
2021-01-28 13:20 | 3.3733 | 1.6075 | 0.38696 | 2.8509 | 65.3265 | 42.6684 | 1.2797 | 0.31265 | 444.3604 | 28.36 | 46.92
2021-01-28 13:25 | 3.3875 | 1.7037 | 0.40596 | 3.0175 | 74.3305 | 67.9529 | 1.2875 | 0.32734 | 444.1371 | 28.38 | 47.98
2021-01-28 13:30 | 3.6922 | 1.7565 | 0.39958 | 3.0921 | 83.5701 | 60.256 | 1.2799 | 0.29089 | 444.2644 | 28.37 | 47.36
2021-01-28 13:35 | 3.1958 | 1.5355 | 0.36404 | 2.7177 | 81.4454 | 56.2968 | 1.2654 | 0.26182 | 446.2837 | 28.42 | 47.35
2021-01-28 13:40 | 3.2589 | 1.5366 | 0.433 | 2.7883 | 78.8237 | 77.7646 | 1.2652 | 0.3054 | 446.3195 | 28.45 | 46.81
2021-01-28 13:45 | 4.4055 | 1.6065 | 0.39962 | 2.8622 | 102.7578 | 82.6911 | 1.2728 | 0.5091 | 445.1657 | 28.45 | 47.36
2021-01-28 13:50 | 4.5729 | 1.6509 | 0.38513 | 2.9136 | 93.405 | 49.5864 | 1.2733 | 0.61845 | 444.5239 | 28.46 | 48.34
2021-01-28 13:55 | 2.5604 | 1.6496 | 0.40397 | 2.9325 | 77.0098 | 60.389 | 1.2806 | 0.53843 | 444.5024 | 28.47 | 48.35
2021-01-28 14:00 | 2.2674 | 1.868 | 0.41443 | 3.2799 | 81.4515 | 52.2663 | 1.2806 | 0.31286 | 444.4807 | 28.49 | 48.25
2021-01-28 14:05 | 2.4331 | 1.7179 | 0.3705 | 3.0017 | 72.6011 | 55.9999 | 1.2734 | 0.28378 | 443.8925 | 28.51 | 48.37
2021-01-28 14:10 | 4.0539 | 1.5661 | 0.34564 | 2.7462 | 68.3504 | 55.9184 | 1.2743 | 0.3568 | 443.5535 | 28.52 | 50.19
2021-01-28 14:15 | 4.0662 | 1.4471 | 0.34979 | 2.5679 | 75.1857 | 63.836 | 1.2742 | 0.37133 | 443.6736 | 28.47 | 50.07
2021-01-28 14:20 | 3.0193 | 1.3794 | 0.33285 | 2.4472 | 73.8707 | 47.5655 | 1.2735 | 0.29108 | 445.5437 | 28.44 | 48.77
2021-01-28 14:25 | 2.83 | 1.3925 | 0.35401 | 2.4907 | 70.226 | 57.5698 | 1.2743 | 0.24758 | 444.2046 | 28.44 | 50.39
2021-01-28 14:30 | 2.8044 | 1.5305 | 0.37494 | 2.721 | 61.3102 | 68.7446 | 1.267 | 0.29854 | 444.7936 | 28.41 | 50.38
2021-01-28 14:35 | 3.7601 | 1.734 | 0.40004 | 3.0558 | 71.0833 | 61.6613 | 1.2814 | 0.32035 | 443.1943 | 28.45 | 50.02
2021-01-28 14:40 | 4.7304 | 1.6348 | 0.32056 | 2.8243 | 81.0932 | 66.731 | 1.2818 | 0.34231 | 443.4857 | 28.51 | 50.69
2021-01-28 14:45 | 3.6837 | 1.544 | 0.34768 | 2.7144 | 70.9715 | 76.2128 | 1.2887 | 0.27667 | 444.1588 | 28.51 | 49.86
2021-01-28 14:50 | 2.9189 | 1.5399 | 0.34977 | 2.7102 | 77.1706 | 51.9433 | 1.2814 | 0.27666 | 444.2368 | 28.46 | 49.98
2021-01-28 14:55 | 3.7735 | 1.8217 | 0.39382 | 3.1841 | 76.4995 | 57.367 | 1.2962 | 0.32768 | 445.251 | 28.44 | 50.44
2021-01-28 15:00 | 5.7243 | 1.8792 | 0.34776 | 3.2304 | 77.4428 | 97.6373 | 1.3181 | 0.37139 | 444.064 | 28.51 | 50.4
2021-01-28 15:05 | 3.4927 | 1.6699 | 0.37913 | 2.9388 | 84.1215 | 70.3647 | 1.3689 | 0.33494 | 443.5851 | 28.52 | 50.01
2021-01-28 15:10 | 5.7492 | 1.7082 | 0.37914 | 2.9975 | 74.4764 | 50.154 | 1.3543 | 0.23301 | 442.4745 | 28.55 | 49.99
2021-01-28 15:15 | 4.2833 | 1.6877 | 0.34982 | 2.9368 | 64.8506 | 60.2206 | 1.2816 | 0.24029 | 443.9897 | 28.59 | 49.92
2021-01-28 15:20 | 4.8691 | 1.7982 | 0.33512 | 3.0914 | 82.168 | 77.6915 | 1.2596 | 0.31307 | 443.4104 | 28.66 | 49.43
2021-01-28 15:25 | 7.6325 | 1.9383 | 0.34757 | 3.3187 | 95.6783 | 16.1876 | 1.2591 | 0.37119 | 444.054 | 28.68 | 48.55
2021-01-28 15:30 | 4.4851 | 1.8454 | 0.31406 | 3.1427 | 108.2037 | 72.2513 | 1.2664 | 0.36391 | 444.5776 | 28.69 | 48.46
2021-01-28 15:35 | [9 empty] | 28.67 | 47.72
2021-01-28 15:40 | 5.0821 | 1.6972 | 0.33906 | 2.9406 | 82.9038 | 74.487 | 1.3023 | 0.40015 | 443.6555 | 28.71 | 47.49
2021-01-28 15:45 | 8.6857 | 1.6506 | 0.3453 | 2.8775 | 91.6456 | 81.345 | 1.3094 | 0.38555 | 444.7353 | 28.73 | 47.13
2021-01-28 15:50 | 7.0941 | 1.7067 | 0.32858 | 2.9446 | 82.552 | 80.3613 | 1.295 | 0.3492 | 444.1971 | 28.72 | 47.3
2021-01-28 15:55 | 7.3775 | 1.9055 | 0.3999 | 3.3207 | 87.5819 | 79.4985 | 1.3683 | 0.4003 | 443.4511 | 28.74 | 48.31
2021-01-28 16:00 | 6.0778 | 1.9533 | 0.38943 | 3.3834 | 111.3114 | 94.3293 | 1.3756 | 0.62591 | 445.5045 | 28.78 | 48.18
2021-01-28 16:05 | 4.3463 | 1.7093 | 0.3728 | 2.9908 | 107.0736 | 91.32 | 1.3177 | 0.60427 | 443.8145 | 28.76 | 49.01
2021-01-28 16:10 | 4.6026 | 1.5321 | 0.31635 | 2.6649 | 84.6989 | 60.6274 | 1.289 | 0.50978 | 443.7319 | 28.72 | 49.92
2021-01-28 16:15 | 5.6235 | 1.5583 | 0.33525 | 2.7239 | 80.9675 | 66.1859 | 1.2819 | 0.36419 | 443.6662 | 28.72 | 50.29
2021-01-28 16:20 | 4.6799 | 1.8441 | 0.36041 | 3.1871 | 62.5961 | 70.9103 | 1.2965 | 0.40789 | 444.2297 | 28.69 | 50.42
2021-01-28 16:25 | 6.0195 | 1.7404 | 0.35625 | 3.0219 | 47.6969 | 56.2569 | 1.3112 | 0.32052 | 444.7233 | 28.68 | 50.72
2021-01-28 16:30 | 5.2793 | 1.5994 | 0.33736 | 2.789 | 61.4028 | 49.9057 | 1.2892 | 0.30592 | 443.1741 | 28.69 | 50.43
2021-01-28 16:35 | 5.2539 | 1.7648 | 0.31851 | 3.0237 | 58.8642 | 71.2696 | 1.2747 | 0.32778 | 443.6595 | 28.71 | 50.44
2021-01-28 16:40 | 4.5541 | 1.6178 | 0.31652 | 2.7942 | 75.182 | 59.6802 | 1.297 | 0.38619 | 444.562 | 28.71 | 51.29
2021-01-28 16:45 | 6.3015 | 1.4686 | 0.30393 | 2.5551 | 68.2808 | 45.2994 | 1.3334 | 0.41532 | 444.11 | 28.67 | 51.32
2021-01-28 16:50 | 5.4198 | 1.3862 | 0.33318 | 2.458 | 62.4872 | 38.7982 | 1.3257 | 0.3715 | 445.3337 | 28.64 | 50.7
2021-01-28 16:55 | 6.4411 | 1.2839 | 0.35 | 2.318 | 59.4976 | 52.6611 | 1.3114 | 0.33513 | 444.2218 | 28.63 | 51.14
2021-01-28 17:00 | 6.6173 | 1.2998 | 0.30379 | 2.2962 | 56.7022 | 42.0141 | 1.34 | 0.35686 | 444.994 | 28.57 | 50.43
2021-01-28 17:05 | 4.9479 | 1.3397 | 0.26612 | 2.3176 | 73.4332 | 77.718 | 1.3403 | 0.26951 | 444.3728 | 28.58 | 50.85
2021-01-28 17:10 | 4.5415 | 1.2773 | 0.20962 | 2.1654 | 103.985 | 91.228 | 1.2825 | 0.18946 | 445.3382 | 28.53 | 51.92
2021-01-28 17:15 | 4.147 | 1.1394 | 0.17612 | 1.9227 | 83.7561 | 58.0525 | 1.2463 | 0.27696 | 446.4238 | 28.44 | 52.77
2021-01-28 17:20 | 3.9816 | 0.98634 | 0.18034 | 1.6922 | 73.8528 | 54.2615 | 1.2611 | 0.31344 | 447.1362 | 28.28 | 53.56
2021-01-28 17:25 | 4.403 | 1.0507 | 0.19503 | 1.8077 | 60.3815 | 37.3071 | 1.2757 | 0.30618 | 447.8214 | 28.15 | 54.17
2021-01-28 17:30 | 4.3513 | 1.2722 | 0.21807 | 2.1681 | 50.0211 | 26.8685 | 1.2828 | 0.29155 | 447.9931 | 28.08 | 54
2021-01-28 17:35 | 4.2232 | 1.2925 | 0.24949 | 2.2328 | 50.1983 | 33.2648 | 1.2754 | 0.26965 | 446.5573 | 28.02 | 53.85
2021-01-28 17:40 | 3.3041 | 0.90671 | 0.17818 | 1.5659 | 45.8447 | 39.8845 | 1.2752 | 0.29148 | 448.268 | 27.97 | 53.7
2021-01-28 17:45 | 3.5844 | 0.79038 | 0.19703 | 1.4107 | 44.1461 | 37.6762 | 1.2824 | 0.26959 | 447.3905 | 27.88 | 53.72
2021-01-28 17:50 | 4.0567 | 0.84103 | 0.18866 | 1.4757 | 52.4868 | 20.86 | 1.2897 | 0.26961 | 447.4959 | 27.79 | 54.17
2021-01-28 17:55 | 2.628 | 0.7262 | 0.19076 | 1.3039 | 36.6497 | 28.985 | 1.2825 | 0.24776 | 447.5918 | 27.71 | 54.56
2021-01-28 18:00 | 2.4617 | 0.60982 | 0.15509 | 1.0899 | 21.1322 | 16.1731 | 1.275 | 0.18214 | 448.3482 | 27.62 | 54.29
2021-01-28 18:05 | 2.4994 | 0.71359 | 0.12573 | 1.2195 | 35.4816 | 48.5601 | 1.2747 | 0.20395 | 449.1807 | 27.48 | 54.17
2021-01-28 18:10 | 2.5251 | 0.8818 | 0.11107 | 1.4627 | 42.5649 | 31.8013 | 1.2967 | 0.22582 | 449.2049 | 27.44 | 54.51
2021-01-28 18:15 | 2.2064 | 0.76975 | 0.1467 | 1.3245 | 34.9358 | 31.8646 | 1.2895 | 0.18213 | 448.7205 | 27.39 | 54.85
2021-01-28 18:20 | 2.7554 | 0.73708 | 0.11948 | 1.2514 | 31.0441 | 18.9 | 1.2824 | 0.18945 | 449.2673 | 27.32 | 55.6
2021-01-28 18:25 | 2.4751 | 0.58675 | 0.14046 | 1.0378 | 25.1393 | 16.9127 | 1.2826 | 0.14575 | 449.2561 | 27.28 | 56.16
2021-01-28 18:30 | 3.5213 | 0.52657 | 0.13837 | 0.94761 | 24.1085 | 22.0059 | 1.2826 | 0.15304 | 448.8162 | 27.22 | 56.36
2021-01-28 18:35 | 3.0748 | 0.517 | 0.12789 | 0.91826 | 35.6831 | 14.7591 | 1.2899 | 0.27693 | 448.3746 | 27.16 | 56.57
2021-01-28 18:40 | 3.1646 | 0.62377 | 0.13419 | 1.0903 | 30.6454 | 17.4869 | 1.2901 | 0.32071 | 449.9714 | 27.11 | 57.14
2021-01-28 18:45 | 2.2076 | 0.62651 | 0.15097 | 1.1113 | 44.3861 | 81.4528 | 1.2901 | 0.24053 | 450.5582 | 27.07 | 57.29
2021-01-28 18:50 | 1.4802 | 0.5499 | 0.13419 | 0.97501 | 71.6422 | 56.6768 | 1.2755 | 0.17493 | 449.0321 | 27.03 | 57.41
2021-01-28 18:55 | 1.9273 | 0.55003 | 0.13003 | 0.97314 | 55.679 | 45.8665 | 1.2831 | 0.13123 | 449.5322 | 26.98 | 58.22
2021-01-28 19:00 | 1.6082 | 0.58287 | 0.14891 | 1.0423 | 51.0638 | 35.0636 | 1.2831 | 0.058324 | 449.0777 | 26.93 | 58.39
2021-01-28 19:05 | 1.3905 | 0.49366 | 0.15511 | 0.91182 | 34.5445 | 26.462 | 1.2533 | 0.094724 | 449.4419 | 26.85 | 57.15
2021-01-28 19:10 | 1.5683 | 0.53443 | 0.15923 | 0.98052 | 14.2293 | 11.516 | 1.2454 | 0.11653 | 450.8116 | 26.79 | 55.99
2021-01-28 19:15 | 1.1854 | 0.43179 | 0.13405 | 0.79591 | 19.4358 | 16.6622 | 1.2523 | 0.10921 | 449.9289 | 26.76 | 55.26
2021-01-28 19:20 | 0.99446 | 0.37722 | 0.16341 | 0.74163 | 17.2475 | 21.6333 | 1.2599 | 0.072825 | 449.8301 | 26.7 | 56.17
2021-01-28 19:25 | 0.90517 | 0.37311 | 0.16131 | 0.73322 | 16.2676 | 11.8004 | 1.2453 | 0.080104 | 449.9685 | 26.62 | 56.32
2021-01-28 19:30 | 0.86654 | 0.66528 | 0.18008 | 1.1998 | 7.8091 | -5.8313 | 1.2374 | 0.11646 | 452.3847 | 26.56 | 55.26
2021-01-28 19:35 | 1.0198 | 0.46324 | 0.15709 | 0.86926 | 19.0491 | 9.7081 | 1.2523 | 0.13834 | 450.6875 | 26.54 | 56.16
2021-01-28 19:40 | 0.90541 | 0.52494 | 0.15297 | 0.95762 | 19.159 | 26.5553 | 1.2674 | 0.10926 | 451.0645 | 26.52 | 57.39
2021-01-28 19:45 | 1.1219 | 0.46059 | 0.18436 | 0.88827 | 122.3936 | 216.7999 | 1.2671 | 0.10195 | 336.9027 | 26.53 | 56.71
2021-01-28 19:50 | 0.99445 | 0.57403 | 0.16131 | 1.0412 | 240.586 | 132.4916 | 1.2671 | 0.094672 | 290.6124 | 26.59 | 56.52
2021-01-28 19:55 | 1.7596 | 0.71079 | 0.16762 | 1.2571 | 145.6258 | 67.7023 | 1.2673 | 0.11653 | 289.4181 | 26.69 | 56.53
2021-01-28 20:00 | 1.2878 | 0.59597 | 0.14457 | 1.0581 | 92.6228 | 56.1551 | 1.2673 | 0.0874 | 289.9202 | 26.72 | 56.43
2021-01-28 20:05 | 1.4791 | 0.47979 | 0.12153 | 0.85696 | 72.2734 | 25.1146 | 1.2746 | 0.087401 | 290.997 | 26.7 | 56.54
2021-01-28 20:10 | 1.4793 | 0.47574 | 0.14249 | 0.87172 | 54.6519 | 29.0144 | 1.282 | 0.11655 | 289.3742 | 26.7 | 56.83
2021-01-28 20:15 | 1.5562 | 0.46082 | 0.13205 | 0.83841 | 36.9816 | 23.8176 | 1.2896 | 0.12386 | 290.3305 | 26.73 | 57.47
2021-01-28 20:20 | 1.4288 | 0.64687 | 0.12997 | 1.1215 | 25.3005 | 22.7184 | 1.2752 | 0.13117 | 289.6762 | 26.82 | 57.52
2021-01-28 20:25 | 1.1481 | 0.60172 | 0.10691 | 1.0313 | 33.0867 | 18.411 | 1.2825 | 0.087442 | 290.1858 | 26.85 | 57.34
2021-01-28 20:30 | 1.1099 | 0.52788 | 0.109 | 0.91815 | 34.4951 | 7.8379 | 1.2679 | 0.10202 | 289.192 | 26.78 | 57.58
2021-01-28 20:35 | 1.3141 | 0.66197 | 0.12998 | 1.1447 | 13.4218 | 7.3182 | 1.2753 | 0.1166 | 289.1329 | 26.81 | 57.77
2021-01-28 20:40 | 1.0334 | 0.42945 | 0.1153 | 0.77568 | 10.4719 | 24.659 | 1.2753 | 0.10202 | 290.2283 | 26.78 | 57.82
2021-01-28 20:45 | 1.2121 | 0.43495 | 0.11112 | 0.77783 | 16.7603 | 16.4234 | 1.2681 | 0.10932 | 289.7456 | 26.71 | 58.25
2021-01-28 20:50 | 1.0847 | 0.38576 | 0.081778 | 0.67309 | 30.7077 | 22.9082 | 1.2683 | 0.12391 | 290.2259 | 26.72 | 58.61
2021-01-28 20:55 | 1.1231 | 0.40906 | 0.11953 | 0.74655 | 26.9736 | 32.7931 | 1.2757 | 0.11663 | 288.5994 | 26.73 | 58.82
2021-01-28 21:00 | 1.5827 | 0.54048 | 0.10697 | 0.93543 | 26.2529 | 12.6823 | 1.2759 | 0.14582 | 289.5856 | 26.76 | 59.16
2021-01-28 21:05 | 1.1616 | 0.46115 | 0.077608 | 0.78447 | 25.7238 | 14.7766 | 1.2687 | 0.11666 | 288.5235 | 26.74 | 59.43
2021-01-28 21:10 | 1.3659 | 0.44201 | 0.090198 | 0.76563 | 21.1192 | 12.2855 | 1.2687 | 0.12396 | 289.0882 | 26.69 | 59.74
2021-01-28 21:15 | 0.91919 | 0.36267 | 0.090205 | 0.64612 | 7.5884 | 1.2664 | 1.2688 | 0.094799 | 289.6347 | 26.65 | 60.1
2021-01-28 21:20 | 0.82987 | 0.35448 | 0.073427 | 0.61679 | 5.3418 | -1.0418 | 1.2689 | 0.051049 | 289.6551 | 26.61 | 60.42
2021-01-28 21:25 | 0.82992 | 0.31207 | 0.067137 | 0.54549 | 12.002 | 5.6282 | 1.2617 | 0.043759 | 289.6572 | 26.59 | 60.66
2021-01-28 21:30 | 0.66391 | 0.28468 | 0.092309 | 0.52658 | 1.6751 | 4.5963 | 1.2471 | 0.065635 | 289.189 | 26.54 | 60.7
2021-01-28 21:35 | 0.85534 | 0.27234 | 0.096496 | 0.51395 | -5.2291 | 4.5039 | 1.2542 | 0.10209 | 289.8139 | 26.47 | 60.69
2021-01-28 21:40 | 0.62556 | 0.28877 | 0.096499 | 0.53913 | 6.0462 | 19.2111 | 1.2616 | 0.12397 | 289.8849 | 26.39 | 61.04
2021-01-28 21:45 | 0.85547 | 0.28744 | 0.094414 | 0.53711 | 18.6519 | 13.422 | 1.2763 | 0.094812 | 289.8744 | 26.36 | 61.54
2021-01-28 21:50 | 0.77881 | 0.2491 | 0.092309 | 0.47413 | 21.8169 | 17.3228 | 1.2762 | 0.094805 | 289.9338 | 26.32 | 61.48
2021-01-28 21:55 | 0.66364 | 0.20385 | 0.075495 | 0.38796 | 10.3323 | 0.49007 | 1.283 | 0.087478 | 290.0981 | 26.27 | 60.51
2021-01-28 22:00 | 0.7911 | 0.22159 | 0.083866 | 0.42353 | 9.8913 | 3.1031 | 1.2827 | 0.094748 | 289.675 | 26.22 | 60.09
2021-01-28 22:05 | 0.65072 | 0.18876 | 0.081768 | 0.3711 | 15.3826 | 2.7152 | 1.29 | 0.087457 | 289.1894 | 26.18 | 60.16
2021-01-28 22:10 | 0.49767 | 0.14774 | 0.0671 | 0.29356 | 9.3307 | 3.5935 | 1.2902 | 0.087468 | 289.7436 | 26.12 | 60.73
2021-01-28 22:15 | 0.58712 | 0.13272 | 0.069211 | 0.27265 | 0.14295 | -7.2905 | 1.2904 | 0.094776 | 290.7966 | 26.07 | 61.5
2021-01-28 22:20 | 0.56166 | 0.13684 | 0.073414 | 0.28317 | 0.99056 | -6.6173 | 1.2906 | 0.087496 | 289.2354 | 26 | 62.1
2021-01-28 22:25 | 0.54892 | 0.15601 | 0.056637 | 0.29577 | 8.4254 | 15.0942 | 1.2906 | 0.087501 | 289.7503 | 26 | 62.27
2021-01-28 22:30 | 0.53616 | 0.17517 | 0.054539 | 0.32094 | 4.1463 | -0.83743 | 1.2906 | 0.094793 | 289.2487 | 25.97 | 62.37
2021-01-28 22:35 | 0.51069 | 0.18066 | 0.058742 | 0.33567 | 3.6566 | -14.5956 | 1.2835 | 0.087512 | 289.7909 | 25.92 | 62.94
2021-01-28 22:40 | 0.44692 | 0.21081 | 0.07134 | 0.39447 | 8.8772 | -2.9727 | 1.2764 | 0.087526 | 290.2783 | 25.92 | 63.39
2021-01-28 22:45 | 0.68962 | 0.2122 | 0.067152 | 0.39242 | 3.4941 | 7.2436 | 1.2766 | 0.080242 | 290.2333 | 25.93 | 63.71
2021-01-28 22:50 | 0.84268 | 0.21763 | 0.065039 | 0.39862 | -2.5434 | -0.66393 | 1.2763 | 0.065637 | 289.4804 | 25.93 | 62.97
2021-01-28 22:55 | 0.6634 | 0.23113 | 0.060794 | 0.41508 | -0.6634 | -15.493 | 1.2607 | 0.058298 | 289.1784 | 25.93 | 60.64
2021-01-28 23:00 | 0.48463 | 0.14492 | 0.056582 | 0.27662 | 5.4686 | -6.9378 | 1.2384 | 0.10199 | 289.8493 | 25.89 | 59.76
2021-01-28 23:05 | 0.71409 | 0.15447 | 0.044002 | 0.28077 | -8.2222 | -5.6311 | 1.2455 | 0.13111 | 289.4456 | 25.8 | 59.66
2021-01-28 23:10 | 0.7651 | 0.17087 | 0.056575 | 0.3185 | -3.0196 | -4.1214 | 1.2601 | 0.11654 | 289.9922 | 25.78 | 59.78
2021-01-28 23:15 | 0.84154 | 0.26107 | 0.050284 | 0.44837 | 6.2121 | -1.1221 | 1.26 | 0.12381 | 289.4559 | 25.81 | 59.42
2021-01-28 23:20 | 0.94322 | 0.34706 | 0.050267 | 0.58017 | 3.2121 | -2.9469 | 1.2741 | 0.14561 | 290.0786 | 25.82 | 58.36
2021-01-28 23:25 | 0.62446 | 0.40848 | 0.073294 | 0.69943 | -9.0024 | -5.6584 | 1.2739 | 0.16015 | 290.1174 | 25.83 | 57.83
2021-01-28 23:30 | 0.57338 | 0.22947 | 0.060718 | 0.41037 | -2.4872 | -14.0465 | 1.2737 | 0.13101 | 290.7239 | 25.81 | 57.34
2021-01-28 23:35 | 0.39495 | 0.3032 | 0.058618 | 0.52338 | 10.6001 | 1.906 | 1.2663 | 0.087328 | 289.1357 | 25.83 | 56.98
2021-01-28 23:40 | 0.33122 | 0.25947 | 0.05024 | 0.45006 | 3.9848 | -7.9799 | 1.2661 | 0.06549 | 290.218 | 25.84 | 56.67
2021-01-28 23:45 | 0.36943 | 0.37691 | 0.046052 | 0.6238 | -3.8727 | 4.4842 | 1.2661 | 0.072766 | 290.2411 | 25.82 | 56.7
2021-01-28 23:50 |  | 0.26228 | 0.041878 | 0.446 | 8.6141 | -6.3714 | 1.2592 | 0.080066 | 289.2275 | 25.68 | 58.04
2021-01-28 23:55 | 0.255 | 0.19272 | 0.048187 | 0.3415 | 10.4347 | 2.5806 | 1.2672 | 0.065546 | 290.7765 | 25.56 | 60.17
2021-01-29 | 0.39542 | 0.16956 | 0.039823 | 0.29972 | 6.6022 | 9.286 | 1.2605 | 0.043715 | 291.1766 | 25.57 | 61.4
2021-01-29 00:05 | 0.9313 | 0.14223 | 0.046119 | 0.26414 | 11.0123 | -3.2251 | 1.268 | 0.036435 | 289.4846 | 25.62 | 61.7
2021-01-29 00:10 | 0.35727 | 0.10806 | 0.044029 | 0.20757 | 14.9847 | -4.522 | 1.2609 | 0 | 288.8978 | 25.63 | 62.13
2021-01-29 00:15 | 0.43393 | 0.14639 | 0.046137 | 0.27053 | 5.2888 | -1.0516 | 1.2612 | 0.02187 | 290.4638 | 25.59 | 62.99
2021-01-29 00:20 | 0.59994 | 0.20115 | 0.046145 | 0.35448 | -2.1853 | 5.5756 | 1.2541 | 0.036456 | 289.3109 | 25.63 | 63.36
2021-01-29 00:25 | 0.49782 | 0.13 | 0.046145 | 0.24541 | 0.7863 | -10.4875 | 1.2468 | 0.043747 | 289.8342 | 25.64 | 63.31
2021-01-29 00:30 | 0.34464 | 0.10536 | 0.046143 | 0.20765 | 5.6367 | 4.0131 | 1.2468 | 0.036455 | 290.3842 | 25.63 | 63.26
2021-01-29 00:35 | 0.35733 | 0.057459 | 0.037747 | 0.12582 | -5.9215 | -1.5314 | 1.2465 | 0.021869 | 290.5361 | 25.53 | 63.07
2021-01-29 00:40 | 0.29348 | 0.067027 | 0.035645 | 0.13839 | -13.5768 | -7.1967 | 1.2536 | 0.029154 | 289.6171 | 25.42 | 63.08
2021-01-29 00:45 | 0.29347 | 0.095749 | 0.04403 | 0.1908 | -3.389 | -9.0033 | 1.2536 | 0.029154 | 290.1884 | 25.39 | 63.09
2021-01-29 00:50 | 0.34441 | 0.077944 | 0.037729 | 0.1572 | 6.429 | -18.6747 | 1.2532 | 0.014572 | 291.9312 | 25.33 | 62.41
2021-01-29 00:55 | 0.28044 | 0.12025 | 0.043988 | 0.22832 | -4.3749 | -1.0198 | 1.2524 | 0.029125 | 291.0895 | 25.3 | 60.48
2021-01-29 01:00 | 0.31856 | 0.12294 | 0.052345 | 0.24079 | -8.1755 | -4.9032 | 1.2592 | 0.029114 | 291.4107 | 25.34 | 59.05
2021-01-29 01:05 |  |  |  |  | 0.9786 | -11.3457 |  |  | 290.3184 | 25.37 | 58.92
2021-01-29 01:10 |  |  |  |  | 3.7724 | -2.7528 |  |  | 290.2567 | 25.38 | 59.43
2021-01-29 01:15 |  |  |  |  | -6.006 | 7.9536 |  |  | 291.2648 | 25.4 | 59.75
2021-01-29 01:20 |  |  |  |  | -16.9479 | -6.6588 |  |  | 290.248 | 25.34 | 60.07
2021-01-29 01:25 |  |  |  |  | -4.4161 | -11.6879 |  |  | 290.7648 | 25.31 | 60.65
2021-01-29 01:30 |  |  |  |  | 4.8038 | -11.5965 |  |  | 291.2877 | 25.31 | 60.75
2021-01-29 01:35 |  |  |  |  | -8.6498 | -0.23461 |  |  | 290.7538 | 25.28 | 61.18
2021-01-29 01:40 |  |  |  |  | -11.6181 | -5.0492 |  |  | 290.2589 | 25.24 | 61.34
2021-01-29 01:45 |  |  |  |  | 2.3767 | -7.8442 |  |  | 290.2542 | 25.24 | 61.39
2021-01-29 01:50 |  |  |  |  | 9.303 | -4.9575 |  |  | 290.7905 | 25.23 | 61.49
2021-01-29 01:55 |  |  |  |  | 1.8567 | 1.6323 |  |  | 290.7572 | 25.23 | 61.84
2021-01-29 02:00 |  |  |  |  | -5.6721 | -4.5295 |  |  | 290.7073 | 25.29 | 61.53
2021-01-29 02:05 |  |  |  |  | 8.9563 | -0.83647 |  |  | 290.7273 | 25.29 | 61.32
2021-01-29 02:10 | 0.35703 | 0.092951 | 0.03562 | 0.1781 | 3.2847 | -7.9975 | 1.3183 | -0.029134 | 290.7245 | 25.29 | 61.35
2021-01-29 02:15 | 0.16578 | 0.1121 | 0.039813 | 0.21164 | -11.0281 | -7.1208 | 1.2893 | 0.0072841 | 289.6753 | 25.25 | 61.74
2021-01-29 02:20 | 0.3316 | 0.095705 | 0.050297 | 0.197 | -6.2647 | 1.7549 | 1.2749 | 0.021855 | 290.7316 | 25.22 | 62.25
2021-01-29 02:25 | 0.25514 | 0.23248 | 0.048213 | 0.40457 | 10.7668 | 7.2153 | 1.2679 | 0.051007 | 289.5891 | 25.23 | 62.93
2021-01-29 02:30 | 0.21689 | 0.21746 | 0.054508 | 0.38785 | 14.6161 | 2.8987 | 1.2608 | 0.036438 | 291.0719 | 25.31 | 63.01
2021-01-29 02:35 | 0.34445 | 0.21881 | 0.071274 | 0.40668 | -0.79606 | 11.6449 | 1.2606 | 0.065583 | 291.6299 | 25.31 | 62.74
2021-01-29 02:40 | 0.2041 | 0.20102 | 0.058692 | 0.36892 | -1.5716 | -2.1023 | 1.2679 | 0.036433 | 290.0609 | 25.3 | 62.59
2021-01-29 02:45 | 0.24238 | 0.24616 | 0.058695 | 0.43602 | 3.5108 | -13.7369 | 1.2606 | 0.051008 | 290.5798 | 25.3 | 62.73
2021-01-29 02:50 | 0.20411 | 0.29812 | 0.083848 | 0.54082 | 6.5825 | -5.0415 | 1.2606 | 0.036434 | 291.0693 | 25.35 | 62.48
2021-01-29 02:55 | 0.24237 | 0.2735 | 0.077558 | 0.49469 | 0.75519 | 6.9498 | 1.2533 | 0.036433 | 289.9721 | 25.39 | 62.27
2021-01-29 03:00 | [9 empty] | 25.36 | 61.97
2021-01-29 03:05 | -0.91834 | 0.24612 | 0.079643 | 0.4569 | 2.602 | -5.2448 | 1.2604 | 0.036428 | 291.1068 | 25.36 | 61.95
2021-01-29 03:10 | 0.52297 | 0.25707 | 0.077551 | 0.47159 | 7.2859 | -5.3164 | 1.2605 | 0.058287 | 290.2029 | 25.43 | 61.78
2021-01-29 03:15 | 0.35712 | 0.19415 | 0.069161 | 0.36676 | 2.3162 | 7.9995 | 1.2531 | 0.043712 | 289.1441 | 25.45 | 61.46
2021-01-29 03:20 | 0.31883 | 0.16816 | 0.062868 | 0.32062 | 4.1014 | 13.855 | 1.2602 | 0.043707 | 291.1158 | 25.39 | 61.44
2021-01-29 03:25 | 0.17854 | 0.13945 | 0.054485 | 0.27033 | 7.4478 | -8.9475 | 1.2602 | 0.029138 | 290.6524 | 25.32 | 61.69
2021-01-29 03:30 | 0.2934 | 0.20786 | 0.0545 | 0.37312 | 8.4704 | -2.7861 | 1.2533 | 0.02186 | 290.8617 | 25.27 | 62.67
2021-01-29 03:35 | 0.319 | 0.30367 | 0.096449 | 0.56192 | -3.1543 | -4.2057 | 1.2536 | 0.036442 | 289.6748 | 25.32 | 63.27
2021-01-29 03:40 | 0.66384 | 0.34624 | 0.086008 | 0.61884 | -5.5252 | 4.9635 | 1.2542 | 0.058337 | 288.9331 | 25.39 | 64.5
2021-01-29 03:45 | 0.43414 | 0.35452 | 0.086025 | 0.62945 | -1.2258 | 1.9919 | 1.2618 | 0.043761 | 289.8508 | 25.48 | 64.75
2021-01-29 03:50 | 0.37031 | 0.25324 | 0.077636 | 0.46582 | 10.9204 | -0.87854 | 1.2545 | 0.036469 | 289.8258 | 25.49 | 64.87
2021-01-29 03:55 | 0.66408 | 0.62154 | 0.10702 | 1.0618 | 4.8222 | 9.9305 | 1.2547 | 0.065652 | 289.226 | 25.53 | 65.03
2021-01-29 04:00 | 0.79226 | 0.77396 | 0.15118 | 1.3375 | 4.6615 | 10.836 | 1.2554 | 0.07299 | 288.8517 | 25.74 | 65.98
2021-01-29 04:05 | 0.66452 | 0.60688 | 0.11129 | 1.0415 | 17.9727 | 18.4226 | 1.2555 | 0.065696 | 288.2238 | 25.82 | 65.88
2021-01-29 04:10 | 0.80503 | 0.56574 | 0.10499 | 0.97217 | 28.1529 | 24.5546 | 1.2554 | 0.072989 | 289.7986 | 25.86 | 65.48
2021-01-29 04:15 | 0.86889 | 0.53558 | 0.11128 | 0.93224 | 26.8639 | 17.5617 | 1.2554 | 0.065688 | 289.2499 | 25.89 | 65.26
2021-01-29 04:20 | 0.83047 | 0.57388 | 0.11967 | 0.99933 | 17.8258 | 25.7983 | 1.2552 | 0.065681 | 288.7287 | 25.91 | 64.9
2021-01-29 04:25 | 0.99631 | 0.85718 | 0.16162 | 1.4755 | 35.6221 | 44.7269 | 1.2622 | 0.072961 | 289.2737 | 25.97 | 63.93
2021-01-29 04:30 | 1.0343 | 0.96912 | 0.23499 | 1.7205 | 37.2542 |  | 1.2618 | 0.080229 | 343.8262 | 26.09 | 62.46
2021-01-29 04:35 | 1.2764 | 1.0221 | 0.20135 | 1.7702 |  |  | 1.2613 | 0.080197 | 453.5166 | 26.19 | 60.96
2021-01-29 04:40 | 1.927 | 0.94804 | 0.16566 | 1.6188 |  | -5.1658 | 1.261 | 0.11663 | 454.1473 | 26.18 | 60.45
2021-01-29 04:45 | 2.4374 | 1.2791 | 0.2034 | 2.164 | -10.5765 | 46.1241 | 1.261 | 0.17494 | 454.1681 | 26.17 | 60.45
2021-01-29 04:50 | 2.4246 | 1.3994 | 0.24533 | 2.3904 | 27.1757 | 47.0317 | 1.2683 | 0.21867 | 453.1031 | 26.18 | 60.35
2021-01-29 04:55 | 2.9736 | 1.416 | 0.25794 | 2.4263 | 54.5812 | 64.597 | 1.2611 | 0.23327 | 451.8937 | 26.25 | 60.38
2021-01-29 05:00 | 2.1451 | 1.3962 | 0.27066 | 2.4107 | 75.9267 | 60.8088 | 1.269 | 0.24797 | 452.0778 | 26.33 | 61.52
2021-01-29 05:05 | 3.5613 | 1.6694 | 0.36915 | 2.928 | 66.4669 | 58.1343 | 1.2759 | 0.26977 | 451.6935 | 26.33 | 60.6
2021-01-29 05:10 | 3.497 | 1.754 | 0.40265 | 3.0912 | 74.3498 | 68.9589 | 1.2757 | 0.26973 | 450.0787 | 26.39 | 59.98
2021-01-29 05:15 | 3.2288 | 1.8031 | 0.39215 | 3.1561 | 82.0749 | 66.2194 | 1.283 | 0.2843 | 450.5399 | 26.45 | 59.63
2021-01-29 05:20 | 2.4505 | 1.9592 | 0.39218 | 3.3954 | 89.0033 | 85.9708 | 1.2758 | 0.23329 | 450.3275 | 26.57 | 59.41
2021-01-29 05:25 | 3.178 | 2.0277 | 0.3775 | 3.4856 | 111.1618 | 102.4522 | 1.2758 | 0.35722 | 449.1856 | 26.62 | 59.29
2021-01-29 05:30 | 3.8673 | 2.3602 | 0.53691 | 4.1568 | 127.8186 | 122.366 | 1.2758 | 0.43014 | 448.5996 | 26.65 | 59.26
2021-01-29 05:35 | 5.221 | 2.8012 | 0.66704 | 4.9608 | 145.1263 | 167.1439 | 1.276 | 0.45208 | 446.8438 | 26.72 | 59.42
2021-01-29 05:40 | 5.9747 | 3.1791 | 0.68177 | 5.557 | 181.1189 | 181.7827 | 1.298 | 0.50316 | 447.0976 | 26.88 | 59.09
2021-01-29 05:45 | 6.0643 | 3.312 | 0.6818 | 5.7586 | 196.5181 | 181.3816 | 1.3199 | 0.51776 | 445.7846 | 27.04 | 58.65
2021-01-29 05:50 | 7.9932 | 3.7081 | 0.74485 | 6.4288 | 223.2386 | 201.7054 | 1.3055 | 0.64912 | 446.0097 | 27.2 | 58.5
2021-01-29 05:55 | 6.7037 | 3.8341 | 0.78892 | 6.6681 | 237.7787 | 198.4605 | 1.2837 | 0.65643 | 445.7941 | 27.34 | 58.07
2021-01-29 06:00 | 6.3967 | 4.0788 | 0.69864 | 6.9507 | 220.7314 | 202.7643 | 1.2836 | 0.70013 | 446.7235 | 27.45 | 57.47
2021-01-29 06:05 | 5.5923 | 4.6454 | 0.66297 | 7.7836 | 229.5153 | 176.7686 | 1.3127 | 0.71471 | 445.5213 | 27.55 | 57.13
2021-01-29 06:10 | 5.6438 | 4.7142 | 0.77632 | 8.0024 | 218.2328 | 174.1449 | 1.342 | 0.66371 | 445.3732 | 27.63 | 57.04
2021-01-29 06:15 | 4.8403 | 3.7992 | 0.78067 | 6.6021 | 205.0148 | 173.9448 | 1.3131 | 0.48147 | 446.731 | 27.72 | 57.27
2021-01-29 06:20 | 5.2494 | 3.3983 | 0.74505 | 5.9541 | 203.3544 | 154.309 | 1.2913 | 0.37937 | 446.1413 | 27.74 | 57.4
2021-01-29 06:25 | 6.335 | 3.2573 | 0.64641 | 5.6414 | 179.2186 | 150.3843 | 1.2986 | 0.45232 | 446.1002 | 27.77 | 57.28
2021-01-29 06:30 | 5.8756 | 3.2465 | 0.59818 | 5.5725 | 179.7223 | 165.1201 | 1.3279 | 0.43776 | 447.1057 | 27.78 | 57.44
2021-01-29 06:35 | 7.0889 | 2.8549 | 0.51841 | 4.8944 | 180.8413 | 136.801 | 1.3205 | 0.47423 | 445.5086 | 27.8 | 57.3
2021-01-29 06:40 | 6.0412 | 2.4495 | 0.48061 | 4.2352 | 170.9426 | 138.7363 | 1.4518 | 0.53257 | 445.5136 | 27.81 | 57.15
2021-01-29 06:45 | 4.317 | 2.407 | 0.43024 | 4.1198 | 154.6883 | 120.7037 | 1.4737 | 0.3283 | 446.9685 | 27.89 | 56.92
2021-01-29 06:50 | 6.0805 | 3.4207 | 0.51846 | 5.7618 | 157.7034 | 137.6124 | 1.3645 | 0.53265 | 444.7877 | 27.9 | 57.24
2021-01-29 06:55 | 6.8106 | 3.6669 | 0.51442 | 6.1331 | 154.4902 | 130.7846 | 1.3211 | 0.61309 | 447.0915 | 28.03 | 57.59
2021-01-29 07:00 | 5.9179 | 3.0665 | 0.49146 | 5.1919 | 175.0563 | 149.3296 | 1.3068 | 0.46725 | 444.7129 | 28.13 | 57.99
2021-01-29 07:05 | 5.1906 | 2.6218 | 0.43067 | 4.4495 | 154.1342 | 140.2243 | 1.2926 | 0.36514 | 444.0287 | 28.16 | 58.55
2021-01-29 07:10 | 4.77 | 2.6869 | 0.40136 | 4.5221 | 154.3577 | 125.4156 | 1.3075 | 0.35062 | 446.4531 | 28.22 | 59
2021-01-29 07:15 | 6.0749 | 2.8476 | 0.43502 | 4.7978 | 179.1942 | 149.2774 | 1.4099 | 0.48215 | 445.7148 | 28.28 | 59.1
2021-01-29 07:20 | 6.0246 | 2.379 | 0.47081 | 4.1175 | 172.9975 | 138.0726 | 1.4247 | 0.39454 | 444.6988 | 28.27 | 59.43
2021-01-29 07:25 | 5.3993 | 2.0752 | 0.39525 | 3.5762 | 149.7666 | 87.6368 | 1.3082 | 0.34348 | 446.0993 | 28.31 | 59.95
2021-01-29 07:30 | 6.9728 | 2.1711 | 0.41626 | 3.7464 | 119.1192 | 98.1572 | 1.3008 | 0.46041 | 445.5677 | 28.32 | 59.87
2021-01-29 07:35 | 8.4576 | 3.2234 | 0.45414 | 5.3971 | 116.1594 | 111.5327 | 1.3155 | 0.52622 | 445.0252 | 28.31 | 60.09
2021-01-29 07:40 | 7.1658 | 2.6735 | 0.42474 | 4.5249 | 140.5836 | 138.9252 | 1.3303 | 0.54819 | 443.9408 | 28.31 | 60.29
2021-01-29 07:45 | 6.5537 | 2.6113 | 0.41015 | 4.4149 | 147.8166 | 99.2271 | 1.3307 | 0.5118 | 444.894 | 28.28 | 61.2
2021-01-29 07:50 | 8.8989 | 2.7068 | 0.42079 | 4.5698 | 138.8375 |  | 1.3238 | 0.52659 | 444.6841 | 28.33 | 61.8
2021-01-29 07:55 | 9.0868 | 2.9552 | 0.46266 | 4.9925 | 147.6715 | 96.3454 | 1.3817 | 0.70911 | 445.8771 | 28.37 | 60.5
2021-01-29 08:00 | 7.2157 | 2.8911 | 0.45199 | 4.8836 | 155.7972 | 138.6229 | 1.4469 | 0.64309 | 446.0198 | 28.38 | 59.57
2021-01-29 08:05 | 6.3059 | 2.2611 | 0.38673 | 3.8526 | 149.2223 | 137.4854 | 1.4028 | 0.43106 | 444.6524 | 28.31 | 59.22
2021-01-29 08:10 | 6.6405 | 1.9367 | 0.37844 | 3.3471 | 115.7777 | 103.2286 | 1.3228 | 0.32157 | 445.0513 | 28.3 | 60.06
2021-01-29 08:15 | 8.2942 | 2.9954 | 0.50478 | 5.0941 | 40.6212 | 89.1066 | 1.3014 | 0.49716 | 445.3312 | 28.35 | 60.86
2021-01-29 08:20 | 8.3576 | 2.5177 | 0.45637 | 4.3134 | 85.0346 | 91.1677 | 1.3086 | 0.47519 | 446.8965 | 28.38 | 60.55
2021-01-29 08:25 | 5.517 | 2.1832 | 0.42698 | 3.7734 | 99.8023 | 106.5097 | 1.2795 | 0.3802 | 446.2024 | 28.4 | 60.88
2021-01-29 08:30 | 4.8633 | 1.7492 | 0.33017 | 3.0115 | 113.2166 | 106.3568 | 1.2939 | 0.34358 | 445.4049 | 28.34 | 60.56
2021-01-29 08:35 | 5.6188 | 1.8482 | 0.42483 | 3.2577 | 137.6966 | 116.1943 | 1.3013 | 0.32899 | 445.9556 | 28.3 | 60.89
2021-01-29 08:40 | 6.1206 | 2.3733 | 0.41871 | 4.0566 | 128.1179 | 68.9503 | 1.3092 | 0.40958 | 444.7105 | 28.3 | 62.01
2021-01-29 08:45 | 5.8888 | 2.6006 | 0.41651 | 4.4028 | 133.1784 | 103.7448 | 1.2943 | 0.40949 | 444.3031 | 28.29 | 61.46
2021-01-29 08:50 | 4.4924 | 2.375 | 0.39749 | 4.0358 | 140.7047 | 113.0696 | 1.2794 | 0.46057 | 445.4676 | 28.28 | 60.92
2021-01-29 08:55 | 3.4935 | 1.9973 | 0.35326 | 3.4148 | 111.033 | 77.3423 | 1.2938 | 0.46049 | 446.619 | 28.21 | 60.78
2021-01-29 09:00 | 3.968 | 1.7097 | 0.35966 | 2.9804 | 98.8573 | 73.3289 | 1.2941 | 0.46062 | 446.571 | 28.16 | 61.66
2021-01-29 09:05 | 4.6871 | 1.8506 | 0.35142 | 3.1902 | 76.8175 | 80.6082 | 1.3094 | 0.40964 | 446.3661 | 28.15 | 62.96
2021-01-29 09:10 | 3.1629 | 1.8655 | 0.39769 | 3.2593 | 71.4022 | 55.7593 | 1.2873 | 0.32183 | 446.4328 | 28.13 | 62.82
2021-01-29 09:15 | 3.9177 | 1.8473 | 0.35974 | 3.1914 | 76.1409 | 54.2225 | 1.2725 | 0.27058 | 445.608 | 28.09 | 62.41
2021-01-29 09:20 | 3.7752 | 1.627 | 0.32174 | 2.8157 | 76.8455 | 81.5856 | 1.2719 | 0.24122 | 448.1072 | 27.95 | 61.81
2021-01-29 09:25 | 3.6481 | 1.6741 | 0.3113 | 2.8774 | 103.5501 | 97.1807 | 1.2722 | 0.26322 | 446.9943 | 27.92 | 62.54
2021-01-29 09:30 | 2.9054 | 1.7796 | 0.31127 | 3.0391 | 96.2904 | 65.6544 | 1.2721 | 0.25588 | 447.5643 | 27.92 | 62.28
2021-01-29 09:35 | 3.6329 | 1.6291 | 0.33421 | 2.8292 | 78.4911 | 58.5152 | 1.2787 | 0.29958 | 446.7957 | 27.9 | 60.88
2021-01-29 09:40 | 4.5023 | 1.5837 | 0.31316 | 2.7407 | 77.8188 | 59.2773 | 1.2932 | 0.33608 | 446.2814 | 27.92 | 60.57
2021-01-29 09:45 | 3.8639 | 1.554 | 0.37842 | 2.7625 | 74.473 | 77.6153 | 1.2935 | 0.29232 | 445.4835 | 28.02 | 60.94
2021-01-29 09:50 | 3.9658 | 1.477 | 0.41202 | 2.676 | 80.1345 | 71.4558 | 1.2715 | 0.31421 | 446.0588 | 28.02 | 60.65
2021-01-29 09:55 | 4.0047 | 1.5705 | 0.37843 | 2.7857 | 81.926 | 70.2164 | 1.2716 | 0.2704 | 446.0002 | 28.02 | 60.99
2021-01-29 10:00 | 3.1082 | 1.7332 | 0.38674 | 3.0456 | 82.3341 | 86.5296 | 1.264 | 0.21919 | 446.1331 | 28.01 | 60.34
2021-01-29 10:05 | 2.7121 | 1.7046 | 0.34054 | 2.9535 | 111.174 | 117.3452 | 1.2715 | 0.19729 | 444.9382 | 28.07 | 60.45
2021-01-29 10:10 | 3.2137 | 1.6841 | 0.3282 | 2.9117 | 129.294 | 109.3719 | 1.2725 | 0.28522 | 445.543 | 28.12 | 62.42
2021-01-29 10:15 | 3.407 | 1.3978 | 0.30517 | 2.4498 | 95.8877 | 69.2363 | 1.273 | 0.29996 | 447.0077 | 28.08 | 63.54
2021-01-29 10:20 | 3.2652 | 1.3795 | 0.28405 | 2.3986 | 91.1683 | 63.2135 | 1.2726 | 0.32913 | 446.2804 | 27.95 | 63.27
2021-01-29 10:25 | 3.2021 | 1.6943 | 0.2694 | 2.8665 | 80.8868 | 80.4052 | 1.2876 | 0.23411 | 446.7051 | 27.93 | 64.1
2021-01-29 10:30 | 3.7386 | 1.6855 | 0.31137 | 2.897 | 87.8631 | 95.5861 | 1.2945 | 0.25597 | 446.9738 | 27.86 | 63.4
2021-01-29 10:35 | 3.0222 | 1.5869 | 0.31774 | 2.7523 | 111.1025 | 67.686 | 1.2874 | 0.25601 | 446.9272 | 27.84 | 63.92
2021-01-29 10:40 | 2.9964 | 1.6747 | 0.30931 | 2.8764 | 89.3703 | 74.7929 | 1.2946 | 0.24869 | 446.9443 | 27.84 | 63.82
2021-01-29 10:45 | 3.6623 | 1.7722 | 0.32404 | 3.0405 | 83.7767 | 65.286 | 1.2873 | 0.28526 | 446.4208 | 27.84 | 63.81
2021-01-29 10:50 | 4.2115 | 2.1764 | 0.40386 | 3.742 | 89.3396 | 64.1885 | 1.2723 | 0.27054 | 447.0536 | 27.87 | 62.81
2021-01-29 10:55 | 2.9945 | 2.0605 | 0.35958 | 3.5201 | 81.5724 | 88.2984 | 1.2426 | 0.2266 | 446.1114 | 27.89 | 61.93
2021-01-29 11:00 | 2.9686 | 1.598 | 0.3301 | 2.7796 | 88.9954 | 69.0446 | 1.2352 | 0.26312 | 447.2245 | 27.88 | 61.69
2021-01-29 11:05 | 3.5323 | 1.3802 | 0.28811 | 2.4037 | 83.6894 | 57.4789 | 1.2427 | 0.2851 | 445.0319 | 27.88 | 62.22
2021-01-29 11:10 | 4.1232 | 1.4331 | 0.31562 | 2.5102 | 62.0068 | 58.0116 | 1.2361 | 0.3072 | 445.8737 | 27.86 | 63.69
2021-01-29 11:15 | 4.1367 | 1.3949 | 0.3767 | 2.5149 | 83.5134 | 82.1916 | 1.229 | 0.29993 | 446.3203 | 27.86 | 64.15
2021-01-29 11:20 | 5.176 | 1.416 | 0.34947 | 2.52 | 86.8751 | 72.577 | 1.2221 | 0.38786 | 445.0774 | 27.88 | 65.03
2021-01-29 11:25 | 4.8319 | 1.2984 | 0.30959 | 2.2998 | 88.7022 | 44.8176 | 1.2226 | 0.35873 | 446.0233 | 27.89 | 65.91
2021-01-29 11:30 | 3.6516 | 1.1922 | 0.28423 | 2.1096 | 75.7894 | 59.2457 | 1.2149 | 0.28542 | 445.7606 | 27.81 | 65.38
2021-01-29 11:35 | 2.6773 | 1.1398 | 0.28207 | 2.0292 | 54.7049 | 33.5116 | 1.2147 | 0.19025 | 446.9077 | 27.8 | 64.93
2021-01-29 11:40 | 2.6259 | 1.4212 | 0.33045 | 2.511 | 49.945 | 42.69 | 1.2219 | 0.20486 | 444.8664 | 27.79 | 64.72
2021-01-29 11:45 | 2.6136 | 1.3515 | 0.30526 | 2.3768 | 61.8253 | 53.7794 | 1.2368 | 0.44641 | 445.7555 | 27.83 | 65.16
2021-01-29 11:50 | 3.2668 | 1.2854 | 0.25682 | 2.2272 | 70.7771 | 64.8841 | 1.2293 | 0.50491 | 445.3154 | 27.8 | 65.04
2021-01-29 11:55 | 4.0219 | 1.531 | 0.28203 | 2.6288 | 85.9707 | 82.8761 | 1.2364 | 0.45361 | 445.9344 | 27.79 | 64.61
2021-01-29 12:00 | 3.1016 | 1.6199 | 0.21903 | 2.702 | 86.2917 | 69.8352 | 1.2299 | 0.30015 | 446.1468 | 27.81 | 66.19
2021-01-29 12:05 | 2.602 | 1.756 | 0.22957 | 2.9213 | 78.0846 | 54.6438 | 1.2154 | 0.26357 | 446.6532 | 27.8 | 66.42
2021-01-29 12:10 | 2.9487 | 1.553 | 0.24016 | 2.6207 | 70.0303 | 36.6151 | 1.2156 | 0.27827 | 445.0402 | 27.76 | 67.16
2021-01-29 12:15 | 3.6661 | 1.436 | 0.24223 | 2.4413 | 46.116 | 51.0178 |  |  | 447.3507 | 27.66 | 67.17
2021-01-29 12:20 | 3.4616 | 1.5613 | 0.29073 | 2.684 | 60.0426 | 42.2883 | 1.2303 | 0.32955 | 446.237 | 27.65 | 67.68
2021-01-29 12:25 | 2.4236 | 1.4255 | 0.27814 | 2.4633 | 66.0049 | 62.64 | 1.2232 | 0.27834 | 446.5663 | 27.72 | 67.94
2021-01-29 12:30 | 3.1801 | 1.3045 | 0.28024 | 2.2799 | 89.135 | 98.0393 | 1.2232 | 0.21973 | 446.0444 | 27.73 | 67.8
2021-01-29 12:35 | 3.141 | 1.0995 | 0.22962 | 1.9149 | 91.8963 | 70.2145 | 1.2229 | 0.24898 | 446.2245 | 27.67 | 67.5
2021-01-29 12:40 | 2.7433 | 1.1186 | 0.24224 | 1.9569 | 65.0192 | 24.8283 | 1.2155 | 0.21967 | 445.7979 | 27.63 | 67.43
2021-01-29 12:45 | 3.3589 | 1.3111 | 0.33073 | 2.3404 | 54.5827 | 30.7476 | 1.2229 | 0.21236 | 445.6808 | 27.69 | 67.36
2021-01-29 12:50 | 3.7813 | 1.4579 | 0.28224 | 2.5191 | 44.1146 | 55.3227 | 1.23 | 0.24894 | 445.182 | 27.72 | 66.83
2021-01-29 12:55 | 5.5243 | 1.5307 | 0.29275 | 2.639 | 56.5705 | 34.3914 | 1.2373 | 0.3441 | 445.7658 | 27.75 | 66.5
2021-01-29 13:00 | 4.7182 | 1.9077 | 0.34551 | 3.2718 | 73.2551 | 50.7001 | 1.2377 | 0.43941 | 444.9691 | 27.79 | 67.2
2021-01-29 13:05 | 3.9377 | 1.8741 | 0.30561 | 3.1783 | 61.8639 | 57.8108 | 1.2308 | 0.39563 | 445.3641 | 27.81 | 68.1
2021-01-29 13:10 | 3.7455 | 1.5552 | 0.29508 | 2.6789 | 70.5797 | 66.8752 | 1.2456 | 0.30773 | 444.3804 | 27.75 | 68.49
2021-01-29 13:15 | 5.2217 | 1.6807 | 0.37948 | 2.9557 | 90.5272 | 96.2544 | 1.2532 | 0.38108 | 444.2408 | 27.78 | 68.93
2021-01-29 13:20 | 5.0553 | 1.5611 | 0.33312 | 2.724 | 102.4616 | 97.4628 | 1.2606 | 0.43974 | 443.6837 | 27.78 | 69.13
2021-01-29 13:25 | 4.3618 | 1.3533 | 0.25929 | 2.3336 | 96.9761 | 62.2663 | 1.2897 | 0.56425 | 443.2266 | 27.78 | 68.74
2021-01-29 13:30 | 3.4767 | 1.3808 | 0.21924 | 2.3357 | 71.6889 | 45.7536 | 1.319 | 0.38838 | 443.6988 | 27.81 | 68.66
2021-01-29 13:35 | 3.22 | 1.2322 | 0.23399 | 2.1227 | 59.0729 | 28.6641 | 1.3117 | 0.33707 | 444.3146 | 27.76 | 68.75
2021-01-29 13:40 | 4.4387 | 1.2418 | 0.27193 | 2.1755 | 53.1315 | 46.3476 | 1.297 | 0.32975 | 444.367 | 27.72 | 68.95
2021-01-29 13:45 | 4.7599 | 1.6367 | 0.29304 | 2.8018 | 45.6334 | 51.8123 | 1.2751 | 0.30779 | 445.3286 | 27.75 | 69.07
2021-01-29 13:50 | 4.1454 | 1.9193 | 0.30579 | 3.2477 | 86.0812 | 111.2978 | 1.2536 | 0.32989 | 444.5696 | 27.81 | 69.69
2021-01-29 13:55 | 4.5816 | 1.7348 | 0.30789 | 2.9671 | 119.9999 | 112.4434 | 1.2315 | 0.35187 | 445.0948 | 27.82 | 69.55
2021-01-29 14:00 | 4.3894 | 1.4612 | 0.29314 | 2.5329 | 114.935 | 93.0857 | 1.2243 | 0.4252 | 443.5133 | 27.81 | 69.75
2021-01-29 14:05 | 3.3371 | 1.2397 | 0.24887 | 2.147 | 102.3095 | 36.1122 | 1.239 | 0.33724 | 444.021 | 27.81 | 69.84
2021-01-29 14:10 | 3.0802 | 1.1983 | 0.213 | 2.0477 | 62.0554 | 40.258 | 1.2536 | 0.27857 | 443.0616 | 27.77 | 69.84
2021-01-29 14:15 | 2.9518 | 1.329 | 0.18558 | 2.2227 | 48.594 | 24.9284 | 1.2609 | 0.22725 | 443.7173 | 27.74 | 69.84
2021-01-29 14:20 | 2.7465 | 1.3937 | 0.24042 | 2.3767 | 58.7598 | 45.1556 | 1.2389 | 0.21993 | 442.1244 | 27.75 | 69.86
2021-01-29 14:25 | 2.8743 | 1.1692 | 0.22982 | 2.022 | 49.0371 | 40.1577 | 1.2387 | 0.25653 | 444.9004 | 27.7 | 69.54
2021-01-29 14:30 | 4.9787 | 1.2174 | 0.2235 | 2.0895 | 64.2917 | 59.3541 | 1.2753 | 0.35914 | 444.4337 | 27.66 | 69.72
2021-01-29 14:35 | 3.5419 | 1.245 | 0.26359 | 2.172 | 65.1409 | 67.1634 | 1.3121 | 0.30054 | 443.3076 | 27.68 | 69.94
2021-01-29 14:40 | 4.2995 | 1.1805 | 0.2594 | 2.0689 | 64.6235 | 55.6395 | 1.3122 | 0.27125 | 443.7582 | 27.7 | 70.11
2021-01-29 14:45 | 5.5578 | 1.398 | 0.24044 | 2.3833 | 74.6723 | 67.8951 | 1.2757 | 0.3006 | 444.1937 | 27.73 | 70.24
2021-01-29 14:50 | 5.1862 | 1.5344 | 0.27422 | 2.6262 | 82.7941 | 92.5298 | 1.2612 | 0.3153 | 443.5307 | 27.79 | 70.3
2021-01-29 14:55 | 3.8508 | 1.4256 | 0.23834 | 2.4235 | 98.8685 | 87.0593 | 1.2538 | 0.3666 | 443.5813 | 27.78 | 70.13
2021-01-29 15:00 | 3.9924 | 1.4945 | 0.28056 | 2.5714 | 95.9009 | 68.3877 | 1.3199 | 0.39597 | 442.9517 | 27.82 | 70.25
2021-01-29 15:05 | 3.9163 | 1.7523 | 0.30383 | 2.9898 | 78.6858 | 74.7926 | 1.3495 | 0.33738 | 444.27 | 27.92 | 70.43
2021-01-29 15:10 | 4.404 | 1.7907 | 0.25951 | 3.0022 | 91.2124 | 64.9786 | 1.2908 | 0.30803 | 443.7754 | 27.92 | 70.27
2021-01-29 15:15 | 3.9293 | 1.6285 | 0.28485 | 2.7789 | 77.3127 | 62.5713 | 1.2542 | 0.29339 | 444.2062 | 27.95 | 70.42
2021-01-29 15:20 | 4.3274 | 1.6918 | 0.2954 | 2.8886 | 63.5062 | 66.8243 | 1.2616 | 0.38141 | 443.1623 | 27.95 | 70.42
2021-01-29 15:25 | 5.42 | 2.046 | 0.33134 | 3.4654 | 84.5627 | 71.267 | 1.2692 | 0.44018 | 444.0086 | 28.02 | 70.68
2021-01-29 15:30 | 4.8937 | 2.2747 | 0.29337 | 3.7801 | 93.8155 | 90.0649 | 1.2693 | 0.46955 | 442.3596 | 28.06 | 70.66
2021-01-29 15:35 | [9 empty] | 28.03 | 70.4
2021-01-29 15:40 | 5.5606 | 1.3959 | 0.25533 | 2.3951 | 97.1157 | 74.8324 | 1.269 | 0.38877 | 443.5621 | 28.01 | 70.37
2021-01-29 15:45 | 6.4214 | 1.4525 | 0.28911 | 2.5155 | 78.5564 | 61.4191 | 1.3204 | 0.50617 | 442.9829 | 28.03 | 70.45
2021-01-29 15:50 | 6.4473 | 1.48 | 0.27857 | 2.5472 | 85.001 | 12.1958 | 1.3645 | 0.49885 | 442.9394 | 28.05 | 70.45
2021-01-29 15:55 | 5.3049 | 1.7253 | 0.24906 | 2.8937 | 77.6649 | 11.0568 | 1.3353 | 0.38886 | 441.7499 | 28.11 | 70.54
2021-01-29 16:00 | 5.7802 | 1.7336 | 0.24695 | 2.9022 | 81.3229 | 79.2369 | 1.394 | 0.50625 | 443.2716 | 28.14 | 70.41
2021-01-29 16:05 | 6.1525 | 1.9607 | 0.27227 | 3.2778 | 102.7555 | 84.5062 | 1.4087 | 0.38151 | 443.7904 | 28.15 | 70.3
2021-01-29 16:10 | 7.7452 | 1.812 | 0.26383 | 3.0435 | 92.8708 | 76.3477 | 1.2913 | 0.41086 | 442.2242 | 28.15 | 70.31
2021-01-29 16:15 | 6.1277 | 1.8509 | 0.27442 | 3.1094 | 84.6625 | 66.7598 | 1.2621 | 0.3889 | 443.6515 | 28.2 | 70.47
2021-01-29 16:20 | 4.7653 | 1.7033 | 0.26382 | 2.8725 | 83.4992 | 71.6207 | 1.2546 | 0.38885 | 442.7177 | 28.17 | 70.22
2021-01-29 16:25 | 4.8804 | 1.4869 | 0.23003 | 2.5093 | 68.8914 | 66.8159 | 1.2545 | 0.3668 | 441.7442 | 28.15 | 70.07
2021-01-29 16:30 | 6.0363 | 1.3864 | 0.21526 | 2.3425 | 75.2199 | 61.1438 | 1.2545 | 0.33746 | 442.8056 | 28.14 | 70.09
2021-01-29 16:35 | 4.6865 | 1.2333 | 0.22575 | 2.114 | 87.8649 | 79.9967 | 1.2321 | 0.27869 | 443.0271 | 28.07 | 69.69
2021-01-29 16:40 | 4.2375 | 1.3394 | 0.22999 | 2.283 | 83.4754 | 72.1036 | 1.2249 | 0.33006 | 443.6201 | 28.05 | 69.91
2021-01-29 16:45 | 5.2906 | 1.4495 | 0.20468 | 2.4266 | 83.7557 | 60.1792 | 1.2323 | 0.41076 | 444.1407 | 28.04 | 70.04
2021-01-29 16:50 | 4.7895 | 1.3366 | 0.25319 | 2.302 | 61.7989 | 34.8338 | 1.2395 | 0.53542 | 443.6881 | 28.01 | 70.02
2021-01-29 16:55 | 3.9545 | 1.331 | 0.2595 | 2.2996 | 64.0838 | 68.6957 | 1.2394 | 0.68938 | 442.2376 | 27.96 | 69.99
2021-01-29 17:00 | 3.7748 | 1.3998 | 0.20676 | 2.3524 | 66.8984 | 60.8485 | 1.3861 | 0.83606 | 442.2656 | 27.94 | 70.08
2021-01-29 17:05 | 5.1614 | 1.4713 | 0.18144 | 2.4368 | 55.0962 | 45.8622 | 1.4154 | 0.5207 | 443.2955 | 27.95 | 70.03
2021-01-29 17:10 | 5.0329 | 1.4107 | 0.20464 | 2.3671 | 53.0608 | 38.8969 | 1.3787 | 0.53535 | 443.3093 | 27.95 | 69.95
2021-01-29 17:15 | 4.5059 | 1.2991 | 0.21727 | 2.2086 | 54.02 | 36.4789 | 1.2759 | 0.41063 | 442.8688 | 27.93 | 69.73
2021-01-29 17:20 | 4.5951 | 1.0677 | 0.17717 | 1.8138 | 43.2503 | 48.9801 | 1.2757 | 0.38858 | 443.5332 | 27.88 | 69.53
2021-01-29 17:25 | 5.0438 | 1.0277 | 0.17504 | 1.7504 | 53.4511 | 45.9765 | 1.2682 | 0.40319 | 444.686 | 27.84 | 69.4
2021-01-29 17:30 | 4.9153 | 1.2272 | 0.15816 | 2.0392 | 56.406 | 53.7572 | 1.2609 | 0.43983 | 443.18 | 27.81 | 69.43
2021-01-29 17:35 | 4.4399 | 1.2793 | 0.18766 | 2.1486 | 54.2236 | 43.3625 | 1.268 | 0.45444 | 444.3311 | 27.77 | 69.31
2021-01-29 17:40 | 4.0033 | 1.1458 | 0.21506 | 1.9714 | 50.3084 | 35.2601 | 1.2679 | 0.41043 | 444.4691 | 27.7 | 69.39
2021-01-29 17:45 | 4.3624 | 0.88716 | 0.20872 | 1.5686 | 37.4858 | 33.6469 | 1.2532 | 0.28582 | 442.4446 | 27.67 | 69.39
2021-01-29 17:50 | 3.4512 | 0.82796 | 0.19395 | 1.4631 | 46.536 | 39.3308 | 1.2605 | 0.24184 | 444.6372 | 27.62 | 69.42
2021-01-29 17:55 | 4.093 | 0.86103 | 0.18553 | 1.5054 | 51.6821 | 61.3411 | 1.2459 | 0.24918 | 445.6184 | 27.64 | 69.54
2021-01-29 18:00 | 3.1685 | 0.81685 | 0.17917 | 1.4313 | 51.0662 | 43.9337 | 1.2457 | 0.23448 | 445.2453 | 27.6 | 69.17
2021-01-29 18:05 | 2.9371 | 0.72322 | 0.15385 | 1.2603 | 56.1675 | 43.8545 | 1.2381 | 0.21246 | 445.4236 | 27.53 | 69.01
2021-01-29 18:10 | 2.5394 | 0.74105 | 0.15384 | 1.2897 | 49.3819 | 42.4563 | 1.238 | 0.21977 | 445.5564 | 27.46 | 69.12
2021-01-29 18:15 | 2.2701 | 0.8483 | 0.15384 | 1.4541 | 46.8998 | 30.1345 | 1.2381 | 0.18315 | 444.5764 | 27.41 | 69.37
2021-01-29 18:20 | 2.2186 | 0.7616 | 0.13908 | 1.3065 | 48.4234 | 29.6286 | 1.2379 | 0.18313 | 445.2356 | 27.35 | 69.33
2021-01-29 18:25 | 2.4363 | 0.73677 | 0.14538 | 1.2747 | 30.7638 | 39.5447 | 1.2378 | 0.16113 | 446.3596 | 27.28 | 69.38
2021-01-29 18:30 | 2.2823 | 0.70648 | 0.14959 | 1.2304 | 32.6286 | 30.6284 | 1.2377 | 0.1538 | 444.398 | 27.21 | 69.48
2021-01-29 18:35 | 1.7948 | 0.60195 | 0.12008 | 1.0407 | 28.3787 | 23.743 | 1.2376 | 0.13913 | 445.6018 | 27.14 | 69.45
2021-01-29 18:40 | 1.9357 | 0.56619 | 0.12007 | 0.98794 | 28.6949 | 10.9119 | 1.2375 | 0.14645 | 446.7667 | 27.08 | 69.53
2021-01-29 18:45 | 2.0509 | 0.56887 | 0.11374 | 0.98573 | 34.9881 | 34.9574 | 1.2374 | 0.04393 | 447.4723 | 26.99 | 69.61
2021-01-29 18:50 | 1.3074 | 0.59909 | 0.1369 | 1.0552 | 30.4753 | 26.3634 | 1.208 | 0.087858 | 447.0494 | 26.93 | 69.78
2021-01-29 18:55 | 1.179 | 0.51793 | 0.14951 | 0.94341 | 21.3352 | 18.1057 | 1.1932 | 0.095163 | 446.7213 | 26.85 | 69.63
2021-01-29 19:00 | 1.5634 | 0.49866 | 0.13898 | 0.90334 | 32.4158 | 11.0513 | 1.1931 | 0.080517 | 447.411 | 26.76 | 69.81
2021-01-29 19:05 | 1.2046 | 0.45748 | 0.11793 | 0.81916 | 39.8505 | 136.2114 | 1.1859 | 0.065881 | 391.2391 | 26.73 | 70.09
2021-01-29 19:10 | 1.6404 | 0.441 | 0.12003 | 0.79391 | 222.1298 | 247.4124 | 1.1859 | 0.080523 | 284.121 | 26.71 | 70.23
2021-01-29 19:15 | 1.7946 | 0.48095 | 0.14323 | 0.88045 | 160.8769 | 55.4681 | 1.1861 | 0.087863 | 285.0594 | 26.76 | 70.65
2021-01-29 19:20 | 1.3589 | 0.46727 | 0.14746 | 0.86582 | 72.4804 | 21.1688 | 1.1863 | 0.087875 | 283.9137 | 26.82 | 70.78
2021-01-29 19:25 | 1.7051 | 0.43429 | 0.1264 | 0.78998 | 43.5375 | 19.6919 | 1.1936 | 0.095198 | 283.8944 | 26.84 | 70.7
2021-01-29 19:30 | 1.6668 | 0.3986 | 0.1243 | 0.73529 | 35.9107 | 15.4064 | 1.1938 | 0.10986 | 284.3518 | 26.88 | 70.82
2021-01-29 19:35 | 1.5001 | 0.42196 | 0.10956 | 0.75636 | 23.2122 | 21.089 | 1.1938 | 0.087884 | 284.3228 | 26.91 | 70.7
2021-01-29 19:40 | 1.7822 | 0.51679 | 0.11587 | 0.90803 | 12.1238 | -0.020514 | 1.1864 | 0.10985 | 284.8643 | 26.9 | 70.67
2021-01-29 19:45 | 2.3976 | 0.58552 | 0.10534 | 1.0028 | 18.6988 | 6.862 | 1.1791 | 0.16112 | 283.811 | 26.9 | 70.71
2021-01-29 19:50 | 2.4103 | 0.54014 | 0.10323 | 0.93117 | 17.1594 | 17.621 | 1.1937 | 0.16844 | 284.3587 | 26.89 | 70.62
2021-01-29 19:55 | 3.3203 | 0.55657 | 0.08426 | 0.9374 | 9.9377 | 12.4503 | 1.2155 | 0.15377 | 285.4746 | 26.85 | 70.51
2021-01-29 20:00 | 1.9612 | 0.40673 | 0.080038 | 0.70349 | 12.6848 | 18.0581 | 1.2227 | 0.10983 | 284.4955 | 26.81 | 70.36
2021-01-29 20:05 | 3.2557 | 0.4974 | 0.07161 | 0.83405 | 25.9018 | 7.1573 | 1.23 | 0.14643 | 284.0289 | 26.76 | 70.46
2021-01-29 20:10 | 3.6406 | 0.47822 | 0.10743 | 0.84046 | 23.5253 | 19.9052 | 1.2374 | 0.15377 | 285.0491 | 26.76 | 70.75
2021-01-29 20:15 | 2.8199 | 0.43695 | 0.07793 | 0.74981 | 16.376 | 16.0581 | 1.23 | 0.13911 | 285.1135 | 26.72 | 70.66
2021-01-29 20:20 | 1.9099 | 0.38888 | 0.092678 | 0.68877 | 20.2019 | 11.1264 | 1.2301 | 0.12447 | 284.5537 | 26.74 | 70.73
2021-01-29 20:25 | 1.2815 | 0.25552 | 0.054749 | 0.44641 | 21.2212 | 14.2193 | 1.2224 | 0.095157 | 285.7719 | 26.65 | 70.3
2021-01-29 20:30 | 1.5364 | 0.28686 | 0.063115 | 0.50071 | 12.7418 | 12.6599 | 1.2286 | 0.10239 | 285.8929 | 26.24 | 69.46
2021-01-29 20:35 | 2.0338 | 0.38806 | 0.052546 | 0.64737 | 12.2182 | 16.3011 | 1.2275 | 0.12421 | 286.6122 | 25.22 | 70.92
2021-01-29 20:40 | 1.675 | 0.40298 | 0.06093 | 0.67863 | 24.038 | 9.8607 | 1.2343 | 0.11686 | 287.8629 | 24.59 | 72.38
2021-01-29 20:45 | 1.4826 | 0.40692 | 0.069304 | 0.69304 | 17.5964 | 14.2121 | 1.2338 | 0.1095 | 286.9932 | 23.97 | 73.71
2021-01-29 20:50 | 1.5724 | 0.37685 | 0.07562 | 0.65328 | 17.5183 | 31.6414 | 1.2413 | 0.10223 | 288.2565 | 23.7 | 75.63
2021-01-29 20:55 | 1.4455 | 0.40592 | 0.079877 | 0.70208 | 26.168 | 10.4999 | 1.2349 | 0.058456 | 286.3254 | 23.84 | 77.31
2021-01-29 21:00 | 1.0496 | 0.35538 | 0.098851 | 0.64359 | 22.5784 | 14.0385 | 1.221 | 0.021933 | 286.8203 | 24.26 | 77.2
2021-01-29 21:05 | 0.98605 | 0.39124 | 0.0989 | 0.69861 | 13.4205 | 14.1581 | 1.1923 | 0.073147 | 286.7957 | 24.69 | 76.77
2021-01-29 21:10 | 0.99954 | 0.34893 | 0.075805 | 0.61065 | 14.8445 | 5.864 | 1.2004 | 0.1098 | 285.7041 | 25.07 | 77.17
2021-01-29 21:15 | 0.821 | 0.33692 | 0.084317 | 0.60076 | 24.3119 | 16.5124 | 1.2164 | 0.080602 | 285.0596 | 25.43 | 78.69
2021-01-29 21:20 | 0.96265 | 0.34674 | 0.10967 | 0.64117 | 20.8856 | 10.5147 | 1.2244 | 0.029326 | 284.5956 | 25.75 | 78.85
2021-01-29 21:25 | 0.71892 | 0.35094 | 0.10759 | 0.64552 | 12.4168 | 20.6331 | 1.2099 | 0.021999 | 285.3601 | 25.99 | 78.33
2021-01-29 21:30 | 0.98864 | 0.34547 | 0.11604 | 0.64559 | 19.4338 | 1.3353 | 1.1881 | 0.036669 | 283.8105 | 26.18 | 77.72
2021-01-29 21:35 | 0.88578 | 0.28349 | 0.088597 | 0.52314 | 16.3806 | 1.787 | 1.1806 | 0.051329 | 283.7979 | 26.24 | 77
2021-01-29 21:40 | 1.5276 | 0.35779 | 0.088593 | 0.63491 | 4.3029 | -5.1964 | 1.1805 | 0.080657 | 283.2393 | 26.29 | 76.64
2021-01-29 21:45 | 1.2578 | 0.30406 | 0.067485 | 0.53145 | 6.6738 | 9.7026 | 1.1803 | 0.073309 | 284.891 | 26.27 | 76.14
2021-01-29 21:50 | 1.6684 | 0.28616 | 0.069592 | 0.51034 | 12.3103 | 1.8789 | 1.1802 | 0.15394 | 283.8297 | 26.29 | 75.98
2021-01-29 21:55 | 1.4115 | 0.31362 | 0.071688 | 0.55242 | 3.1104 | -2.3405 | 1.1874 | 0.13926 | 283.9203 | 26.25 | 75.63
2021-01-29 22:00 | 1.6551 | 0.35072 | 0.065355 | 0.60296 | 5.7273 | 12.6351 | 1.1872 | 0.19787 | 283.9611 | 26.24 | 75.36
2021-01-29 22:05 | 1.3855 | 0.29017 | 0.063239 | 0.50802 | 15.2094 | 6.1987 | 1.1944 | 0.20517 | 283.472 | 26.24 | 75
2021-01-29 22:10 | 1.3339 | 0.27087 | 0.065336 | 0.48054 | 11.5334 | 6.7825 | 1.1942 | 0.19781 | 284.6084 | 26.2 | 74.69
2021-01-29 22:15 | 1.4493 | 0.27224 | 0.061119 | 0.47842 | 3.7452 | 2.873 | 1.1942 | 0.17583 | 283.04 | 26.2 | 74.62
2021-01-29 22:20 | 1.1929 | 0.28877 | 0.071664 | 0.5164 | 13.4019 | 4.6999 | 1.1796 | 0.11723 | 284.006 | 26.26 | 74.63
2021-01-29 22:25 | 0.83368 | 0.23649 | 0.061119 | 0.42362 | 13.3183 | 6.8849 | 1.1722 | 0.087913 | 282.9672 | 26.28 | 74.24
2021-01-29 22:30 | 2.052 | 0.2736 | 0.056901 | 0.47628 | 3.6321 | -3.0678 | 1.1721 | 0.13186 | 284.0223 | 26.29 | 74.05
2021-01-29 22:35 | 1.6797 | 0.25292 | 0.04846 | 0.43825 | 1.2822 | 17.0691 | 1.1792 | 0.14648 | 284.1323 | 26.24 | 73.64
2021-01-29 22:40 | 1.372 | 0.28317 | 0.05689 | 0.49094 | 13.4382 | -14.5973 | 1.1792 | 0.16846 | 283.6001 | 26.24 | 73.71
2021-01-29 22:45 | 1.295 | 0.25977 | 0.056884 | 0.45507 | 8.339 | 8.0005 | 1.2157 | 0.13182 | 284.1826 | 26.21 | 73.55
2021-01-29 22:50 | 1.5642 | 0.29825 | 0.075844 | 0.53302 | 0.71799 | 12.093 | 1.223 | 0.087882 | 284.711 | 26.21 | 73.52
2021-01-29 22:55 | 1.1024 | 0.19788 | 0.065299 | 0.36862 | 9.1374 | -2.5228 | 1.2228 | 0.058578 | 284.2824 | 26.16 | 73.24
2021-01-29 23:00 | 0.5767 | 0.17173 | 0.054753 | 0.31799 | 15.348 | 2.1223 | 1.2225 | 0.043922 | 284.4615 | 26.05 | 72.96
2021-01-29 23:05 | 0.83295 | 0.22392 | 0.065276 | 0.4085 | 1.2404 | 12.1585 | 1.2224 | 0.036598 | 285.1163 | 25.94 | 73.19
2021-01-29 23:10 | 0.52544 | 0.24042 | 0.067387 | 0.43591 | 1.8967 | -1.9582 | 1.2225 | 0.029281 | 284.0801 | 25.9 | 73.59
2021-01-29 23:15 | 0.52551 | 0.24183 | 0.061078 | 0.43176 | 10.6435 | 1.8457 | 1.2226 | 0.036606 | 284.5671 | 25.9 | 73.99
2021-01-29 23:20 | 0.57686 | 0.26934 | 0.054767 | 0.46763 | 5.0764 | 1.5178 | 1.2228 | 0.043934 | 283.4279 | 25.95 | 74.18
2021-01-29 23:25 | 0.53829 | 0.17449 | 0.054756 | 0.32222 | 0.1538 | -1.456 | 1.2226 | 0.10981 | 285.1009 | 25.91 | 73.77
2021-01-29 23:30 | 0.69212 | 0.23358 | 0.092668 | 0.45281 | 11.9864 | 0.59471 | 1.2299 | 0.051247 | 285.1099 | 25.89 | 73.96
2021-01-29 23:35 | 0.53841 | 0.2185 | 0.096897 | 0.43183 | 8.8402 | -5.6097 | 1.2155 | -0.0073224 | 284.2004 | 25.94 | 74.19
2021-01-29 23:40 | 0.61531 | 0.20475 | 0.067405 | 0.38126 | -8.1733 | -3.2406 | 1.1935 | 0.065899 | 284.1993 | 25.95 | 74.06
2021-01-29 23:45 | 1.3203 | 0.17451 | 0.046339 | 0.31384 | 0.55376 | -5.1274 | 1.2008 | 0.043931 | 284.2199 | 25.94 | 73.99
2021-01-29 23:50 |  | 0.24325 | 0.063197 | 0.43606 | 29.7113 | 44.8182 | 1.1863 | 0.043936 | 283.6534 | 25.95 | 74.27
2021-01-29 23:55 | 1.282 | 0.21851 | 0.056877 | 0.39182 | 45.3824 | 64.0173 | 1.179 | 0.073227 | 283.1085 | 25.97 | 74.19
2021-01-30 | 2.115 | 0.20199 | 0.056869 | 0.36649 | 43.9098 | 42.3203 |  |  | 282.6595 | 25.93 | 73.97
2021-01-30 00:05
2021-01-30 00:10
2021-01-30 00:15 | 4.5754 | 0.15388 | 0.05265 | 0.28852 | 8.2845 | 4.1423 | 1.1713 | 0.043924 | 284.3884 | 25.81 | 74.1
2021-01-30 00:20 | 1.2688 | 0.13876 | 0.058966 | 0.27167 | 14.559 | 5.6596 | 1.1713 | 0.029282 | 283.9081 | 25.77 | 74.2
2021-01-30 00:25 | 1.9612 | 0.15802 | 0.052656 | 0.29488 | 17.1762 | -1.9381 | 1.1715 | 0.036608 | 284.3614 | 25.8 | 74.52
2021-01-30 00:30 | 1.192 | 0.1058 | 0.052652 | 0.21693 | 1.8046 | 7.2698 | 1.1714 | 0.036605 | 283.8788 | 25.78 | 74.36
2021-01-30 00:35 | 1.4739 | 0.11266 | 0.046333 | 0.21903 | -0.37937 | -13.155 | 1.1713 | 0.029283 | 284.1546 | 25.75 | 74.35
2021-01-30 00:40 | 0.98683 | 0.090676 | 0.04633 | 0.18532 | 6.1517 | 5.0034 | 1.164 | 0.021962 | 284.2157 | 25.7 | 74.43
2021-01-30 00:45 | 0.80756 | 0.13329 | 0.037914 | 0.24223 | 2.6252 | 6.1118 | 1.1568 | 0.014644 | 284.1267 | 25.74 | 74.78
2021-01-30 00:50 | 0.51276 | 0.13467 | 0.040022 | 0.24435 | 2.5843 | -7.7427 | 1.1569 | 0.021967 | 285.1416 | 25.76 | 74.86
2021-01-30 00:55 | 0.67947 | 0.17042 | 0.056878 | 0.3181 | 3.3435 | -5.1588 | 1.157 | 0.029291 | 283.5053 | 25.8 | 74.92
2021-01-30 01:00 | 0.66661 | 0.15804 | 0.04213 | 0.28438 | -3.2613 | -3.2203 | 1.157 | 0.05858 | 284.0439 | 25.8 | 74.78
2021-01-30 01:05 |  |  |  |  | -7.619 |  |  |  | 284.6398 | 25.76 | 74.62
2021-01-30 01:10 |  |  |  |  | 1.5176 | 11.4843 |  |  | 284.1688 | 25.72 | 74.63
2021-01-30 01:15 |  |  |  |  | 24.7832 | 32.0223 |  |  | 284.7268 | 25.69 | 74.72
2021-01-30 01:20 |  |  |  |  | 15.2782 | 3.9887 |  |  | 284.7428 | 25.67 | 74.84
2021-01-30 01:25 |  |  |  |  | 16.7455 | 13.5359 |  |  | 283.1584 | 25.66 | 75.07
2021-01-30 01:30 |  |  |  |  | 27.8733 | 20.0282 |  |  | 284.6881 | 25.69 | 75.12
2021-01-30 01:35 |  |  |  |  | 18.9699 | 13.5968 |  |  | 283.7251 | 25.63 | 75.07
2021-01-30 01:40 |  |  |  |  | 16.0174 | 18.0171 |  |  | 284.247 | 25.62 | 75.25
2021-01-30 01:45 |  |  |  |  | 19.6375 | 4.7684 |  |  | 282.6679 | 25.62 | 75.28
2021-01-30 01:50 |  |  |  |  | 14.5928 | 4.8198 |  |  | 283.1818 | 25.62 | 75.4
2021-01-30 01:55 |  |  |  |  | 5.9583 | 8.2658 |  |  | 283.1623 | 25.63 | 75.46
2021-01-30 02:00 |  |  |  |  | 13.0652 | 7.2197 |  |  | 283.1642 | 25.63 | 75.44
2021-01-30 02:05 |  |  |  |  | 14.1421 | 8.1222 |  |  | 283.6867 | 25.63 | 75.47
2021-01-30 02:10 | 0.56414 | 0.085216 | 0.16644 | 0.29495 | 4.5849 | 4.6977 | 1.245 | -0.014647 | 284.1079 | 25.69 | 75.69
2021-01-30 02:15 | 0.37183 | 0.10858 | 0.13905 | 0.30339 | 6.3801 | 7.8674 | 1.2304 | 0 | 282.486 | 25.73 | 75.6
2021-01-30 02:20 | 0.26921 | 0.076959 | 0.099006 | 0.21697 | 12.3889 | -4.1023 | 1.2302 | 0.0073226 | 283.105 | 25.68 | 75.34
2021-01-30 02:25 | 0.282 | 0.065958 | 0.10742 | 0.20853 | -0.53324 | -10.7469 | 1.2228 | 0.021966 | 284.7557 | 25.63 | 75.28
2021-01-30 02:30 | 0.064087 | 0.056335 | 0.14532 | 0.23168 | 0.20508 | 10.1001 | 1.2227 | 0.014643 | 283.7847 | 25.57 | 75.31
2021-01-30 02:35 | 0.42296 | 0.060455 | 0.21272 | 0.30538 | 5.1576 | -9.2385 | 1.2226 | 0.021963 | 284.3459 | 25.54 | 75.37
2021-01-30 02:40 | 0.61528 | 0.11955 | 0.10953 | 0.29278 | 1.6407 | 8.901 | 1.2227 | 0.029287 | 284.8147 | 25.57 | 75.53
2021-01-30 02:45 | 0.35895 | 0.14292 | 0.10322 | 0.3223 | 2.4614 | -5.4765 | 1.2155 | 0.051258 | 283.687 | 25.62 | 75.61
2021-01-30 02:50 | 0.62826 | 0.16219 | 0.12009 | 0.3687 | 6.78 | 7.8468 | 1.2231 | 0.058589 | 284.6092 | 25.71 | 75.65
2021-01-30 02:55 | 0.14103 | 0.15393 | 0.14958 | 0.38553 | 9.4875 | -5.672 | 1.223 | 0.036617 | 284.0687 | 25.74 | 75.38
2021-01-30 03:00 | [9 empty] | 25.68 | 75.25
2021-01-30 03:05 | 0.30767 | 0.1443 | 0.17484 | 0.39602 | 4.7791 | 0.30767 | 1.2229 | 0.036613 | 283.367 | 25.66 | 75.33
2021-01-30 03:10 | 0.08974 | 0.24325 | 0.14957 | 0.52243 | 10.4201 | 18.5531 | 1.2302 | 0.043937 | 283.8902 | 25.65 | 75.49
2021-01-30 03:15 | 0.35903 | 0.28041 | 0.24019 | 0.67002 | 4.5443 | 10.0733 | 1.2378 | 0.051269 | 284.2957 | 25.72 | 75.72
2021-01-30 03:20 | 0.29491 | 0.17182 | 0.15802 | 0.42139 | 9.8373 | -5.5803 | 1.2305 | 0.043945 | 283.2188 | 25.75 | 75.58
2021-01-30 03:25 | 0.19232 | 0.11683 | 0.10745 | 0.28653 | 13.6522 | 12.1957 | 1.2304 | 0.029294 | 283.7845 | 25.73 | 75.44
2021-01-30 03:30 | 0.30768 | 0.09895 | 0.10112 | 0.25279 | 6.81 | 0.020512 | 1.2229 | 0.029291 | 283.8603 | 25.68 | 75.37
2021-01-30 03:35 | 0.2692 | 0.10306 | 0.099 | 0.25698 | 3.4765 | -2.6458 | 1.2228 | 0.021966 | 283.9351 | 25.63 | 75.31
2021-01-30 03:40 | 0.38458 | 0.14154 | 0.096896 | 0.31386 | 13.937 | 4.0303 | 1.2228 | 0.021967 | 283.9373 | 25.62 | 75.43
2021-01-30 03:45 | 0.16665 | 0.097568 | 0.094789 | 0.24435 | 7.2402 | 10.8911 | 1.2228 | 0.021967 | 284.4651 | 25.62 | 75.4
2021-01-30 03:50 | 0.26921 | 0.10032 | 0.063195 | 0.21697 | 8.8301 | 11.3735 | 1.2302 | 0.02929 | 283.9197 | 25.63 | 75.47
2021-01-30 03:55 | 0.26924 | 0.15393 | 0.046348 | 0.2823 | 19.9184 | 16.0516 | 1.2303 | 0.036616 | 283.8349 | 25.69 | 75.49
2021-01-30 04:00 | 0.57695 | 0.14844 | 0.063203 | 0.29073 | 19.8265 | 18.4931 | 1.2303 | 0.036617 | 282.7321 | 25.74 | 75.33
2021-01-30 04:05 | 0.8334 | 0.21304 | 0.065312 | 0.39187 | 16.0013 | 14.1345 | 1.2377 | 0.043942 | 282.6928 | 25.77 | 75.31
2021-01-30 04:10 | 0.28208 | 0.19518 | 0.063206 | 0.36238 | 25.1613 | 13.7551 | 1.2377 | 0.029295 | 282.6523 | 25.81 | 75.16
2021-01-30 04:15 | 0.53854 | 0.2213 | 0.073744 | 0.41296 | 18.7 | 16.1664 | 1.2597 | 0.051269 | 282.6199 | 25.83 | 75.21
2021-01-30 04:20 | 0.88488 | 0.2942 | 0.10747 | 0.55843 | 11.4906 | 9.0694 | 1.2453 | 0.051277 | 282.4999 | 25.91 | 75.31
2021-01-30 04:25 | 0.75667 | 0.3767 | 0.099047 | 0.67647 | 21.833 | 23.0847 | 1.2453 | 0.073255 | 282.9747 | 25.95 | 75.25
2021-01-30 04:30 | 0.89773 | 0.28046 | 0.082187 | 0.51209 | 26.7163 | 20.7349 | 1.2307 | 0.087905 | 282.4358 | 25.97 | 75.12
2021-01-30 04:35 | 1.167 | 0.38082 | 0.07165 | 0.65539 | 12.4451 | 5.0273 | 1.2307 | 0.11721 | 282.9687 | 25.96 | 75.17
2021-01-30 04:40 | 1.3339 | 0.45512 | 0.077983 | 0.77772 | 18.2443 | 20.8917 | 1.2528 | 0.12455 | 282.3403 | 26.03 | 75.25
2021-01-30 04:45 | 1.27 | 0.46755 | 0.1075 | 0.82418 | -8.0764 |  | 1.2456 | 0.11724 | 347.7222 | 26.08 | 75.34
2021-01-30 04:50 | 1.4111 | 0.46757 | 0.14334 | 0.86005 |  |  | 1.2457 | 0.11724 | 466.4682 | 26.15 | 75.15
2021-01-30 04:55 | 1.1161 | 0.51432 | 0.12226 | 0.91063 |  | 21.767 | 1.2383 | 0.095258 | 465.4245 | 26.15 | 75.13
2021-01-30 05:00 | 1.2445 | 0.48687 | 0.12649 | 0.8749 |  | 56.533 | 1.2312 | 0.08794 | 464.8782 | 26.13 | 75.55
2021-01-30 05:05 | 2.2586 | 0.52139 | 0.14761 | 0.94681 | 16.6624 | 45.1516 | 1.2168 | 0.095293 | 463.6672 | 26.16 | 76.14
2021-01-30 05:10 | 2.49 | 0.61229 | 0.15185 | 1.0904 | 39.8405 | 23.8427 | 1.2024 | 0.14663 | 465.1575 | 26.16 | 76.63
2021-01-30 05:15 | 2.3621 | 0.60689 | 0.18985 | 1.1201 | 45.1877 | 36.9102 | 1.1952 | 0.15399 | 464.507 | 26.19 | 76.99
2021-01-30 05:20 | 1.6178 | 0.57536 | 0.14769 | 1.0296 | 55.9723 | 57.924 | 1.1955 | 0.11735 | 464.3813 | 26.21 | 77.48
2021-01-30 05:25 | 1.7595 | 0.63743 | 0.13084 | 1.1079 | 43.4187 | 44.5694 | 1.1957 | 0.19807 | 463.7308 | 26.23 | 77.98
2021-01-30 05:30 | 1.9911 | 0.84688 | 0.23008 | 1.5303 | 56.8082 | 42.9658 | 1.2033 | 0.33752 | 463.0592 | 26.26 | 78.47
2021-01-30 05:35 | 2.5825 | 1.0674 | 0.21323 | 1.8494 | 63.089 | 63.459 | 1.2182 | 0.27887 | 461.3408 | 26.3 | 78.83
2021-01-30 05:40 | 2.2489 | 1.3321 | 0.23228 | 2.2742 | 58.794 | 57.2417 | 1.2332 | 0.20553 | 461.1719 | 26.35 | 79.16
2021-01-30 05:45 | 3.0976 | 1.4495 | 0.25766 | 2.4816 | 67.9974 | 55.2267 | 1.2407 | 0.19088 | 462.5754 | 26.4 | 79.45
2021-01-30 05:50 | 2.8538 | 1.5462 | 0.30418 | 2.6742 | 65.941 | 69.6227 | 1.2483 | 0.22028 | 463.454 | 26.46 | 79.61
2021-01-30 05:55 | 2.1727 | 1.1646 | 0.25351 | 2.0386 | 83.5662 | 56.0845 | 1.2557 | 0.18359 | 464.403 | 26.49 | 79.76
2021-01-30 06:00 | 1.8515 | 1.2708 | 0.26198 | 2.212 | 69.2958 | 54.1036 | 1.2558 | 0.17626 | 463.8615 | 26.48 | 80.02
2021-01-30 06:05 | 2.7645 | 1.4873 | 0.3127 | 2.5925 | 82.5592 | 55.0017 | 1.2559 | 0.22768 | 463.8182 | 26.49 | 80.14
2021-01-30 06:10 | 2.2502 | 1.0462 | 0.21763 | 1.8192 | 64.1574 | 62.9951 | 1.2486 | 0.22034 | 464.8718 | 26.48 | 80.22
2021-01-30 06:15 | 1.9287 | 0.84356 | 0.16057 | 1.4536 | 72.5287 | 39.0879 | 1.2486 | 0.19095 | 463.9034 | 26.44 | 80.33
2021-01-30 06:20 | 1.6587 | 0.72639 | 0.15001 | 1.2635 | 60.2466 | 50.8244 | 1.2559 | 0.16892 | 463.9518 | 26.41 | 80.46
2021-01-30 06:25 | 1.4273 | 0.60514 | 0.15847 | 1.0882 | 59.2733 | 60.1066 | 1.256 | 0.11017 | 463.9054 | 26.42 | 80.6
2021-01-30 06:30 | 1.7359 | 0.59688 | 0.16904 | 1.084 | 70.2093 | 59.6239 | 1.2413 | 0.10283 | 464.3647 | 26.42 | 80.72
2021-01-30 06:35 | 1.9034 | 0.72103 | 0.17329 | 1.2806 | 57.9854 | 56.2467 | 1.2121 | 0.14692 | 462.7339 | 26.46 | 80.81
2021-01-30 06:40 | 1.6077 | 0.76659 | 0.1268 | 1.3019 | 72.7138 | 59.5333 | 1.2122 | 0.16162 | 463.6073 | 26.51 | 80.87
2021-01-30 06:45 | 1.2734 | 0.98177 | 0.15641 | 1.6613 | 84.8535 | 90.8425 | 1.2049 | 0.16164 | 464.0041 | 26.56 | 80.92
2021-01-30 06:50 | 1.3379 | 0.9612 | 0.1522 | 1.6256 | 104.3239 | 64.8667 | 1.2051 | 0.16166 | 463.8602 | 26.62 | 80.94
2021-01-30 06:55 | 1.5695 | 0.76541 | 0.18391 | 1.3572 | 71.1064 | 58.1901 | 1.2051 | 0.16166 | 463.7932 | 26.65 | 80.92
2021-01-30 07:00 | 1.5181 | 0.63027 | 0.14798 | 1.1141 | 76.9338 | 48.157 | 1.2052 | 0.14697 | 464.3015 | 26.65 | 81
2021-01-30 07:05 | 1.6597 | 0.64549 | 0.15222 | 1.1395 | 61.3249 | 57.4342 | 1.2126 | 0.15433 | 463.7011 | 26.68 | 81.05
2021-01-30 07:10 | 1.8141 | 0.60409 | 0.1501 | 1.0761 | 64.9259 | 44.4333 | 1.2199 | 0.15433 | 463.743 | 26.66 | 81.08
2021-01-30 07:15 | 2.0844 | 0.68413 | 0.15857 | 1.2093 | 57.8582 | 42.0993 | 1.2273 | 0.16904 | 463.7314 | 26.65 | 81.29
2021-01-30 07:20 | 2.3548 | 0.73524 | 0.13533 | 1.2644 | 53.4587 | 55.3014 | 1.2348 | 0.24256 | 463.1428 | 26.66 | 81.55
2021-01-30 07:25 | 2.3807 | 0.74081 | 0.1163 | 1.2518 | 49.0561 | 30.9882 | 1.257 | 0.22787 | 463.6477 | 26.65 | 81.79
2021-01-30 07:30 | 2.4451 | 0.87327 | 0.17975 | 1.5162 | 42.1491 | 30.2889 | 1.257 | 0.24258 | 462.5778 | 26.66 | 81.81
2021-01-30 07:35 | 2.7544 | 1.0942 | 0.19035 | 1.8675 | 42.402 | 37.233 | 1.2425 | 0.20585 | 462.9432 | 26.72 | 81.9
2021-01-30 07:40 | 3.3726 | 1.0212 | 0.18191 | 1.7472 | 41.3363 | 56.1449 | 1.2426 | 0.22794 | 462.839 | 26.75 | 82.1
2021-01-30 07:45 | 2.8065 | 0.76457 | 0.15866 | 1.3306 | 61.5481 | 40.6201 | 1.2428 | 0.22061 | 463.276 | 26.77 | 82.32
2021-01-30 07:50 | 2.6135 | 0.66384 | 0.16078 | 1.1783 | 58.192 | 44.813 | 1.2428 | 0.1912 | 463.6989 | 26.79 | 82.37
2021-01-30 07:55 | 2.8326 | 0.6639 | 0.15233 | 1.17 | 51.4815 | 30.2729 | 1.2429 | 0.18386 | 463.1032 | 26.81 | 82.53
2021-01-30 08:00 | 3.5025 | 0.88483 | 0.19678 | 1.5531 | 52.1151 | 37.8167 | 1.2357 | 0.27214 | 463.547 | 26.83 | 82.71
2021-01-30 08:05 | 3.1937 | 0.91389 | 0.18198 | 1.5807 | 54.7873 | 42.9604 | 1.2505 | 0.32366 | 464.0024 | 26.85 | 82.82
2021-01-30 08:10 | 3.0137 | 0.84632 | 0.17142 | 1.4687 | 47.5182 | 43.3455 | 1.28 | 0.26483 | 462.887 | 26.87 | 82.97
2021-01-30 08:15 | 2.1896 | 0.87262 | 0.19048 | 1.5281 | 47.9955 | 36.6406 | 1.2801 | 0.22071 | 462.3184 | 26.88 | 83.11
2021-01-30 08:20 | 2.1511 | 0.87267 | 0.18202 | 1.5197 | 47.4008 | 15.9823 | 1.2728 | 0.19865 | 461.7533 | 26.89 | 83.23
2021-01-30 08:25 | 1.9966 | 0.92796 | 0.2032 | 1.6256 | 41.9523 | 42.921 | 1.2803 | 0.21338 | 461.1882 | 26.9 | 83.35
2021-01-30 08:30 | 2.2158 | 0.79132 | 0.20322 | 1.4162 | 57.5591 | 34.5561 | 1.2804 | 0.20604 | 463.2031 | 26.92 | 83.48
2021-01-30 08:35 | 3.1951 | 0.74717 | 0.14184 | 1.2871 | 41.3298 | 49.2248 | 1.2805 | 0.26492 | 461.5943 | 26.93 | 83.61
2021-01-30 08:40 | 4.4322 | 0.82597 | 0.19055 | 1.4566 | 44.4462 | 30.5413 | 1.2953 | 0.31646 | 462.0305 | 26.96 | 83.69
2021-01-30 08:45 | 4.3037 | 0.8053 | 0.18632 | 1.4207 | 44.7583 | 43.2843 | 1.3027 | 0.32384 | 461.9694 | 26.98 | 83.77
2021-01-30 08:50 | 3.4278 | 0.77083 | 0.16093 | 1.3404 | 51.0714 | 46.2467 | 1.3028 | 0.26499 | 461.4514 | 26.99 | 83.87
2021-01-30 08:55 | 3.5054 | 0.74464 | 0.16306 | 1.3066 | 47.8277 | 39.188 | 1.2956 | 0.26501 | 461.8902 | 27.02 | 83.93
2021-01-30 09:00 | 3.7762 | 0.71705 | 0.16519 | 1.2643 | 39.8192 | 44.3558 | 1.2957 | 0.25766 | 461.3122 | 27.04 | 83.99
2021-01-30 09:05 | 2.8613 | 0.71848 | 0.16096 | 1.2644 | 53.9168 | 34.7588 | 1.3031 | 0.30921 | 462.7992 | 27.07 | 84
2021-01-30 09:10 | 2.7713 | 0.74477 | 0.1525 | 1.2941 | 40.1432 | 41.5766 | 1.3105 | 0.30186 | 460.1601 | 27.08 | 84.09
2021-01-30 09:15 | 3.0423 | 0.94385 | 0.19276 | 1.6395 | 50.4503 | 45.7683 | 1.2812 | 0.32399 | 462.6454 | 27.12 | 84.2
2021-01-30 09:20 | 3.1972 | 1.0213 | 0.22879 | 1.7943 | 53.7748 | 71.2666 | 1.3108 | 0.28719 | 460.4727 | 27.16 | 84.19
2021-01-30 09:25 | 3.2231 | 0.82787 | 0.18007 | 1.4491 | 69.8572 | 49.3941 | 1.2961 | 0.27248 | 460.403 | 27.19 | 84.18
2021-01-30 09:30 | 3.1588 | 0.76156 | 0.16313 | 1.3284 | 56.2552 | 49.3652 | 1.2741 | 0.25039 | 461.3928 | 27.21 | 84.19
2021-01-30 09:35 | 2.7078 | 0.81967 | 0.19281 | 1.4492 | 61.7162 | 56.6204 | 1.2594 | 0.19886 | 462.3362 | 27.25 | 84.19
2021-01-30 09:40 | 2.7724 | 0.85289 | 0.20553 | 1.5129 | 53.2705 | 52.8785 | 1.2521 | 0.18414 | 459.6709 | 27.28 | 84.17
2021-01-30 09:45 | 3.1852 | 0.80594 | 0.20554 | 1.4409 | 52.5212 | 51.5824 | 1.2596 | 0.22834 | 460.0967 | 27.32 | 84.16
2021-01-30 09:50 | 3.8817 | 0.97601 | 0.19495 | 1.691 | 48.6644 | 52.6777 | 1.2596 | 0.26518 | 461.6086 | 27.34 | 84.15
2021-01-30 09:55 | 4.5655 | 1.0411 | 0.21404 | 1.8098 | 43.2924 | 61.0077 | 1.2671 | 0.3315 | 459.9571 | 27.38 | 84.14
2021-01-30 10:00 | 4.2174 | 1.03 | 0.20133 | 1.7802 | 55.9223 | 47.6165 | 1.2671 | 0.33151 | 460.4354 | 27.4 | 84.1
2021-01-30 10:05 | 4.307 | 1.0409 | 0.23096 | 1.8265 | 49.9918 | 50.8686 | 1.2522 | 0.35355 | 459.9637 | 27.38 | 83.85
2021-01-30 10:10 | 4.0816 | 1.0269 | 0.20946 | 1.7836 | 60.0314 | 50.8639 | 1.2429 | 0.28683 | 462.4671 | 27.22 | 80.59
2021-01-30 10:15 | 4.3197 | 0.93027 | 0.18379 | 1.6097 | 71.0582 | 42.4251 | 1.241 | 0.30842 | 462.6021 | 27.25 | 76.38
2021-01-30 10:20 | 4.7012 | 0.86749 | 0.21529 | 1.545 | 68.6426 | 49.3035 | 1.2473 | 0.2788 | 462.8708 | 27.34 | 73.63
2021-01-30 10:25 | 3.8512 | 0.82708 | 0.18141 | 1.4492 | 58.3946 | 44.4892 | 1.2392 | 0.21998 | 463.5529 | 27.41 | 71.79
2021-01-30 10:30 | 3.7478 | 0.89158 | 0.21512 | 1.5818 | 60.1083 | 69.7499 | 1.239 | 0.27126 | 461.4925 | 27.45 | 71.11
2021-01-30 10:35 | 3.6703 | 0.88458 | 0.20455 | 1.5584 | 65.5413 | 52.934 | 1.2388 | 0.3152 | 462.5542 | 27.48 | 70.62
2021-01-30 10:40 | 3.0159 | 0.98643 | 0.22143 | 1.7335 | 60.8316 | 57.6489 | 1.2389 | 0.2639 | 461.9349 | 27.53 | 70.53
2021-01-30 10:45 | 3.234 | 1.1446 | 0.24462 | 1.9991 | 70.5726 | 45.6145 | 1.2315 | 0.2419 | 462.4415 | 27.55 | 70.36
2021-01-30 10:50 | 3.0286 | 1.1707 | 0.25726 | 2.0518 | 68.969 | 54.935 | 1.2315 | 0.21257 | 462.9307 | 27.58 | 70.16
2021-01-30 10:55 | 3.8242 | 0.86392 | 0.21087 | 1.5351 | 69.3789 | 55.8789 | 1.2315 | 0.22723 | 461.8766 | 27.59 | 70.09
2021-01-30 11:00 | 5.0704 | 0.75133 | 0.17085 | 1.3225 | 61.4094 | 49.3843 | 1.2391 | 0.30795 | 461.6828 | 27.63 | 70.68
2021-01-30 11:05 | 5.0589 | 0.78595 | 0.17512 | 1.3798 | 58.098 | 48.0623 | 1.2615 | 0.34471 | 462.0638 | 27.64 | 71.35
2021-01-30 11:10 | 4.006 | 0.9098 | 0.21942 | 1.614 | 57.5727 | 30.4966 | 1.2761 | 0.32269 | 462.179 | 27.61 | 71.34
2021-01-30 11:15 | 3.9809 | 0.94436 | 0.22789 | 1.6776 | 50.9761 | 40.1994 | 1.2836 | 0.33008 | 460.5126 | 27.63 | 71.67
2021-01-30 11:20 | 3.8151 | 0.94464 | 0.24696 | 1.6949 | 48.4325 | 56.9619 | 1.284 | 0.3155 | 461.3857 | 27.65 | 72.37
2021-01-30 11:25 | 3.8035 | 0.9174 | 0.24704 | 1.6533 | 46.8549 | 41.4786 | 1.2845 | 0.28625 | 461.2202 | 27.66 | 73.18
2021-01-30 11:30 | 4.2538 | 0.80042 | 0.22595 | 1.455 | 67.2997 | 60.8021 | 1.2773 | 0.29363 | 461.6966 | 27.65 | 73.56
2021-01-30 11:35 | 4.6122 | 0.86077 | 0.19633 | 1.5157 | 59.7759 | 45.5103 | 1.2695 | 0.2862 | 461.8096 | 27.67 | 72.66
2021-01-30 11:40 | 4.8568 | 0.99309 | 0.2238 | 1.746 | 67.8614 | 62.6294 | 1.255 | 0.30824 | 460.0464 | 27.77 | 72.51
2021-01-30 11:45 | 4.2406 | 1.0855 | 0.26605 | 1.93 | 61.4342 | 38.1496 | 1.2405 | 0.2936 | 461.4756 | 27.82 | 72.61
2021-01-30 11:50 | 4.6003 | 1.1489 | 0.28294 | 2.044 | 73.9135 | 70.7061 | 1.2405 | 0.28626 | 460.8838 | 27.87 | 72.37
2021-01-30 11:55 | 4.8948 | 1.1211 | 0.21955 | 1.938 | 82.0791 | 70.0745 | 1.2402 | 0.30087 | 461.9755 | 27.9 | 71.7
2021-01-30 12:00 | 5.7158 | 1.2186 | 0.2195 | 2.0895 | 72.1865 | 38.8523 | 1.2326 | 0.32282 | 460.9727 | 27.94 | 70.98
2021-01-30 12:05 | 5.6523 | 1.1361 | 0.18365 | 1.923 | 57.2113 | 61.1987 | 1.2327 | 0.39623 | 461.8521 | 28.01 | 70.99
2021-01-30 12:10 | 5.203 | 0.94889 | 0.21955 | 1.674 | 61.3984 | 36.0641 | 1.2255 | 0.42562 | 461.7729 | 28.04 | 71.05
2021-01-30 12:15 | 5.2152 | 0.94325 | 0.24273 | 1.6865 | 61.9039 | 34.5692 | 1.2253 | 0.38154 | 460.7493 | 28.07 | 70.58
2021-01-30 12:20 | 6.0095 | 1.1604 | 0.2321 | 2.0108 | 50.5929 | 56.3456 | 1.2396 | 0.35207 | 461.4282 | 28.07 | 69.7
2021-01-30 12:25 | 5.1601 | 1.0073 | 0.24467 | 1.7886 | 57.1158 | 48.952 | 1.2464 | 0.42526 | 460.0044 | 28.09 | 68.69
2021-01-30 12:30 | 4.4268 | 0.88308 | 0.24669 | 1.6003 | 75.8487 | 57.5666 | 1.2386 | 0.57168 | 461.739 | 28.09 | 67.73
2021-01-30 12:35 | 4.2337 | 0.86782 | 0.24243 | 1.5727 | 70.6643 | 21.5226 | 1.2165 | 0.469 | 462.3148 | 28.1 | 67.3
2021-01-30 12:40 | 3.6045 | 0.92545 | 0.27191 | 1.6884 | 46.5588 | 33.9981 | 1.209 | 0.32972 | 461.3404 | 28.1 | 66.93
2021-01-30 12:45 | 6.6064 | 0.98736 | 0.26349 | 1.7769 | 63.8112 | 54.4109 | 1.231 | 0.38102 | 463.3631 | 28.13 | 66.89
2021-01-30 12:50 | 4.8619 | 0.97913 | 0.23187 | 1.7327 | 99.0131 | 92.0038 | 1.2164 | 0.41034 | 463.2763 | 28.18 | 66.75
2021-01-30 12:55 | 5.0414 | 0.97223 | 0.19814 | 1.6884 | 91.4473 | 26.487 | 1.2163 | 0.3224 | 462.2008 | 28.21 | 66.57
2021-01-30 13:00 | 4.1436 | 0.87738 | 0.20869 | 1.5515 | 69.6324 | 40.9892 | 1.209 | 0.30043 | 462.1977 | 28.2 | 66.71
2021-01-30 13:05 | 3.9766 | 0.75495 | 0.25505 | 1.4123 | 51.3522 | 22.9874 | 1.2017 | 0.31507 | 463.2757 | 28.19 | 66.63
2021-01-30 13:10 | 3.8615 | 0.70413 | 0.2361 | 1.3154 | 42.2018 | 11.3612 | 1.2164 | 0.36639 | 462.2116 | 28.18 | 66.88
2021-01-30 13:15 | 3.0668 | 0.62864 | 0.21718 | 1.1787 | 29.7802 | 4.2191 | 1.2314 | 0.23455 | 461.6546 | 28.17 | 67.45
2021-01-30 13:20 | 4.0434 | 0.74718 | 0.2278 | 1.3752 | 35.253 | 21.2565 | 1.2244 | 0.26395 | 460.9841 | 28.17 | 68.28
2021-01-30 13:25 | 4.6181 | 0.84436 | 0.2403 | 1.5346 | 36.863 | 49.6603 | 1.2164 | 0.30043 | 460.8094 | 28.13 | 66.87
2021-01-30 13:30 | 4.3722 | 0.84669 | 0.276 | 1.5738 | 39.1321 | 21.674 | 1.2158 | 0.32957 | 462.0631 | 28.14 | 65.57
2021-01-30 13:35 | 4.2169 | 0.90686 | 0.2738 | 1.6639 | 41.8361 | 47.2092 | 1.23 | 0.36607 | 460.613 | 28.17 | 64.59
2021-01-30 13:40 | 3.1137 | 0.84753 | 0.2653 | 1.5644 | 52.3827 | 18.1238 | 1.2223 | 0.27081 | 462.2607 | 28.2 | 63.75
2021-01-30 13:45 | 2.998 | 0.75264 | 0.23368 | 1.3873 | 51.7391 | 43.0681 | 1.2221 | 0.19759 | 461.7503 | 28.24 | 63.21
2021-01-30 13:50 | 3.7803 | 0.71845 | 0.20846 | 1.3097 | 48.7973 | 30.6521 | 1.2224 | 0.31474 | 461.0889 | 28.27 | 63.62
2021-01-30 13:55 | 4.4111 | 0.71617 | 0.20228 | 1.3 | 58.1336 | 6.9038 | 1.2305 | 0.29298 | 461.23 | 28.32 | 65.09
2021-01-30 14:00 | 4.487 | 0.85482 | 0.20645 | 1.5167 | 45.1267 | 47.6599 | 1.2156 | 0.29291 | 460.2739 | 28.33 | 64.51
2021-01-30 14:05 | 3.8602 | 0.82901 | 0.20231 | 1.473 | 66.3601 | 23.4025 | 1.1867 | 0.27104 | 461.056 | 28.39 | 65.19
2021-01-30 14:10 | 3.4774 | 0.68915 | 0.20452 | 1.2609 | 80.1719 | 84.1035 | 1.1874 | 0.2492 | 460.1966 | 28.45 | 66.31
2021-01-30 14:15 | 2.2079 | 0.69354 | 0.24468 | 1.3078 | 79.0415 | 1.7458 | 1.1878 | 0.2273 | 459.9633 | 28.49 | 67.09
2021-01-30 14:20 | 2.1952 | 0.58487 | 0.23626 | 1.1328 | 67.6474 | 31.4462 | 1.1952 | 0.19065 | 461.5044 | 28.48 | 67.3
2021-01-30 14:25 | 3.0425 | 0.64681 | 0.22361 | 1.213 | 78.6178 | 34.713 | 1.2026 | 0.29331 | 460.4381 | 28.49 | 67.33
2021-01-30 14:30 | 4.52 | 0.78601 | 0.23843 | 1.4433 | 81.5453 | 45.077 | 1.1442 | 0.44742 | 460.3292 | 28.52 | 67.79
2021-01-30 14:35 | 3.6338 | 0.808 | 0.24686 | 1.4854 | 81.3567 | 27.3963 | 1.1808 | 0.27137 | 460.2891 | 28.56 | 67.52
2021-01-30 14:40 | 3.5304 | 0.72251 | 0.25314 | 1.3606 | 69.1906 | 36.3464 | 1.1659 | 0.38865 | 460.3669 | 28.57 | 66.98
2021-01-30 14:45 | 4.196 | 0.70979 | 0.21507 | 1.301 | 55.2075 | 19.104 | 1.1654 | 0.34449 | 461.6196 | 28.57 | 65.82
2021-01-30 14:50 | 4.1325 | 0.72366 | 0.24041 | 1.3497 | 55.2366 | 4.6304 | 1.1656 | 0.34454 | 460.465 | 28.6 | 66.09
2021-01-30 14:55 | 3.8503 | 0.70855 | 0.21933 | 1.3054 | 61.0912 | 29.9501 | 1.1583 | 0.33722 | 460.4016 | 28.63 | 66.07
2021-01-30 15:00 | 3.1302 | 0.71237 | 0.21291 | 1.3049 | 51.8482 | -11.4739 | 1.1431 | 0.23449 | 460.6343 | 28.61 | 65.06
2021-01-30 15:05 | 2.6678 | 0.70121 | 0.23183 | 1.3067 | 65.5651 | 40.2112 | 1.1429 | 0.20513 | 460.7238 | 28.62 | 64.46
2021-01-30 15:10 | 2.1808 | 0.66697 | 0.2382 | 1.2606 | 84.4721 | 12.7155 | 1.1504 | 0.19052 | 460.5992 | 28.64 | 64.89
2021-01-30 15:15 | 4.3235 | 0.77292 | 0.24243 | 1.4272 | 88.9946 | 48.341 | 1.1578 | 0.27114 | 459.4802 | 28.67 | 64.97
2021-01-30 15:20 | 3.5922 | 0.86094 | 0.24876 | 1.5684 | 99.2069 | 13.281 | 1.1578 | 0.38106 | 462.0267 | 28.7 | 64.86
2021-01-30 15:25 | 2.8097 | 0.84996 | 0.2593 | 1.5622 | 92.5684 | 28.9129 | 1.1652 | 0.36641 | 460.9339 | 28.73 | 64.8
2021-01-30 15:30 | 3.7979 | 0.79639 | 0.26354 | 1.4843 | 91.807 | 38.359 | 1.1653 | 0.30049 | 459.2911 | 28.76 | 64.91
2021-01-30 15:35 | [9 empty] | 28.8 | 65.09
2021-01-30 15:40 | 3.4256 | 0.75232 | 0.28882 | 1.442 | 63.9644 | 41.6302 | 1.1579 | 0.24184 | 459.7382 | 28.83 | 64.46
2021-01-30 15:45 | 3.2828 | 0.67084 | 0.30132 | 1.3275 | 63.0299 |  | 1.1646 | 0.32229 | 458.3647 | 28.86 | 63.14
2021-01-30 15:50 | 3.6155 | 0.70781 | 0.23806 | 1.323 | 60.9863 | 45.4064 | 1.1717 | 0.32955 | 459.5207 | 28.88 | 62.51
2021-01-30 15:55 | 3.5116 | 0.99468 | 0.24429 | 1.7711 | 65.9763 | 2.7375 | 1.1713 | 0.36602 | 459.6224 | 28.93 | 61.39
2021-01-30 16:00 | 4.2289 | 0.92865 | 0.22321 | 1.6467 | 82.804 | 41.5609 | 1.2151 | 0.37331 | 460.1049 | 28.98 | 61
2021-01-30 16:05 | 4.1656 | 0.76532 | 0.2064 | 1.3774 | 67.8284 | 24.9576 | 1.2153 | 0.35142 | 460.4617 | 29.03 | 61.27
2021-01-30 16:10 | 4.7299 | 0.67332 | 0.21906 | 1.2532 | 66.573 | 19.0121 | 1.2154 | 0.39538 | 460.9088 | 29.05 | 61.41
2021-01-30 16:15 | 4.8335 | 0.74218 | 0.23595 | 1.3736 | 79.7461 | 49.7041 | 1.223 | 0.39546 | 459.2456 | 29.06 | 61.87
2021-01-30 16:20 | 3.2823 | 0.69135 | 0.25703 | 1.3147 | 80.6829 | 11.4983 | 1.223 | 0.33689 | 459.6828 | 29.1 | 61.83
2021-01-30 16:25 | 2.3982 | 0.7369 | 0.2571 | 1.3887 | 85.2175 | 57.7932 | 1.216 | 0.38825 | 459.5518 | 29.11 | 62.4
2021-01-30 16:30 | 4.0271 | 0.72867 | 0.255 | 1.3719 | 69.6557 | -11.4708 | 1.2161 | 0.33698 | 457.9695 | 29.12 | 62.44
2021-01-30 16:35 | 5.6185 | 0.70681 | 0.24662 | 1.33 | 57.8476 | 46.0257 | 1.209 | 0.25645 | 458.3954 | 29.12 | 62.92
2021-01-30 16:40 | 6.6066 | 0.7151 | 0.23609 | 1.3322 | 59.0921 | 3.0377 | 1.1871 | 0.25646 | 459.9409 | 29.11 | 63.07
2021-01-30 16:45 | 4.3749 | 0.75506 | 0.26985 | 1.4251 | 47.2952 | 42.1325 | 1.1799 | 0.31512 | 458.3247 | 29.12 | 63.29
2021-01-30 16:50 | 3.7209 | 0.85279 | 0.2783 | 1.5855 | 69.3789 | 34.0171 | 1.202 | 0.35912 | 458.769 | 29.14 | 63.44
2021-01-30 16:55 | 3.4389 | 0.71941 | 0.24037 | 1.3431 | 49.0477 | 21.8036 | 1.224 | 0.27852 | 459.7435 | 29.16 | 63.52
2021-01-30 17:00 | 3.4898 | 0.67532 | 0.22137 | 1.2565 | 25.845 | 20.6514 | 1.2239 | 0.2565 | 459.251 | 29.18 | 63.16
2021-01-30 17:05 | 3.9384 | 0.71513 | 0.19183 | 1.2859 | 46.7584 | 12.7877 | 1.2237 | 0.2638 | 459.7854 | 29.2 | 62.84
2021-01-30 17:10 | 4.6571 | 0.7468 | 0.19817 | 1.3429 | 47.2228 | 41.5881 | 1.2238 | 0.32977 | 459.2432 | 29.2 | 62.97
2021-01-30 17:15 | 6.0685 | 0.72482 | 0.2319 | 1.3429 | 53.6598 | 3.2742 | 1.2385 | 0.42505 | 459.2133 | 29.21 | 63.01
2021-01-30 17:20 | 4.2469 | 0.69322 | 0.2277 | 1.2903 | 44.8555 | 42.5563 | 1.2312 | 0.32247 | 459.6928 | 29.22 | 63.09
2021-01-30 17:25 | 3.6951 | 0.65606 | 0.2045 | 1.2101 | 49.0826 | 44.4227 | 1.2019 | 0.27116 | 459.7101 | 29.22 | 63
2021-01-30 17:30 | 3.5924 | 0.77846 | 0.2045 | 1.3999 | 56.4413 | 60.4853 | 1.2019 | 0.32978 | 460.2475 | 29.21 | 63.01
2021-01-30 17:35 | 3.8106 | 0.77298 | 0.26564 | 1.4505 | 52.0502 | 32.4146 | 1.2092 | 0.35911 | 459.744 | 29.19 | 63.17
2021-01-30 17:40 | 4.5545 | 0.65052 | 0.23189 | 1.229 | 51.3075 | 36.764 | 1.2311 | 0.39572 | 458.7732 | 29.17 | 63.07
2021-01-30 17:45 | 2.7456 | 0.51027 | 0.21715 | 0.99931 | 39.9581 | 35.3084 | 1.2165 | 0.2565 | 458.2476 | 29.16 | 63.23
2021-01-30 17:50 | 3.0152 | 0.58593 | 0.20661 | 1.1069 | 44.1165 | 15.3145 | 1.2239 | 0.22719 | 460.864 | 29.13 | 63.42
2021-01-30 17:55 | 2.8096 | 0.57211 | 0.19605 | 1.073 | 37.6661 | 29.2502 | 1.2164 | 0.19053 | 460.9634 | 29.1 | 63.25
2021-01-30 18:00 | 2.8736 | 0.55834 | 0.17496 | 1.0287 | 21.3366 | -5.152 | 1.2237 | 0.19785 | 460.9836 | 29.06 | 63.39
2021-01-30 18:05 | 2.1039 | 0.55009 | 0.1834 | 1.0287 | 25.4624 | 39.461 | 1.2237 | 0.18319 | 461.0441 | 29.02 | 63.54
2021-01-30 18:10 | 2.1166 | 0.50605 | 0.20025 | 0.97383 | 20.0113 | 15.2086 | 1.2236 | 0.16853 | 461.1535 | 28.97 | 63.55
2021-01-30 18:15 | 2.0782 | 0.43593 | 0.1855 | 0.85371 | 22.475 | 34.6054 | 1.2237 | 0.17586 | 462.2039 | 28.95 | 63.71
2021-01-30 18:20 | 1.9115 | 0.38094 | 0.1581 | 0.74202 | 10.8788 | 39.5126 | 1.2164 | 0.18319 | 461.178 | 28.93 | 63.89
2021-01-30 18:25 | 2.0012 | 0.30529 | 0.12858 | 0.59654 | 11.0424 | 3.52 | 1.2237 | 0.1612 | 460.7764 | 28.87 | 63.98
2021-01-30 18:30 | 2.4501 | 0.34515 | 0.14544 | 0.67239 | 1.8677 | 34.6753 | 1.2309 | 0.16852 | 460.8892 | 28.81 | 64.09
2021-01-30 18:35 | 2.4242 | 0.41525 | 0.16229 | 0.7988 | -4.3097 | 4.166 | 1.2162 | 0.1392 | 460.4524 | 28.78 | 64.01
2021-01-30 18:40 | 2.5268 | 0.43587 | 0.18336 | 0.85148 | -3.0578 | 28.5258 | 1.1942 | 0.19049 | 461.0374 | 28.74 | 64.13
2021-01-30 18:45 | 2.078 | 0.4359 | 0.17705 | 0.84522 | -0.66702 | 96.3278 | 1.2089 | 0.1905 | 438.2447 | 28.7 | 64.46
2021-01-30 18:50 | 2.0653 | 0.51155 | 0.15387 | 0.93799 | 210.0044 | 332.4523 | 1.2236 | 0.18318 | 349.0986 | 28.64 | 64.76
2021-01-30 18:55 | 2.4373 | 0.60781 | 0.20236 | 1.134 | 157.9874 | 67.5769 | 1.2383 | 0.21249 | 348.0919 | 28.61 | 64.9
2021-01-30 19:00 | 2.4372 | 0.54591 | 0.16441 | 1.0012 | 70.2215 | 19.6821 | 1.2529 | 0.18317 | 349.5191 | 28.59 | 64.93
2021-01-30 19:05 | 2.6425 | 0.53767 | 0.17284 | 0.99701 | 31.8844 | 34.8296 | 1.2676 | 0.19051 | 350.0624 | 28.56 | 65.12
2021-01-30 19:10 | 2.2322 | 0.51022 | 0.20448 | 0.98656 | 4.7108 | 17.6833 | 1.275 | 0.19052 | 349.0012 | 28.55 | 65.4
2021-01-30 19:15 | 2.0656 | 0.51988 | 0.19395 | 0.99085 | 1.8988 | 37.9249 | 1.2825 | 0.19054 | 349.0112 | 28.52 | 65.69
2021-01-30 19:20 | 2.8097 | 0.61615 | 0.20027 | 1.1447 | -9.6067 | 33.2233 | 1.2898 | 0.19786 | 348.0147 | 28.49 | 65.75
2021-01-30 19:25 | 2.63 | 0.557 | 0.16443 | 1.0182 | -4.4338 | 17.1092 | 1.2971 | 0.21252 | 349.5899 | 28.48 | 65.75
2021-01-30 19:30 | 2.3603 | 0.49643 | 0.14544 | 0.90639 | -1.2109 | 34.276 | 1.2969 | 0.19784 | 349.7226 | 28.4 | 65.77
2021-01-30 19:35 | 2.2449 | 0.47442 | 0.14544 | 0.87266 | -5.87 | 13.9464 | 1.2969 | 0.20516 | 349.2384 | 28.37 | 65.88
2021-01-30 19:40 | 2.1037 | 0.49228 | 0.14544 | 0.90002 | 2.627 | 42.5145 | 1.3042 | 0.18317 | 349.8102 | 28.34 | 65.87
2021-01-30 19:45 | 2.1675 | 0.52795 | 0.1412 | 0.95046 | -2.247 | 54.3589 | 1.2893 | 0.15384 | 349.3758 | 28.31 | 65.62
2021-01-30 19:50 | 2.0517 | 0.39726 | 0.12853 | 0.73747 | 5.3548 | 7.1193 | 1.2671 | 0.16114 | 349.9864 | 28.29 | 65.21
2021-01-30 19:55 | 1.2691 | 0.29821 | 0.11796 | 0.57718 | -18.2344 | 21.0855 | 1.2595 | 0.14645 | 349.1655 | 28.18 | 64.96
2021-01-30 20:00 | 1.5895 | 0.36414 | 0.13059 | 0.68665 | -12.7361 | 15.1459 | 1.2593 | 0.1684 | 349.7922 | 28.12 | 64.92
2021-01-30 20:05 | 2.3969 | 0.37375 | 0.12216 | 0.69506 | -12.6333 | 17.0632 | 1.2666 | 0.205 | 350.3195 | 28.12 | 64.87
2021-01-30 20:10 | 1.7943 | 0.29402 | 0.11162 | 0.5623 | -8.2846 | 21.0703 | 1.2738 | 0.15374 | 351.2656 | 28.09 | 64.77
2021-01-30 20:15 | 1.8328 | 0.27616 | 0.098982 | 0.52229 | -14.3442 | 10.0276 | 1.2811 | 0.14642 | 349.9306 | 28.04 | 64.89
2021-01-30 20:20 | 1.9225 | 0.37509 | 0.12005 | 0.69711 | -9.2179 | 8.8898 | 1.2885 | 0.16106 | 352.9135 | 28.01 | 65.14
2021-01-30 20:25 | 1.8199 | 0.49186 | 0.14952 | 0.90346 | -2.8708 | 27.3447 | 1.3031 | 0.21962 | 349.7682 | 28.04 | 64.9
2021-01-30 20:30 | 1.4739 | 0.41629 | 0.10951 | 0.74972 | -9.1867 | -11.914 | 1.3031 | 0.16105 | 351.5465 | 28 | 64.99
2021-01-30 20:35 | 1.3456 | 0.35994 | 0.11161 | 0.66123 | -11.5647 | -11.5134 | 1.303 | 0.1464 | 351.1512 | 27.91 | 65.18
2021-01-30 20:40 | 1.5118 | 0.44637 | 0.12 | 0.80422 | -9.3272 | 34.4594 | 1.3027 | 0.16832 | 351.6666 | 27.85 | 64.79
2021-01-30 20:45 | 1.2296 | 0.38858 | 0.11786 | 0.7135 | 2.367 | 7.7364 | 1.3023 | 0.16096 | 350.7403 | 27.83 | 64.17
2021-01-30 20:50 | 1.7162 | 0.30342 | 0.10522 | 0.57032 | -5.1844 | 17.8789 | 1.3095 | 0.13899 | 351.348 | 27.79 | 64.03
2021-01-30 20:55 | 1.4096 | 0.29809 | 0.094755 | 0.55379 | -11.1126 | -3.4855 | 1.3029 | 0.15371 | 350.8237 | 27.77 | 65.49
2021-01-30 21:00 | 2.2564 | 0.32709 | 0.10954 | 0.61092 | -11.9279 | -12.7177 | 1.3108 | 0.18307 | 350.6863 | 27.75 | 66.76
2021-01-30 21:05 | 2.2054 | 0.36562 | 0.10745 | 0.66789 | -9.16 | 14.5247 | 1.3183 | 0.25634 | 350.1182 | 27.75 | 67.11
2021-01-30 21:10 | 1.667 | 0.32578 | 0.11167 | 0.61105 | 1.8773 | 30.4262 | 1.3331 | 0.271 | 351.0755 | 27.8 | 67.11
2021-01-30 21:15 | 1.2949 | 0.26113 | 0.086373 | 0.48874 | -9.682 | -10.3486 | 1.3474 | 0.16843 | 350.1958 | 27.72 | 66.91
2021-01-30 21:20 | 2.7435 | 0.27761 | 0.09901 | 0.52243 | -1.1077 | 13.9995 | 1.362 | 0.17575 | 350.2756 | 27.66 | 67.07
2021-01-30 21:25 | 2.1154 | 0.28586 | 0.086372 | 0.52666 | -8.4922 | 25.8869 | 1.3694 | 0.14646 | 350.2893 | 27.64 | 67.22
2021-01-30 21:30 | 2.0384 | 0.25562 | 0.08005 | 0.47188 | -2.5332 | -6.7792 | 1.3694 | 0.13913 | 350.8316 | 27.63 | 67.19
2021-01-30 21:35 | 2.1795 | 0.23914 | 0.08848 | 0.45504 | -4.5333 | 5.0359 | 1.3621 | 0.1904 | 350.3227 | 27.61 | 67.35
2021-01-30 21:40 | 1.8847 | 0.23777 | 0.094804 | 0.45716 | -0.91285 | 14.6775 | 1.3621 | 0.13914 | 350.8757 | 27.57 | 67.62
2021-01-30 21:45 | 1.7053 | 0.29414 | 0.11798 | 0.56885 | -1.354 | 11.4779 | 1.3549 | 0.13183 | 349.8286 | 27.56 | 67.78
2021-01-30 21:50 | 1.718 | 0.32024 | 0.11377 | 0.60254 | -0.57439 | 6.3798 | 1.3548 | 0.095205 | 349.8637 | 27.54 | 67.77
2021-01-30 21:55 | 1.5642 | 0.34086 | 0.12008 | 0.64256 | 7.7029 | 17.0981 | 1.3402 | 0.073234 | 349.878 | 27.53 | 67.79
2021-01-30 22:00 | 1.1153 | 0.34495 | 0.14325 | 0.672 | -2.8819 | -0.62562 | 1.3254 | 0.12449 | 349.9058 | 27.53 | 67.58
2021-01-30 22:05 | 1.2048 | 0.25694 | 0.098989 | 0.49284 | -4.5527 | -1.2612 | 1.3398 | 0.14643 | 351.0927 | 27.47 | 67.26
2021-01-30 22:10 | 1.8966 | 0.27475 | 0.094759 | 0.51591 | 5.0542 | 20.6783 | 1.3542 | 0.2196 | 351.7489 | 27.41 | 67.01
2021-01-30 22:15 | 0.98657 | 0.25959 | 0.10948 | 0.5095 | 3.7823 | 12.218 | 1.3466 | 0.15369 | 352.3963 | 27.36 | 66.7
2021-01-30 22:20 | 0.99926 | 0.25269 | 0.090519 | 0.47786 | 4.325 | -13.2414 | 1.3464 | 0.24148 | 350.8966 | 27.34 | 66.45
2021-01-30 22:25 | 1.0376 | 0.22109 | 0.086302 | 0.4252 | -0.70711 | 26.0299 | 1.3463 | 0.18293 | 351.4695 | 27.32 | 66.32
2021-01-30 22:30 | 1.422 | 0.2211 | 0.077885 | 0.41679 | 12.6464 | 16.7048 | 1.3537 | 0.12439 | 351.9683 | 27.33 | 66.37
2021-01-30 22:35 | 1.5884 | 0.20873 | 0.073673 | 0.39363 | 16.899 | 2.6133 | 1.3463 | 0.087805 | 352.4997 | 27.33 | 66.3
2021-01-30 22:40 | 0.98633 | 0.21147 | 0.079984 | 0.40413 | 13.4448 | 9.1101 | 1.3463 | 0.036584 | 352.0409 | 27.29 | 66.33
2021-01-30 22:45 | 1.1657 | 0.22246 | 0.08209 | 0.42308 | 9.5816 | 21.8378 | 1.3244 | 0.087802 | 350.4815 | 27.28 | 66.4
2021-01-30 22:50 | 1.1656 | 0.23618 | 0.077878 | 0.43991 | 1.0657 | 7.747 | 1.3243 | 0.073166 | 351.5598 | 27.26 | 66.4
2021-01-30 22:55 | 1.0631 | 0.19361 | 0.073667 | 0.37044 | 11.651 | 13.1676 | 1.3243 | 0.058532 | 351.5921 | 27.24 | 66.41
2021-01-30 23:00 | 0.9094 | 0.19086 | 0.082082 | 0.37463 | 11.4353 | 18.0445 | 1.3169 | 0.051213 | 351.6296 | 27.22 | 66.38
2021-01-30 23:05 | 0.81967 | 0.13867 | 0.061031 | 0.27359 | 0.94262 | -2.3975 | 1.3022 | 0.051209 | 352.2284 | 27.18 | 66.31
2021-01-30 23:10 | 0.53791 | 0.14141 | 0.054718 | 0.27148 | 3.4119 | 0.70697 | 1.2949 | 0.10973 | 351.2269 | 27.14 | 66.49
2021-01-30 23:15 | 0.83247 | 0.16475 | 0.063135 | 0.31567 | 8.4528 | 16.2396 | 1.3095 | 0.058524 | 350.5854 | 27.1 | 66.67
2021-01-30 23:20 | 1.2166 | 0.17985 | 0.067341 | 0.34302 | 9.9483 | -1.4856 | 1.3094 | 0.15362 | 351.6681 | 27.08 | 66.65
2021-01-30 23:25 | 1.3191 | 0.22104 | 0.06103 | 0.39985 | 9.2621 | 23.0323 | 1.3095 | 0.21215 | 351.1589 | 27.06 | 66.8
2021-01-30 23:30 | 0.92216 | 0.24577 | 0.054719 | 0.43354 | 11.0045 | 23.9148 | 1.3388 | 0.14632 | 352.6978 | 27.07 | 66.91
2021-01-30 23:35 | 0.79407 | 0.15652 | 0.052613 | 0.29253 | 14.4059 | -18.2687 | 1.3388 | 0.11705 | 351.7055 | 27.03 | 67.01
2021-01-30 23:40 | 0.87095 | 0.11808 | 0.063139 | 0.24414 | 2.2235 | 22.778 | 1.3461 | 0.10242 | 352.2834 | 26.97 | 67.37
2021-01-30 23:45 | 0.7173 | 0.12907 | 0.058933 | 0.25678 | 7.3472 | 6.9885 | 1.3535 | 0.080481 | 351.7627 | 26.95 | 67.61
2021-01-30 23:50 |  | 0.1277 | 0.054724 | 0.25047 | -0.5431 | 1.035 | 1.3462 | 0.051215 | 352.333 | 26.91 | 67.77
2021-01-30 23:55 | 0.53799 | 0.15379 | 0.058935 | 0.29257 | 3.8838 | 2.9922 | 1.3243 | 0.051216 | 351.8239 | 26.89 | 67.92
2021-01-31 | 1.1529 | 0.11672 | 0.046308 | 0.22522 | 1.9266 | 16.3453 | 1.3097 | 0.080486 | 351.8437 | 26.86 | 68.16
2021-01-31 00:05 | 0.8839 | 0.1387 | 0.052624 | 0.26523 | 7.3172 | 12.9741 | 1.3171 | 0.080489 | 351.3334 | 26.84 | 68.32
2021-01-31 00:10 | 0.98633 | 0.13457 | 0.056831 | 0.26311 | 5.5542 | -10.9444 | 1.317 | 0.087801 | 353.4811 | 26.81 | 68.3
2021-01-31 00:15 | 0.92233 | 0.20187 | 0.052624 | 0.36205 | 0.91208 | 7.8295 | 1.3244 | 0.19025 | 352.9526 | 26.8 | 68.47
2021-01-31 00:20 | 1.1913 | 0.16753 | 0.050516 | 0.30731 | 7.6344 | 9.6532 | 1.3463 | 0.13902 | 350.9004 | 26.78 | 68.4
2021-01-31 00:25 | 1.0503 | 0.14829 | 0.048408 | 0.27572 | -4.3959 | -10.6977 | 1.3608 | 0.14633 | 352.5653 | 26.72 | 68.46
2021-01-31 00:30 | 0.88381 | 0.13045 | 0.046305 | 0.24626 | -3.3098 | 5.6359 | 1.3609 | 0.12438 | 352.6036 | 26.68 | 68.69
2021-01-31 00:35 | 1.0887 | 0.16889 | 0.046304 | 0.30729 | -4.6316 | 7.1114 | 1.3682 | 0.11706 | 352.6547 | 26.64 | 68.82
2021-01-31 00:40 | 0.94791 | 0.12359 | 0.052622 | 0.24206 | -5.3698 | -14.1622 | 1.3682 | 0.10975 | 352.8018 | 26.64 | 68.93
2021-01-31 00:45 | 0.74295 | 0.14556 | 0.048411 | 0.27363 | 0.08198 | 10.0221 | 1.3755 | 0.10975 | 352.8529 | 26.6 | 69.06
2021-01-31 00:50 | 0.79421 | 0.16478 | 0.048413 | 0.301 | 6.0052 | 21.7869 | 1.3829 | 0.1317 | 352.673 | 26.6 | 69.21
2021-01-31 00:55 | 0.61488 | 0.1387 | 0.050519 | 0.26312 | 5.9029 | 2.5415 | 1.3829 | 0.12439 | 352.1401 | 26.6 | 69.28
2021-01-31 01:00 | 0.85826 | 0.12222 | 0.044203 | 0.23154 | 6.1692 | -10.8832 | 1.3829 | 0.10244 | 352.8878 | 26.56 | 69.32
2021-01-31 01:05 |  |  |  |  | 5.4417 | 19.6558 |  |  | 351.6635 | 26.56 | 69.44
2021-01-31 01:10 |  |  |  |  | 1.8547 | 0.65582 |  |  | 352.2902 | 26.5 | 69.43
2021-01-31 01:15 |  |  |  |  | 7.9107 | 2.49 |  |  | 353 | 26.49 | 69.37
2021-01-31 01:20 |  |  |  |  | 4.8775 | 13.3517 |  |  | 352.5382 | 26.44 | 69.55
2021-01-31 01:25 |  |  |  |  | 17.9098 | 1.916 |  |  | 351.586 | 26.39 | 69.46
2021-01-31 01:30 |  |  |  |  | 7.9299 | 2.7253 |  |  | 353.0649 | 26.34 | 69.59
2021-01-31 01:35 |  |  |  |  | -0.16394 | 8.2276 |  |  | 353.052 | 26.33 | 69.83
2021-01-31 01:40 |  |  |  |  | 6.9877 | 11.5061 |  |  | 353.0689 | 26.32 | 69.83
2021-01-31 01:45 |  |  |  |  | 6.8033 | 3.125 |  |  | 352.5669 | 26.3 | 69.92
2021-01-31 01:50 |  |  |  |  | 4.6005 | 0.2664 |  |  | 353.0998 | 26.29 | 69.99
2021-01-31 01:55 |  |  |  |  | -1.2295 | 9.4364 |  |  | 352.6052 | 26.27 | 70.02
2021-01-31 02:00 |  |  |  |  | 0.4201 | 8.1253 |  |  | 352.6155 | 26.25 | 70.21
2021-01-31 02:05 |  |  |  |  | 5.7065 | -0.77862 |  |  | 353.2289 | 26.21 | 70.04
2021-01-31 02:10 | 0.44822 | 0.05354 | 0.048399 | 0.13257 | 4.5693 | 11.3002 | 1.3459 | 0.058519 | 354.8408 | 26.18 | 70.15
2021-01-31 02:15 | 0.60191 | 0.049423 | 0.046297 | 0.12205 | 3.5961 | -3.5859 | 1.3314 | 0.065836 | 352.7527 | 26.16 | 70.33
2021-01-31 02:20 | 0.56347 | 0.054913 | 0.046295 | 0.13047 | 3.4423 | 2.971 | 1.3313 | 0.080463 | 352.7795 | 26.15 | 70.25
2021-01-31 02:25 | 0.43543 | 0.045305 | 0.048401 | 0.11785 | -9.7741 | 0.64546 | 1.3167 | 0.073152 | 352.761 | 26.15 | 70.4
2021-01-31 02:30 | 0.57632 | 0.03295 | 0.046298 | 0.096805 | 1.4754 | 12.1923 | 1.3241 | 0.080469 | 353.3267 | 26.11 | 70.62
2021-01-31 02:35 | 0.43545 | 0.041188 | 0.054717 | 0.11996 | 6.8134 | 17.9609 | 1.3241 | 0.065839 | 352.2705 | 26.11 | 70.67
2021-01-31 02:40 | 0.62758 | 0.05492 | 0.056823 | 0.14101 | 1.6599 | -15.9635 | 1.3168 | 0.087789 | 352.257 | 26.11 | 70.78
2021-01-31 02:45 | 0.62758 | 0.048055 | 0.052614 | 0.12627 | 12.2749 | 13.7094 | 1.3095 | 0.095105 | 353.295 | 26.12 | 70.74
2021-01-31 02:50 | 0.58915 | 0.052173 | 0.042091 | 0.12206 | 1.7008 | 10.0207 | 1.3022 | 0.073157 | 351.7477 | 26.1 | 70.79
2021-01-31 02:55 | 0.89655 | 0.086499 | 0.046301 | 0.18099 | 7.0495 | -3.2993 | 1.2949 | 0.058527 | 353.8162 | 26.12 | 70.77
2021-01-31 03:00 | [9 empty] | 26.12 | 70.53
2021-01-31 03:05 | 1.1654 | 0.052169 | 0.046296 | 0.12626 | 4.928 | 22.1708 | 1.2801 | 0.058521 | 351.7627 | 26.11 | 70.53
2021-01-31 03:10 | 0.62755 | 0.061782 | 0.046299 | 0.141 | 21.2703 | 19.3748 | 1.2656 | 0.051208 | 353.3085 | 26.12 | 70.63
2021-01-31 03:15 | 0.46101 | 0.030201 | 0.037877 | 0.08417 | 15.0289 | -7.622 | 1.2508 | 0.036573 | 352.9055 | 26.05 | 70.6
2021-01-31 03:20 | 0.74267 | 0.037062 | 0.037873 | 0.094682 | -4.4765 | 3.0526 | 1.2507 | 0.051198 | 354.072 | 25.98 | 70.62
2021-01-31 03:25 | 0.69144 | 0.031571 | 0.037873 | 0.086265 | 5.8184 | 2.0692 | 1.2507 | 0.043883 | 354.6602 | 25.93 | 70.8
2021-01-31 03:30 | 0.30731 | 0.034317 | 0.035769 | 0.088371 | 1.2702 | -0.54292 | 1.2507 | 0.03657 | 353.6141 | 25.92 | 70.9
2021-01-31 03:35 | 0.49934 | 0.031569 | 0.031558 | 0.079948 | 3.4826 | -0.81943 | 1.2506 | 0.029254 | 354.2062 | 25.89 | 70.77
2021-01-31 03:40 | 0.61461 | 0.21276 | 0.044184 | 0.37031 | 8.9631 | 16.4818 | 1.2507 | 0.051197 | 352.0703 | 25.9 | 70.91
2021-01-31 03:45 | 0.96034 | 0.10158 | 0.044185 | 0.19988 | 2.5609 | -5.2447 | 1.2507 | 0.043884 | 353.0815 | 25.93 | 70.82
2021-01-31 03:50 | 0.83234 | 0.19493 | 0.052604 | 0.35139 | 10.2339 | 0.80929 | 1.2508 | 0.036572 | 353.0043 | 25.98 | 70.76
2021-01-31 03:55 | 0.64024 | 0.12217 | 0.044186 | 0.23145 | 3.6263 | 11.7702 | 1.2434 | 0.03657 | 352.4912 | 25.98 | 70.66
2021-01-31 04:00 | 0.57618 | 0.096081 | 0.035767 | 0.18515 | 2.9091 | 10.2841 | 1.236 | 0.014627 | 352.5383 | 25.96 | 70.55
2021-01-31 04:05 | 0.80666 | 0.090592 | 0.044183 | 0.18305 | 4.0973 | -3.9744 | 1.236 | 0.014627 | 353.0816 | 25.94 | 70.68
2021-01-31 04:10 | 0.72981 | 0.12628 | 0.04839 | 0.24195 | -2.1715 | -0.87066 | 1.236 | 0 | 353.1034 | 25.93 | 70.64
2021-01-31 04:15 | 0.80657 | 0.087837 | 0.05049 | 0.18513 | 14.1445 | 20.7507 | 1.2213 | -0.0073129 | 353.4856 | 25.93 | 70.48
2021-01-31 04:20 | 0.5633 | 0.059013 | 0.044177 | 0.13463 | 13.8367 | 10.6925 | 1.2139 | 0 | 354.5981 | 25.89 | 70.54
2021-01-31 04:25 | 0.70414 | 0.057642 | 0.046282 | 0.13464 | 13.7756 | -3.298 | 1.2066 | 0.014626 | 354.0394 | 25.91 | 70.53
2021-01-31 04:30 | 0.62744 | 0.089224 | 0.052602 | 0.19147 | 5.7263 | 9.5371 | 1.2141 | 0.029257 | 352.8653 | 25.96 | 70.84
2021-01-31 04:35 | 0.66589 | 0.15512 | 0.058918 | 0.29669 | 10.7465 | 23.3165 | 1.2142 | 0.051202 | 354.8537 | 26.04 | 70.67
2021-01-31 04:40 | 0.33295 | 0.13179 | 0.071544 | 0.27355 | 10.5315 | -7.6527 | 1.2069 | 0 | 352.1736 | 26.08 | 70.54
2021-01-31 04:45 | 0.64027 | 0.13727 | 0.063125 | 0.27354 | 21.2467 | 15.5918 | 1.1923 | 0.029258 | 353.2238 | 26.09 | 70.41
2021-01-31 04:50 | 0.6147 | 0.17984 | 0.069443 | 0.34721 | 12.3247 | 16.3305 | 1.1923 | 0.036575 | 353.6793 | 26.13 | 70.43
2021-01-31 04:55 | 0.67872 | 0.12081 | 0.067337 | 0.25462 | 8.6569 | 14.9574 | 1.1996 | 0.036574 | 353.6854 | 26.13 | 70.38
2021-01-31 05:00 | 0.76829 | 0.14001 | 0.065226 | 0.27774 | 11.7394 | 6.8838 | 1.2068 | 0.080455 | 352.7153 | 26.09 | 70.27
2021-01-31 05:05 | 0.92216 | 0.32403 | 0.10102 | 0.5977 | 11.0966 | 30.5951 | 1.2144 | 0.029263 | 353.0651 | 26.17 | 70.6
2021-01-31 05:10 | 0.78127 | 0.25538 | 0.092601 | 0.48405 | 21.1173 | 9.3752 | 1.1998 | 0.036579 | 353.5677 | 26.19 | 70.51
2021-01-31 05:15 | 0.71715 | 0.23475 | 0.082069 | 0.44191 | 15.9003 | 1.0143 | 1.1997 | 0.05852 | 353.642 | 26.16 | 70.32
2021-01-31 05:20 | 0.96058 | 0.25126 | 0.10102 | 0.48616 | 14.4881 | 15.9021 | 1.2071 | 0.080474 | 354.1267 | 26.16 | 70.65
2021-01-31 05:25 | 0.87102 | 0.25128 | 0.084192 | 0.46937 | 24.6754 | 27.0836 | 1.2292 | 0.095115 | 352.5136 | 26.16 | 70.95
2021-01-31 05:30 | 0.97358 | 0.22247 | 0.092619 | 0.43573 | 21.962 | 23.5812 | 1.2366 | 0.08049 | 352.4336 | 26.2 | 71.05
2021-01-31 05:35 | 1.2299 | 0.26782 | 0.10947 | 0.51999 | 33.659 | 18.8281 | 1.2368 | 0.080499 | 352.6645 | 26.27 | 71.15
2021-01-31 05:40 | 0.90971 | 0.30493 | 0.10948 | 0.57688 | 34.318 | 50.0727 | 1.2295 | 0.043912 | 352.5746 | 26.32 | 71.19
2021-01-31 05:45 | 1.0893 | 0.47669 | 0.12424 | 0.85492 | 28.5512 | 20.3293 | 1.2224 | 0.080518 | 352.9781 | 26.38 | 71.35
2021-01-31 05:50 | 1.0894 | 0.4369 | 0.1074 | 0.77709 | 39.3197 | 19.9726 | 1.2225 | 0.065885 | 350.7932 | 26.42 | 71.48
2021-01-31 05:55 | 0.66642 | 0.35995 | 0.10319 | 0.65493 | 32.3368 | 30.0915 | 1.2298 | 0.080524 | 352.4001 | 26.4 | 71.5
2021-01-31 06:00 | 0.69204 | 0.35307 | 0.10319 | 0.64229 | 16.9679 | 20.7613 | 1.2371 | 0.065882 | 352.4171 | 26.39 | 71.5
2021-01-31 06:05 | 0.75617 | 0.36134 | 0.11372 | 0.6676 | 27.9296 | 27.1811 | 1.2372 | 0.051245 | 353.4438 | 26.39 | 71.69
2021-01-31 06:10 | 0.7818 | 0.26379 | 0.10951 | 0.51175 | 16.4767 | 12.6523 | 1.2372 | 0.036604 | 351.8828 | 26.38 | 71.71
2021-01-31 06:15 | 0.78167 | 0.2143 | 0.08212 | 0.4106 | 16.146 | 11.2971 | 1.237 | 0.036598 | 352.5362 | 26.32 | 71.5
2021-01-31 06:20 | 1.6402 | 0.2871 | 0.084226 | 0.52431 | 17.1302 | 19.6623 | 1.237 | 0.087835 | 353.6207 | 26.29 | 71.64
2021-01-31 06:25 | 2.2168 | 0.28571 | 0.088432 | 0.52428 | 13.8387 | 4.8487 | 1.2443 | 0.14638 | 352.5776 | 26.3 | 71.44
2021-01-31 06:30 | 2.4853 | 0.19364 | 0.092622 | 0.38943 | 24.9449 | 21.5014 | 1.2513 | 0.20489 | 354.0767 | 26.29 | 70.89
2021-01-31 06:35 | 2.4981 | 0.21149 | 0.096832 | 0.42101 | 23.1001 | 30.6224 | 1.2513 | 0.13171 | 353.5398 | 26.3 | 70.84
2021-01-31 06:40 | 3.0237 | 0.27882 | 0.10527 | 0.53265 | 16.6766 | 13.8681 | 1.2515 | 0.20492 | 353.4553 | 26.33 | 71.11
2021-01-31 06:45 | 3.6011 | 0.41489 | 0.11161 | 0.74756 | 30.48 | 11.7388 | 1.2664 | 0.24156 | 352.2398 | 26.4 | 71.47
2021-01-31 06:50 | 3.1147 | 0.49328 | 0.1011 | 0.85721 | 25.9119 | 29.2444 | 1.2593 | 0.17571 | 352.6466 | 26.45 | 71.74
2021-01-31 06:55 | 2.2558 | 0.49464 | 0.11162 | 0.87194 | 32.8326 | 29.4488 | 1.2592 | 0.16839 | 352.6313 | 26.47 | 71.59
2021-01-31 07:00 | 1.9475 | 0.37085 | 0.10316 | 0.67372 | 27.8188 | 13.6121 | 1.2588 | 0.10978 | 352.8162 | 26.42 | 70.79
2021-01-31 07:05 | 1.4478 | 0.31453 | 0.10316 | 0.58529 | 22.2938 | 21.9556 | 1.2368 | 0.043911 | 353.3445 | 26.42 | 70.77
2021-01-31 07:10 | 1.0764 | 0.20742 | 0.086329 | 0.40427 | 28.0267 | 25.3717 | 1.2223 | 0.058555 | 352.744 | 26.45 | 70.96
2021-01-31 07:15 | 1.4605 | 0.20601 | 0.092628 | 0.40841 | 21.2056 | 1.8449 | 1.2221 | 0.087815 | 352.8354 | 26.43 | 70.5
2021-01-31 07:20 | 1.2681 | 0.22656 | 0.092609 | 0.43989 | 9.3659 | 15.5961 | 1.2365 | 0.095114 | 353.4098 | 26.45 | 69.84
2021-01-31 07:25 | 1.6138 | 0.29245 | 0.088392 | 0.53456 | 17.2341 | 18.4739 | 1.2437 | 0.095105 | 353.9563 | 26.46 | 69.54
2021-01-31 07:30 | 1.511 | 0.28003 | 0.096789 | 0.52603 | 6.6074 | 3.2268 | 1.2507 | 0.080456 | 355.1087 | 26.44 | 69.01
2021-01-31 07:35 | 1.9462 | 0.35412 | 0.12624 | 0.66905 | 11.165 | 2.0384 | 1.2506 | 0.051195 | 354.0628 | 26.46 | 68.69
2021-01-31 07:40 | 1.8565 | 0.41038 | 0.13885 | 0.7679 | 21.4276 | 26.385 | 1.2286 | 0.073132 | 353.5056 | 26.5 | 68.4
2021-01-31 07:45 | 2.0872 | 0.40907 | 0.14098 | 0.76801 | 14.0754 | 23.0799 | 1.2142 | 0.087771 | 354.4361 | 26.56 | 68.56
2021-01-31 07:50 | 1.9208 | 0.42554 | 0.14519 | 0.79747 | 23.961 | 7.5294 | 1.2142 | 0.11703 | 353.8615 | 26.6 | 68.41
2021-01-31 07:55 | 3.2781 | 0.44339 | 0.14519 | 0.82272 | 22.906 | 19.7918 | 1.2288 | 0.1536 | 353.6403 | 26.64 | 68.33
2021-01-31 08:00 | 3.7388 | 0.39393 | 0.13886 | 0.7448 | 26.663 | 28.1688 | 1.2433 | 0.1609 | 354.1889 | 26.65 | 68.02
2021-01-31 08:05 | 2.9316 | 0.52011 | 0.14515 | 0.9445 | 38.8145 | 24.6508 | 1.2431 | 0.13162 | 353.1667 | 26.68 | 67.38
2021-01-31 08:10 | 2.6627 | 0.49678 | 0.16408 | 0.92556 | 19.059 | 5.7556 | 1.2431 | 0.087747 | 352.6417 | 26.68 | 67.37
2021-01-31 08:15 | 2.2019 | 0.49266 | 0.1767 | 0.93187 | 25.0089 | 21.6908 | 1.2284 | 0.12431 | 352.6442 | 26.68 | 67.35
2021-01-31 08:20 | 2.4958 | 0.48021 | 0.12829 | 0.86438 | 15.7784 | 5.9079 | 1.2136 | 0.19739 | 353.2309 | 26.69 | 66.74
2021-01-31 08:25 | 2.7518 | 0.46375 | 0.11357 | 0.82653 | 26.1098 | 19.0755 | 1.2209 | 0.2705 | 354.2461 | 26.72 | 66.64
2021-01-31 08:30 | 3.1227 | 0.48841 | 0.13459 | 0.88534 | 30.8172 | 26.8857 | 1.2281 | 0.32896 | 353.1759 | 26.76 | 66.25
2021-01-31 08:35 | 3.3532 | 0.54742 | 0.1388 | 0.98002 | 21.1532 | 49.8217 | 1.2574 | 0.32166 | 352.0255 | 26.83 | 66.1
2021-01-31 08:40 | 3.3406 | 0.57352 | 0.18928 | 1.0684 | 34.8853 | 12.3691 | 1.2575 | 0.18277 | 353.011 | 26.87 | 66.1
2021-01-31 08:45 | 2.9687 | 0.55144 | 0.17452 | 1.0198 | 27.3527 | 30.0552 | 1.2352 | 0.14618 | 353.0863 | 26.88 | 65.38
2021-01-31 08:50 | 3.8003 | 0.64743 | 0.19974 | 1.1943 | 34.6707 | 45.8181 | 1.2206 | 0.27773 | 354.1168 | 26.91 | 65.16
2021-01-31 08:55 | 4.0429 | 0.75297 | 0.185 | 1.3392 | 52.8651 | 44.6359 | 1.2277 | 0.34347 | 354.0976 | 26.96 | 64.66
2021-01-31 09:00 | 3.7361 | 0.73108 | 0.15769 | 1.2804 | 50.3509 | 37.5661 | 1.2205 | 0.33619 | 353.977 | 27.04 | 64.56
2021-01-31 09:05 | 3.5186 | 0.64739 | 0.18922 | 1.1816 | 39.6535 | 38.0464 | 1.2205 | 0.32888 | 354.4748 | 27.07 | 64.39
2021-01-31 09:10 | 3.1085 | 0.59104 | 0.17867 | 1.0846 | 35.9001 | 29.5449 | 1.2349 | 0.26305 | 355.0352 | 27.1 | 63.74
2021-01-31 09:15 | 2.5073 | 0.44569 | 0.16186 | 0.84503 | 28.1639 | 10.6433 | 1.2495 | 0.18998 | 352.3519 | 27.14 | 63.64
2021-01-31 09:20 | 2.6349 | 0.42643 | 0.14082 | 0.79446 | 26.4919 | 30.4314 | 1.2566 | 0.19726 | 353.969 | 27.15 | 63.21
2021-01-31 09:25 | 2.7881 | 0.53881 | 0.17863 | 1.0045 | 31.7483 | 34.5722 | 1.2638 | 0.21185 | 354.5174 | 27.16 | 62.91
2021-01-31 09:30 | 2.9797 | 0.67587 | 0.17442 | 1.2104 | 32.084 | 32.6057 | 1.2637 | 0.22645 | 354.5042 | 27.19 | 62.63
2021-01-31 09:35 | 4.1182 | 1.1955 | 0.2774 | 2.1099 | 61.0816 | 51.5255 | 1.2638 | 0.24838 | 355.8322 | 27.24 | 62.66
2021-01-31 09:40 | 4.1566 | 1.0845 | 0.26059 | 1.9229 | 61.277 | 81.2593 | 1.2638 | 0.25569 | 353.6975 | 27.26 | 62.63
2021-01-31 09:45 | 5.7165 | 0.95828 | 0.24587 | 1.7169 | 70.8486 | 58.7967 | 1.2856 | 0.4602 | 353.6997 | 27.28 | 62.36
2021-01-31 09:50 | 5.6913 | 0.74722 | 0.22067 | 1.366 | 71.3042 | 36.4144 | 1.2784 | 0.35066 | 354.678 | 27.32 | 62.42
2021-01-31 09:55 | 5.9863 | 0.73086 | 0.20598 | 1.3263 | 50.6225 | 46.4883 | 1.2859 | 0.46761 | 355.1581 | 27.32 | 62.77
2021-01-31 10:00 | 4.5659 | 0.74311 | 0.20596 | 1.345 | 51.0771 | 47.0458 | 1.2785 | 0.32875 | 354.1226 | 27.34 | 62.39
2021-01-31 10:05 | 4.0417 | 0.73217 | 0.23329 | 1.3556 | 48.122 | 20.3007 | 1.2639 | 0.33607 | 353.0332 | 27.36 | 62.42
2021-01-31 10:10 | 3.6708 | 0.87889 | 0.23959 | 1.5868 | 49.7596 | 46.2806 | 1.2639 | 0.36529 | 352.4805 | 27.38 | 62.37
2021-01-31 10:15 | 3.312 | 0.88419 | 0.20172 | 1.557 | 40.0201 | 38.3423 | 1.2709 | 0.29948 | 353.0941 | 27.37 | 61.83
2021-01-31 10:20 | 3.44 | 0.94867 | 0.22905 | 1.6832 | 37.5259 | 15.6835 | 1.271 | 0.27758 | 353.578 | 27.39 | 61.9
2021-01-31 10:25 | 3.2352 | 0.8636 | 0.23534 | 1.5591 | 41.2775 | 34.8838 | 1.249 | 0.22643 | 354.0955 | 27.42 | 61.59
2021-01-31 10:30 | 3.4523 | 0.87451 | 0.24162 | 1.5821 | 35.3109 | 40.8551 | 1.2343 | 0.21911 | 354.1444 | 27.4 | 61.47
2021-01-31 10:35 | 3.6949 | 0.87443 | 0.22899 | 1.5693 | 38.8773 | 33.2211 | 1.2342 | 0.2483 | 354.1887 | 27.39 | 61.26
2021-01-31 10:40 | 3.3877 | 0.79895 | 0.22687 | 1.4515 | 38.4433 | 12.8963 | 1.2268 | 0.22636 | 354.2058 | 27.41 | 60.88
2021-01-31 10:45 | 3.3368 | 0.7209 | 0.20378 | 1.3067 | 27.0425 | 32.4122 | 1.2415 | 0.24829 | 353.1229 | 27.41 | 61.11
2021-01-31 10:50 | 4.2698 | 0.87571 | 0.25838 | 1.6007 | 38.362 | 44.6516 | 1.2487 | 0.28478 | 353.6518 | 27.43 | 60.84
2021-01-31 10:55 | 4.1938 | 0.90601 | 0.28364 | 1.6724 | 33.0801 | 7.7739 | 1.2562 | 0.32135 | 354.0473 | 27.49 | 61.08
2021-01-31 11:00 | 3.8232 | 0.91839 | 0.29625 | 1.704 | 44.3236 | 55.8008 | 1.2708 | 0.31406 | 353.9615 | 27.55 | 60.98
2021-01-31 11:05 | 2.9789 | 0.7538 | 0.27101 | 1.4265 | 47.3759 | 36.1661 | 1.2561 | 0.20448 | 354.5341 | 27.55 | 60.63
2021-01-31 11:10 | 3.0299 | 0.74418 | 0.24789 | 1.3886 | 38.1387 | 17.9801 | 1.2633 | 0.25559 | 354.0674 | 27.51 | 60.68
2021-01-31 11:15 | 4.0399 | 0.88945 | 0.2815 | 1.6449 | 38.108 | 31.2965 | 1.2487 | 0.45276 | 353.5413 | 27.51 | 60.68
2021-01-31 11:20 | 4.8074 | 0.97724 | 0.29413 | 1.7921 | 52.3592 |  | 1.2342 | 0.54043 | 353.4077 | 27.6 | 60.57
2021-01-31 11:25 | 4.756 | 1.0142 | 0.31092 | 1.8655 | 50.5878 | 28.4851 | 1.2415 | 0.64995 | 352.2986 | 27.66 | 60.26
2021-01-31 11:30 | 4.9473 | 0.95244 | 0.29409 | 1.754 | 44.0683 | 20.3518 | 1.2633 | 0.56226 | 353.8515 | 27.71 | 59.83
2021-01-31 11:35 | 4.1809 | 0.86075 | 0.26051 | 1.582 | 39.7376 | 38.6431 | 1.2634 | 0.42358 | 352.7158 | 27.74 | 60.09
2021-01-31 11:40 | 5.0621 | 0.86058 | 0.28777 | 1.6069 | 37.8278 | 43.7183 | 1.2705 | 0.32128 | 352.7952 | 27.73 | 59.62
2021-01-31 11:45 | 5.3423 | 0.93439 | 0.27511 | 1.7053 | 37.6465 | 12.433 | 1.2702 | 0.29931 | 352.8882 | 27.71 | 59.17
2021-01-31 11:50 | 4.6775 | 0.85489 | 0.231 | 1.5414 | 33.238 | 23.832 | 1.2775 | 0.2774 | 353.9823 | 27.69 | 59.1
2021-01-31 11:55 | 3.7953 | 0.84797 | 0.25828 | 1.5581 | 38.3571 | 44.3989 | 1.2774 | 0.20438 | 353.5324 | 27.65 | 59.02
2021-01-31 12:00 | 3.7954 | 0.93566 | 0.25619 | 1.6904 | 36.9166 | 28.6663 | 1.2701 | 0.18979 | 353.5465 | 27.63 | 59.16
2021-01-31 12:05 | 4.434 | 1.1904 | 0.28976 | 2.1165 | 49.3742 | 43.9154 | 1.27 | 0.27006 | 353.5565 | 27.65 | 58.84
2021-01-31 12:10 | 3.6928 | 0.95611 | 0.26456 | 1.7301 | 56.0487 | 47.646 | 1.27 | 0.22626 | 354.5784 | 27.68 | 58.7
2021-01-31 12:15 | 4.0376 | 0.88209 | 0.24775 | 1.5977 | 40.0078 | 32.7401 |  |  | 353.5806 | 27.65 | 58.66
2021-01-31 12:20 | 3.9479 | 0.90259 | 0.20994 | 1.5935 | 54.3051 | 43.6137 | 1.2625 | 0.20434 | 353.5993 | 27.65 | 58.52
2021-01-31 12:25 | 5.5327 | 0.87116 | 0.27085 | 1.6041 | 58.603 | 66.1162 | 1.2699 | 0.24815 | 354.5974 | 27.67 | 58.68
2021-01-31 12:30 | 6.1572 | 0.82849 | 0.26028 | 1.5302 | 44.291 | 47.3773 | 1.2769 | 0.31376 | 354.1857 | 27.65 | 58.07
2021-01-31 12:35 | 5.9653 | 0.79969 | 0.26027 | 1.4861 | 48.9691 | 21.613 | 1.2769 | 0.32833 | 354.6938 | 27.68 | 57.84
2021-01-31 12:40 | 4.6878 | 0.72436 | 0.24348 | 1.3538 | 37.329 | 22.7469 | 1.2768 | 0.22618 | 352.0462 | 27.7 | 57.72
2021-01-31 12:45 | 4.6871 | 0.78449 | 0.24344 | 1.4459 | 33.226 | 22.2426 | 1.2547 | 0.23344 | 352.1374 | 27.67 | 57.4
2021-01-31 12:50 | 4.1886 | 0.84327 | 0.28118 | 1.5738 | 30.311 | 33.621 | 1.24 | 0.27718 | 352.7471 | 27.63 | 57.26
2021-01-31 12:55 | 4.6882 | 1.012 | 0.30856 | 1.8577 | 27.6742 | 21.9104 | 1.2331 | 0.30646 | 354.7476 | 27.62 | 58.17
2021-01-31 13:00 | 3.4742 | 0.93383 | 0.28125 | 1.7127 | 38.4209 | 36.1013 | 1.233 | 0.26995 | 355.2649 | 27.66 | 57.75
2021-01-31 13:05 | 4.062 | 0.93388 | 0.30435 | 1.7337 | 39.077 | 43.5222 | 1.255 | 0.32104 | 352.6377 | 27.64 | 57.96
2021-01-31 13:10 | 3.5889 | 0.77082 | 0.25604 | 1.4376 | 35.7814 | 12.1587 | 1.2621 | 0.26992 | 354.8528 | 27.59 | 57.75
2021-01-31 13:15 | 4.1642 | 0.81612 | 0.25607 | 1.5091 | 44.7482 | 50.9203 | 1.2622 | 0.28455 | 354.2659 | 27.6 | 58.08
2021-01-31 13:20 | 4.1514 | 0.7367 | 0.24978 | 1.3811 | 44.9427 | 54.9061 | 1.2623 | 0.24807 | 354.2632 | 27.6 | 58.1
2021-01-31 13:25 | 4.1505 | 0.80362 | 0.26441 | 1.4962 | 39.1193 | 22.834 | 1.2693 | 0.25531 | 354.9054 | 27.57 | 57.6
2021-01-31 13:30 | 3.6918 | 0.76414 | 0.24559 | 1.4169 | 36.7393 | 7.215 | 1.255 | 0.19701 | 353.2111 | 27.58 | 58.34
2021-01-31 13:35 | 3.8714 | 0.91221 | 0.24984 | 1.6481 | 25.1858 | 35.2847 | 1.248 | 0.29922 | 354.2193 | 27.56 | 58.92
2021-01-31 13:40 | 3.743 | 0.84907 | 0.23511 | 1.5366 | 24.4256 | 31.0072 | 1.2405 | 0.26999 | 354.7783 | 27.58 | 58.43
2021-01-31 13:45 | 4.4974 | 0.82729 | 0.21205 | 1.4822 | 24.8688 | 19.0937 | 1.2334 | 0.27003 | 354.7235 | 27.58 | 58.84
2021-01-31 13:50 | 4.8032 | 0.78467 | 0.20571 | 1.4085 | 38.272 | 20.8273 | 1.2331 | 0.32106 | 354.7806 | 27.59 | 58.29
2021-01-31 13:55 | 4.9566 | 0.82852 | 0.20992 | 1.4799 | 44.0475 | 56.6179 | 1.2405 | 0.26999 | 354.2066 | 27.62 | 58.28
2021-01-31 14:00 | 4.3561 | 0.87232 | 0.2288 | 1.5638 | 37.3931 | 46.6213 | 1.2331 | 0.24809 | 354.1953 | 27.64 | 58.12
2021-01-31 14:05 | 3.5636 | 0.84756 | 0.23507 | 1.5321 | 37.1025 | 2.3706 | 1.2257 | 0.24806 | 355.2909 | 27.64 | 57.8
2021-01-31 14:10 | 3.5648 | 0.87523 | 0.24774 | 1.5893 | 32.9544 | 18.8486 | 1.2188 | 0.27003 | 355.1755 | 27.64 | 58.66
2021-01-31 14:15 | 3.5909 | 0.88771 | 0.27088 | 1.6337 | 26.9894 | 47.6916 | 1.2263 | 0.30658 | 354.0643 | 27.64 | 59.1
2021-01-31 14:20 | 3.8601 | 1.0181 | 0.26464 | 1.8251 | 43.8258 | 15.4914 | 1.2485 | 0.25553 | 355.0093 | 27.67 | 59.53
2021-01-31 14:25 | 3.3872 | 0.98108 | 0.25414 | 1.758 | 37.9776 | 37.1494 | 1.2339 | 0.24093 | 353.9507 | 27.67 | 59.58
2021-01-31 14:30 | 3.5269 | 0.76987 | 0.20998 | 1.3901 | 34.5945 | 33.7256 | 1.2336 | 0.24087 | 355.1507 | 27.62 | 59.09
2021-01-31 14:35 | 3.7947 | 0.73004 | 0.23094 | 1.3521 | 40.2114 | 39.2915 | 1.2553 | 0.24084 | 355.225 | 27.6 | 58.78
2021-01-31 14:40 | 3.7819 | 0.73689 | 0.25194 | 1.3815 | 31.6661 | 16.7632 | 1.2553 | 0.21165 | 352.6306 | 27.57 | 58.87
2021-01-31 14:45 | 4.5994 | 0.85875 | 0.25403 | 1.5724 | 37.1431 | 14.105 | 1.2625 | 0.27732 | 353.6992 | 27.57 | 58.75
2021-01-31 14:50 | 6.1216 | 0.91106 | 0.2667 | 1.6632 | 37.2563 | 45.7422 | 1.2702 | 0.3285 | 353.0335 | 27.6 | 59.43
2021-01-31 14:55 | 6.0695 | 0.99583 | 0.24986 | 1.7742 | 42.361 | 69.3784 | 1.2773 | 0.37223 | 354.6141 | 27.65 | 58.8
2021-01-31 15:00 | 5.7626 | 1.0136 | 0.24565 | 1.7994 | 61.4953 | 42.1554 | 1.2772 | 0.34303 | 353.5246 | 27.69 | 58.59
2021-01-31 15:05 | 3.7177 | 0.92308 | 0.24142 | 1.6563 | 66.791 | 61.6603 | 1.2625 | 0.27001 | 354.1482 | 27.65 | 58.35
2021-01-31 15:10 | 3.7686 | 0.89838 | 0.28129 | 1.6584 | 49.7099 | 52.3773 | 1.2624 | 0.2554 | 353.6996 | 27.6 | 58.38
2021-01-31 15:15 | 3.9234 | 0.97407 | 0.2814 | 1.7745 | 46.3242 | 45.4961 | 1.2629 | 0.27739 | 354.08 | 27.61 | 59.35
2021-01-31 15:20 | 4.0521 | 0.9647 | 0.30247 | 1.7812 | 42.6638 | 12.7726 | 1.2632 | 0.27746 | 354.5232 | 27.61 | 59.97
2021-01-31 15:25 | 4.9583 | 0.90963 | 0.24359 | 1.6379 | 32.8681 | 36.2214 | 1.2701 | 0.28468 | 354.6222 | 27.61 | 59.23
2021-01-31 15:30 | 4.3693 | 0.7738 | 0.20783 | 1.3918 | 37.3154 | 28.7812 | 1.2625 | 0.24082 | 354.2279 | 27.58 | 58.61
2021-01-31 15:35 | [9 empty] | 27.55 | 58.6
2021-01-31 15:40 | 5.711 | 0.70262 | 0.17845 | 1.2533 | 24.694 | 8.7901 | 1.2698 | 0.30651 | 354.3844 | 27.58 | 58.67
2021-01-31 15:45 | 4.8562 | 0.72196 | 0.19739 | 1.3019 | 26.1415 | 24.5773 | 1.2701 | 0.27008 | 353.2366 | 27.59 | 59.27
2021-01-31 15:50 | 5.2267 | 0.77265 | 0.23939 | 1.4237 | 22.1439 | 33.2364 | 1.2847 | 0.33578 | 354.7803 | 27.62 | 59.15
2021-01-31 15:55 | 4.562 | 0.84111 | 0.25618 | 1.5455 | 28.2157 | 16.6943 | 1.2847 | 0.29197 | 353.7411 | 27.62 | 59.06
2021-01-31 16:00 | 3.9229 | 0.78764 | 0.22887 | 1.4362 | 31.0966 | 35.0425 | 1.2846 | 0.25546 | 353.7405 | 27.64 | 58.82
2021-01-31 16:05 | 4.2541 | 0.82992 | 0.21622 | 1.4883 | 29.9348 | 41.6777 | 1.2843 | 0.27 | 353.8194 | 27.64 | 58.23
2021-01-31 16:10 | 4.3561 | 0.84219 | 0.2288 | 1.5197 | 30.4337 | 27.2555 | 1.2696 | 0.24809 | 352.7893 | 27.64 | 58.07
2021-01-31 16:15 | 3.9602 | 0.75593 | 0.22251 | 1.3812 | 30.8738 | 12.1615 | 1.2405 | 0.21161 | 354.9199 | 27.61 | 58.23
2021-01-31 16:20 | 4.4189 | 0.75573 | 0.22245 | 1.3809 | 29.1492 | 36.4544 | 1.2256 | 0.32098 | 353.9741 | 27.6 | 57.56
2021-01-31 16:25 | 5.3775 | 0.79282 | 0.23508 | 1.4503 | 38.1972 | 34.774 | 1.2476 | 0.26996 | 353.358 | 27.63 | 57.87
2021-01-31 16:30 | 4.2791 | 0.7942 | 0.23718 | 1.4545 | 35.2851 | 24.1161 | 1.2476 | 0.27725 | 353.3444 | 27.64 | 57.85
2021-01-31 16:35 | 4.7643 | 0.77637 | 0.25606 | 1.444 | 37.7567 | 22.511 | 1.2476 | 0.24076 | 353.8823 | 27.64 | 57.76
2021-01-31 16:40 | 4.1128 | 0.70105 | 0.22037 | 1.2971 | 55.0962 | 66.8471 | 1.2403 | 0.21887 | 353.8767 | 27.65 | 57.68
2021-01-31 16:45 | 4.65 | 0.7532 | 0.22671 | 1.3812 | 52.0391 | 51.9982 | 1.2478 | 0.27728 | 354.3106 | 27.68 | 58
2021-01-31 16:50 | 4.42 | 0.65458 | 0.233 | 1.2364 | 59.8254 | 22.2684 | 1.2477 | 0.21161 | 353.7685 | 27.7 | 57.88
2021-01-31 16:55 | 5.3268 | 0.62991 | 0.2246 | 1.1901 | 57.4217 | 47.6419 | 1.2331 | 0.2189 | 354.8209 | 27.71 | 57.75
2021-01-31 17:00 | 4.2147 | 0.65855 | 0.25394 | 1.2634 | 58.7093 | 68.4976 | 1.2329 | 0.27722 | 353.3056 | 27.71 | 57.29
2021-01-31 17:05 | 4.599 | 0.74774 | 0.20152 | 1.3456 | 59.9817 | 33.6241 | 1.2478 | 0.27729 | 353.7387 | 27.71 | 57.98
2021-01-31 17:10 | 5.2793 | 0.78519 | 0.18064 | 1.3863 | 43.0729 | 16.6995 | 1.2559 | 0.27016 | 352.487 | 27.7 | 59.6
2021-01-31 17:15 | 6.2765 | 0.72217 | 0.17854 | 1.2855 | 39.249 | 44.3009 | 1.2632 | 0.26286 | 354.6175 | 27.67 | 59.75
2021-01-31 17:20 | 5.7899 | 0.64123 | 0.19742 | 1.1803 | 44.4887 | 41.7995 | 1.2557 | 0.23362 | 354.132 | 27.68 | 59.33
2021-01-31 17:25 | 2.977 | 0.53829 | 0.18686 | 1.012 | 28.8759 | 19.789 | 1.2553 | 0.14596 | 355.1521 | 27.66 | 58.59
2021-01-31 17:30 | 3.1553 | 0.56694 | 0.19941 | 1.0684 | 35.9525 | 32.6311 | 1.2477 | 0.16783 | 353.6896 | 27.62 | 58.21
2021-01-31 17:35 | 4.3181 | 0.60671 | 0.20993 | 1.1399 | 42.1082 | 26.614 | 1.2333 | 0.22622 | 354.7005 | 27.63 | 58.4
2021-01-31 17:40 | 5.7102 | 0.6765 | 0.20361 | 1.2385 | 32.4577 | 30.567 | 1.2332 | 0.25539 | 355.8033 | 27.61 | 58.27
2021-01-31 17:45 | 3.1674 | 0.71606 | 0.19308 | 1.2907 | 32.4301 | 6.0691 | 1.2402 | 0.2991 | 355.3792 | 27.59 | 57.75
2021-01-31 17:50 | 5.71 | 0.71892 | 0.19521 | 1.2951 | 31.0868 | 7.4191 | 1.2477 | 0.28456 | 354.8146 | 27.57 | 58.28
2021-01-31 17:55 | 2.8866 | 0.66682 | 0.1847 | 1.2068 | 22.5823 |  | 1.2476 | 0.28454 | 354.3338 | 27.56 | 58.06
2021-01-31 18:00 | 3.4746 | 0.61349 | 0.19731 | 1.1377 | 24.0464 | 15.6153 | 1.255 | 0.2262 | 355.3675 | 27.54 | 58.45
2021-01-31 18:05 | 3.2076 | 0.60277 | 0.22259 | 1.1486 | 27.3169 | 10.3052 | 1.2555 | 0.17519 | 353.6871 | 27.51 | 59.58
2021-01-31 18:10 | 2.4665 | 0.77542 | 0.2457 | 1.4343 | 38.2576 | 53.0003 | 1.2556 | 0.1533 | 353.7542 | 27.44 | 59.94
2021-01-31 18:15 | 3.5786 | 0.75217 | 0.22471 | 1.3756 | 41.1433 | 26.9108 | 1.2629 | 0.1022 | 355.3584 | 27.4 | 60.25
2021-01-31 18:20 | 4.0013 | 0.7085 | 0.18485 | 1.2709 | 38.1465 | 30.0467 | 1.2486 | 0.12413 | 354.2084 | 27.41 | 60.86
2021-01-31 18:25 | 4.0523 | 0.6893 | 0.17435 | 1.233 | 32.2653 | 25.3623 | 1.234 | 0.16794 | 353.7599 | 27.35 | 61.02
2021-01-31 18:30 | 3.8354 | 0.7017 | 0.17856 | 1.252 | 33.7921 | 26.5714 | 1.2487 | 0.22638 | 353.7759 | 27.31 | 61.4
2021-01-31 18:35 | 3.8358 | 0.63325 | 0.18279 | 1.1535 | 20.5907 | 30.0523 | 1.2635 | 0.25562 | 355.8395 | 27.31 | 61.72
2021-01-31 18:40 | 3.209 | 0.67568 | 0.18907 | 1.2248 | 23.1663 | 18.5637 | 1.2707 | 0.23369 | 354.8535 | 27.28 | 61.59
2021-01-31 18:45 | 4.5011 | 0.7183 | 0.1681 | 1.2691 | 28.8071 | 26.6691 | 1.2709 | 0.33599 | 354.8245 | 27.25 | 62.19
2021-01-31 18:50 | 3.9521 | 0.65538 | 0.14501 | 1.1496 | 24.4955 | 33.6839 | 1.2712 | 0.29223 | 354.7699 | 27.23 | 62.86
2021-01-31 18:55 | 3.5299 | 0.59639 | 0.16602 | 1.0802 | 43.5246 | 50.0523 | 1.2711 | 0.23377 | 356.4643 | 27.15 | 63
2021-01-31 19:00 | 4.2077 | 0.57994 | 0.1408 | 1.0298 | 64.8882 | 61.8597 | 1.2638 | 0.21185 | 355.9836 | 27.11 | 63.16
2021-01-31 19:05 | 2.5582 | 0.49775 | 0.1156 | 0.87647 | 58.0309 | 45.1067 | 1.264 | 0.17535 | 356.4964 | 27.08 | 63.65
2021-01-31 19:10 | 3.121 | 0.42781 | 0.11139 | 0.76505 | 45.6376 | 31.9668 | 1.2713 | 0.14612 | 355.8549 | 27.04 | 63.79
2021-01-31 19:15 | 3.556 | 0.52107 | 0.14083 | 0.93955 | 33.3192 | 41.9969 | 1.2713 | 0.17536 | 354.4525 | 27.02 | 63.94
2021-01-31 19:20 | 2.7374 | 0.48543 | 0.16395 | 0.91014 | 26.2897 | 8.3505 | 1.2714 | 0.13883 | 354.9701 | 27.02 | 64.01
2021-01-31 19:25 | 2.2895 | 0.38529 | 0.14082 | 0.72931 | 28.8557 | 9.2195 | 1.2712 | 0.10228 | 355.9075 | 27 | 63.9
2021-01-31 19:30 | 1.8034 | 0.30164 | 0.1219 | 0.58426 | 16.0232 | 24.2395 | 1.2712 | 0.058445 | 355.4829 | 26.93 | 64.01
2021-01-31 19:35 | 2.622 | 0.29753 | 0.124 | 0.58006 | 6.9987 | 25.7439 | 1.2566 | 0.080363 | 357.6468 | 26.88 | 64.24
2021-01-31 19:40 | 3.2741 | 0.25501 | 0.11979 | 0.51068 | 18.2839 | 1.0846 | 1.2565 | 0.1315 | 355.0606 | 26.85 | 64.23
2021-01-31 19:45 | 2.2129 | 0.27699 | 0.12611 | 0.55279 | 13.0574 | 21.8271 | 1.264 | 0.1169 | 356.0424 | 26.87 | 64.54
2021-01-31 19:50 | 2.891 | 0.34557 | 0.1072 | 0.6369 | 7.7059 | 13.3343 | 1.2714 | 0.094988 | 356.0128 | 26.88 | 64.64
2021-01-31 19:55 | 2.2129 | 0.37023 | 0.1114 | 0.67679 | 21.4583 | 5.6486 | 1.2567 | 0.094982 | 356.588 | 26.86 | 64.53
2021-01-31 20:00 | 2.5202 | 0.52935 | 0.14084 | 0.95225 | 18.9435 | 0.32749 | 1.2422 | 0.15345 | 356.0026 | 26.87 | 64.85
2021-01-31 20:05 | 3.7354 | 0.52934 | 0.15555 | 0.96695 | 20.2121 | 32.8613 | 1.2568 | 0.17537 | 355.9871 | 26.89 | 64.71
2021-01-31 20:10 | 2.7237 | 0.48252 | 0.15339 | 0.893 | 26.4132 | 33.9218 | 1.249 | 0.094952 | 355.1029 | 26.87 | 63.64
2021-01-31 20:15 | 2.7485 | 0.74275 | 0.096627 | 1.2351 | 21.7832 | -0.91019 | 1.234 | 0.15334 | 355.7549 | 26.85 | 62.93
2021-01-31 20:20 | 2.5173 | 0.98901 | 0.14068 | 1.6567 | 24.718 | 39.8167 | 1.2335 | 0.13138 | 355.9176 | 26.84 | 61.79
2021-01-31 20:25 | 2.2485 | 0.80529 | 0.14695 | 1.3813 | 32.1333 | 50.9901 | 1.2333 | 0.15325 | 356.0108 | 26.82 | 61.32
2021-01-31 20:30 | 1.8907 | 0.65597 | 0.10286 | 1.1084 | 34.6249 | 30.0669 | 1.2332 | 0.12405 | 356.6089 | 26.78 | 61.29
2021-01-31 20:35 | 2.593 | 0.4957 | 0.090255 | 0.85007 | 38.0652 | 14.2655 | 1.2331 | 0.094851 | 354.0857 | 26.71 | 61.26
2021-01-31 20:40 | 2.1463 | 0.41633 | 0.092367 | 0.73054 | 39.0109 | 30.1907 | 1.2332 | 0.094865 | 356.2084 | 26.66 | 61.84
2021-01-31 20:45 | 2.4014 | 0.28344 | 0.10285 | 0.53732 | 20.0692 | 19.5685 | 1.2257 | 0.10214 | 356.3047 | 26.63 | 61.47
2021-01-31 20:50 | 1.6605 | 0.23414 | 0.079755 | 0.43865 | 20.0991 | 14.7857 | 1.2184 | 0.11673 | 356.3301 | 26.62 | 61.4
2021-01-31 20:55 | 1.4692 | 0.23693 | 0.081871 | 0.44504 | 12.6119 | 6.9703 | 1.2187 | 0.13135 | 355.2566 | 26.57 | 62.18
2021-01-31 21:00 | 1.9413 | 0.24781 | 0.081847 | 0.4617 | 8.9095 | 26.5547 | 1.2256 | 0.16779 | 356.997 | 26.53 | 61.48
2021-01-31 21:05 | 1.4177 | 0.22317 | 0.077651 | 0.41974 | 19.5769 | -7.6019 | 1.2475 | 0.11673 | 356.4936 | 26.5 | 61.67
2021-01-31 21:10 | 1.5841 | 0.21775 | 0.073471 | 0.40724 | 1.9418 | -9.0753 | 1.2551 | 0.10216 | 355.9659 | 26.43 | 62.58
2021-01-31 21:15 | 1.4563 | 0.30676 | 0.058776 | 0.53109 | 9.1059 | 8.5029 | 1.2624 | 0.10216 | 356.5331 | 26.4 | 62.67
2021-01-31 21:20 | 2.159 | 0.29582 | 0.041985 | 0.49752 | 14.5435 | 13.2149 | 1.2624 | 0.10216 | 355.9995 | 26.39 | 62.84
2021-01-31 21:25 | 1.0986 | 0.24239 | 0.079766 | 0.45131 | 2.6571 | 4.8339 | 1.2551 | 0.014594 | 355.5541 | 26.34 | 62.83
2021-01-31 21:30 | 1.9034 | 0.22047 | 0.073468 | 0.41142 | 11.0063 | -6.3361 | 1.2404 | 0.029187 | 356.666 | 26.3 | 62.93
2021-01-31 21:35 | 1.6607 | 0.18214 | 0.069272 | 0.34846 | 5.1201 | 1.1446 | 1.2259 | 0.051079 | 357.2535 | 26.24 | 63.26
2021-01-31 21:40 | 1.2645 | 0.16704 | 0.062963 | 0.31901 | 2.391 | 2.5852 | 1.233 | 0.10214 | 356.3902 | 26.13 | 63.15
2021-01-31 21:45 | 0.67698 | 0.20266 | 0.073462 | 0.3841 | 5.8451 |  | 1.2476 | 0.080257 | 355.8861 | 26.09 | 63.48
2021-01-31 21:50 | 1.2136 | 0.16982 | 0.060877 | 0.32118 | 0.22484 | 2.1871 | 1.2551 | 0.05108 | 355.8591 | 26.07 | 63.97
2021-01-31 21:55 | 1.2772 | 0.12049 | 0.06506 | 0.24975 | 6.0285 | 4.6695 | 1.2548 | 0.043773 | 357.0598 | 26.02 | 63.49
2021-01-31 22:00 | 1.6605 | 0.13008 | 0.060868 | 0.25817 | 5.8553 | -1.778 | 1.2549 | 0.051073 | 356.5577 | 25.97 | 63.94
2021-01-31 22:05 | 1.0985 | 0.12324 | 0.050376 | 0.23718 | 0.4292 | -15.8599 | 1.255 | 0.036482 | 356.0519 | 25.94 | 64.15
2021-01-31 22:10 | 0.89407 | 0.14924 | 0.05037 | 0.27704 | 10.126 | 17.0128 | 1.2548 | 0.051069 | 356.1245 | 25.91 | 63.96
2021-01-31 22:15 | 1.4817 | 0.16295 | 0.044078 | 0.29595 | 2.8204 | 14.5109 | 1.255 | 0.13133 | 356.5959 | 25.93 | 64.17
2021-01-31 22:20 | 2.2607 | 0.20675 | 0.054568 | 0.37148 | 0.58242 | -4.0565 | 1.2621 | 0.1605 | 356.0779 | 25.95 | 63.8
2021-01-31 22:25 | 1.4561 | 0.15609 | 0.062963 | 0.30222 | 13.2527 | 2.9121 | 1.2549 | 0.094843 | 355.0506 | 25.92 | 63.94
2021-01-31 22:30 | 0.91964 | 0.1246 | 0.052471 | 0.24346 | 5.947 | 1.8904 | 1.2622 | 0.072958 | 355.6198 | 25.88 | 64.16
2021-01-31 22:35 | 1.9923 | 0.18482 | 0.058759 | 0.34206 | -5.6397 | 10.9014 | 1.262 | 0.065653 | 354.6673 | 25.83 | 63.95
2021-01-31 22:40 | 1.239 | 0.18896 | 0.056668 | 0.34631 | 13.7026 | -2.7487 | 1.2622 | 0.08755 | 356.186 | 25.85 | 64.27
2021-01-31 22:45 | 1.2518 | 0.21636 | 0.067168 | 0.39881 | 6.4687 | 6.3767 | 1.2696 | 0.10215 | 357.204 | 25.86 | 64.48
2021-01-31 22:50 | 2.4012 | 0.14103 | 0.060863 | 0.27703 | 15.531 | 16.3178 | 1.2694 | 0.10214 | 356.2251 | 25.83 | 64.22
2021-01-31 22:55 | 1.1496 | 0.11365 | 0.052473 | 0.22668 | 10.28 | 5.5794 | 1.2695 | 0.072962 | 357.3007 | 25.79 | 64.64
2021-01-31 23:00 | 1.2902 | 0.12598 | 0.058773 | 0.25188 | 19.3553 | 20.1013 | 1.2696 | 0.065669 | 356.2799 | 25.74 | 65
2021-01-31 23:05 | 0.86853 | 0.12049 | 0.062963 | 0.24766 | 29.3053 | 36.8666 | 1.2767 | 0.036478 | 355.8058 | 25.73 | 64.67
2021-01-31 23:10 | 1.1751 | 0.090373 | 0.048275 | 0.1889 | 22.6137 | 23.2064 | 1.2768 | 0.029184 | 357.4362 | 25.68 | 65.03
2021-01-31 23:15 | 1.8649 | 0.11776 | 0.050374 | 0.23298 | 25.5673 | -4.2919 | 1.2622 | 0.051073 | 355.851 | 25.67 | 65.12
2021-01-31 23:20 | 1.1881 | 0.1616 | 0.05668 | 0.30649 | 22.8322 | 20.594 | 1.2551 | 0.029189 | 356.8093 | 25.71 | 65.42
2021-01-31 23:25 | 1.3542 | 0.15339 | 0.054581 | 0.2897 | 2.3609 | -1.206 | 1.2478 | 0.014595 | 357.8318 | 25.74 | 65.32
2021-01-31 23:30 | 1.0474 | 0.1205 | 0.065067 | 0.24977 | 1.9518 |  | 1.2258 | 0.029185 | 357.8979 | 25.73 | 64.91
2021-01-31 23:35 | 1.1881 | 0.10819 | 0.056679 | 0.22252 | -1.4615 | 2.1769 | 1.2186 | 0.043783 | 355.4231 | 25.69 | 65.39
2021-01-31 23:40 | 1.3669 | 0.087643 | 0.039883 | 0.17213 | -9.0954 | 4.701 | 1.2186 | 0.04378 | 356.0238 | 25.65 | 65.35
2021-01-31 23:45 | 1.9415 | 0.061618 | 0.046176 | 0.14063 | -4.2305 | -1.635 | 1.2111 | 0.058368 | 357.1889 | 25.59 | 65.3
2021-01-31 23:50 |  | 0.067102 | 0.052478 | 0.15534 | 0.1533 | -10.8124 | 1.2113 | 0.072969 | 355.607 | 25.55 | 65.79
2021-01-31 23:55 | 1.3413 | 0.07258 | 0.044081 | 0.15743 | -0.49054 | -3.3009 | 1.2259 | 0.094858 | 354.5494 | 25.55 | 65.77
2021-02-01 | 0.35769 | 0.11229 | 0.046181 | 0.21831 | 2.4732 | 9.3714 | 1.2405 | 0.080265 | 355.0299 | 25.59 | 65.63

## MS Data Validation
Lane Cove Tunnel Stack Marden St Data Validation January 2021
Start Date | End Date | Parameters | Reason | Hours affected | User Name | Change Date
2021-01-01 | 2021-01-04 10:05 | PM2.5 | Instrument fault due to unstable cabinet temperature | 82.0833 | TA | 2021-02-08
2021-01-04 10:10 | 2021-01-04 14:50 | All parameters | Maintenance | 4.6667 | TA | 2021-02-08
2021-01-04 15:35 | 2021-01-31 23:25 | PM2.5, PM10 | Intermittent negative data | N/A | TA | 2021-02-08
2021-01-07 02:05 | 2021-01-09 00:55 | CH4, NMHC | Nightly span check out of tolerance | 46.8333 | TA | 2021-02-08
2021-01-10 | 2021-01-30 00:05 | All parameters | Intermittent missing data | N/A | TA | 2021-02-08
2021-01-19 00:05 | 2021-01-19 10:00 | CH4, NMHC | Instrument fault - flatline readings | 9.9167 | TA | 2021-02-08
2021-01-19 10:05 | 2021-01-19 11:10 | CO, NO, NO2, NOx, CH4, NMHC | Maintenance | 1.0833 | TA | 2021-02-08
2021-01-25 01:55 | 2021-01-27 00:55 | CH4, NMHC | Nightly span check out of tolerance | 47 | TA | 2021-02-08
This table details any missing data, data removed due to being deemed invalid, or data that has been adjusted.